## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2006
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses.
According to this protocol, using Method 1, at 0600 of the Day Ahead period, ERCOT will calculate Distribution Loss Factors for each
Settlement Interval as a percentage to be applied to the load for the Operating Day and publish the factors to the MIS. Distribution Loss
Factors will be calculated from the data provided by Distribution Service Providers as follows:
SILFi = ADLF * [ K + ( 1 - K) * (SIELi / AAL)]
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
ADLF = Annual Distribution Loss Factor
K = a factor provided by the DSP
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load
And where:
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
(ERCOT will use the Distribution Loss Factors calculated for each Settlement Interval of the Operating Day for settlement purposes.
The calculations will be done a day ahead based on forecasted load levels.)
For CenterPoint Energy:
Loss Factors for Secondary Customers Designated "D"
ADLF = 3.65 %
K = 0.830
AAL = 8,075 MWh's (for 15 min interval for ERCOT)
Avg Annual Load for CNP that corresponds to secondary service is 1,517 MWH's (for 15 mins)
Loss Factors for Primary Customers Designated "E"
ADLF = 1.25 %
K = 0.310
AAL = 8,075 MWh's (for 15 min interval for ERCOT)
Avg Annual Load for CNP that corresponds to primary service is 98 MWH's (for 15 mins)
Customer Coding:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
Portion of Loss Factor that is not sensitive to load:
D | For CenterPoint Energy, the total no-load losses are 153.6 MW's. Therefore, based on total losses of 248.74 MW at the
Average Annual Load level (AAL) for ERCOT, the portion of the loss factor not sensitive to load for secondary
customers designated "D" is 61.75%.
E | For CenterPoint Energy, the primary no-load losses are 20.30 MW's. Therefore, based on primary losses of 78.74 MW at the
Average Annual Load level (AAL) for ERCOT, the portion of the loss factor not sensitive to load for primary
customers designated "E" is 25.78%.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. The constants
for these equations were updated based on increased substation and distribution transformer installations from 2001 to 2004.
The average annual load (AAL) for ERCOT was determined from data on the ERCOT website. The AAL for CenterPoint Energy was
determined by totalizing the annual energy consumption for all of CenterPoint Energy and subtracting the energy consumption for
transmission customers. Separate extracts were performed to get the breakdown between primary customers and secondary customers.
Peak load values were obtained for ERCOT and for the Centerpoint Energy distribution system. See Tab 2 for a comparison of the
ERCOT load and CenterPoint Energy load, as well as the AAL values.
Since the K Factor equation in Method 1 is based on ERCOT load, not individual TDU load, and the loss equations are based on
CenterPoint Energy load, the results had to be scaled to match at the"AAL level" and at the"peak load level". This would
maximize the accuracy for the calculation of the loss factor at average load levels and at high load levels.
See Tab 3 for loss equations and the scaling.
The constants for the straight line K Factor equation were selected to make the best fit to the distribution % loss curve for both
the secondary customers "D" and the primary customers "E". See Tab 4 for these graphs.
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-207-6710,
or email at richard.moffatt@centerpointenergy.com.
CenterPoint Energy Distribution Loss Factor For 2006.xls

## 2) ERCOT Load Comparison
ERCOT / CenterPont Energy Loading Comparison For 2003
Assumptions for 2005 Using 2003 Data | 2003 |  |  | 10/1/2002 - 9/30/2003
| CNP | CNP | CNP | ERCOT | ERCOT | ERCOT
| Annual | Avg Hr | Avg 15 Min | Annual | Avg Hr | Avg 15 Min
| (GWH's) | (MWH's) | (MWH's) | (GWH's) | One Hour | ERCOT AAL
CNP Annual GWH's (Gross) | 73924 | 8438.8128 | 2109.7032
Less Transmission Customers * | 17327.5113 | 1978.0264 | 494.5066
Total Annual GWH's (All Distribution Customers) | 56596.4887 | 6460.7864 | 1615.1966 | 282959.594 | 32301.3235 | 8075.3309
CNP Distribution Peak Load MW's - Coincident |  | 13145.89
ERCOT Peak Load MW's - Coincident |  |  |  |  | 60095
Distribution Substation Peak MW's for 2003 |  | 13274
Coincidence Factor |  | 0.985
Load on Low Side of Substation Transformers |  | 13074.89
Losses on Substation Transformers |  | 71
Total CNP Distribution Peak Load - Coincident |  | 13145.89
|  | Annual | Avg Hour | Avg
|  | GWH's | MWH's | 15 Min
| Primary Metered Customers | 3432 | 391.7808 | 97.9452
| Secondary Customers | 53164.4887 | 6069.0056 | 1517.2514
| All Customers | 56596.4887 | 6460.7864 | 1615.1966

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 3) Loss Analysis 2006
CenterPoint Energy Distribution Loss Factor For 2006.xls | [5 empty] | K = | 0.31 | [7 empty] | 1667 | K = | 0.83
| CNP |  | PELCAR | Primary | Total | Total | Primary Customer |  |  |  | Secondary |  |  | CNP | ERCOT | ERCOT | Secondary Customer
| Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Coded "E" K Formula | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | 2003 Load | 2003 Load | 2003 15 Min | Coded "D" K Formula
| (MW) | (MW) | (MW) | (MW) |  |  | ERCOT | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (MW) | (MW) | Interval | ERCOT
[6 empty] | ADLF = | 0.0125 | [8 empty] | ADLF = | 0.0365
|  | No Load Losses |  |  |  | ERCOT 15 min AAL = | 8075 |  |  |  |  | No Load Losses |  |  |  | ERCOT 15 min AAL = | 8075
|  | Primary Customers | [9 empty] | Secondary Customers
| 50 | 20.2962 | 29.7038 | 0.00098078 | 20.2972 | 40.59% |  | 29.7028 | 133.2971 | -103.5943 | 0.003804 | 153.5981 | 307.2% | 6400 | 31995.0472 | 7998.7618 | <--- AAL Scaling
| 135 | 20.3009 | 114.6991 | 0.014624 | 20.3155 | 15.05% |  | 114.6845 | 133.304 | -18.6196 | 0.00012289 | 153.6197 | 113.8% | 6461 | 32300 | 8075 | <--- AAL
| 500 | 20.3704 | 479.6296 | 0.25572 | 20.6261 | 4.125% |  | 479.3739 | 133.4262 | 345.9477 | 0.042422 | 154.0947 | 30.82%
| 1000 | 20.5953 | 979.4047 | 1.0663 | 21.6616 | 2.166% |  | 978.3384 | 133.8364 | 844.502 | 0.2528 | 155.7508 | 15.58%
1 | 2400 | 22.0224 | 2377.9776 | 6.2859 | 28.3082 | 1.18% | 0.7967% | 2371.6918 | 136.469 | 2235.2228 | 1.771 | 166.5482 | 6.94% | 2400 | 15325 | 3831.25 | 3.324%
2 | 2800 | 22.646 | 2777.354 | 8.5745 | 31.2205 | 1.115% | 0.8412% | 2768.7795 | 137.6202 | 2631.1593 | 2.4539 | 171.2947 | 6.118% | 2800 | 16992 | 4248 | 3.356%
3 | 3200 | 23.3655 | 3176.6345 | 11.2172 | 34.5827 | 1.081% | 0.8857% | 3165.4173 | 138.9477 | 3026.4696 | 3.2467 | 176.7771 | 5.524% | 3200 | 18659 | 4664.75 | 3.388%
4 | 3600 | 24.181 | 3575.819 | 14.2135 | 38.3945 | 1.067% | 0.9303% | 3561.6055 | 140.4508 | 3421.1547 | 4.1487 | 182.994 | 5.083% | 3600 | 20326 | 5081.5 | 3.42%
5 | 4000 | 25.0924 | 3974.9076 | 17.5632 | 42.6556 | 1.066% | 0.9748% | 3957.3444 | 142.129 | 3815.2154 | 5.1595 | 189.9441 | 4.749% | 4000 | 21993 | 5498.25 | 3.452%
6 | 4400 | 26.0998 | 4373.9002 | 21.266 | 47.3658 | 1.076% | 1.019% | 4352.6342 | 143.9816 | 4208.6526 | 6.2785 | 197.6259 | 4.491% | 4400 | 23660 | 5915 | 3.484%
7 | 4800 | 27.2031 | 4772.7969 | 25.3218 | 52.5249 | 1.094% | 1.064% | 4747.4751 | 146.0081 | 4601.467 | 7.5052 | 206.0381 | 4.292% | 4800 | 25327 | 6331.75 | 3.516%
8 | 5200 | 28.4023 | 5171.5977 | 29.7302 | 58.1325 | 1.118% | 1.108% | 5141.8675 | 148.2078 | 4993.6597 | 8.839 | 215.1794 | 4.138% | 5200 | 26994 | 6748.5 | 3.548%
9 | 5600 | 29.6975 | 5570.3025 | 34.491 | 64.1885 | 1.146% | 1.153% | 5535.8115 | 150.5802 | 5385.2313 | 10.2796 | 225.0483 | 4.019% | 5600 | 28661 | 7165.25 | 3.58%
10 | 6000 | 31.0886 | 5968.9114 | 39.604 | 70.6926 | 1.178% | 1.197% | 5929.3074 | 153.1246 | 5776.1828 | 11.8263 | 235.6435 | 3.927% | 6000 | 30328 | 7582 | 3.612%
11 | 6400 | 32.5757 | 6367.4243 | 45.0688 | 77.6445 | 1.213% | 1.242% | 6322.3555 | 155.8405 | 6166.515 | 13.4787 | 246.9637 | 3.859% | 6400 | 31995 | 7998.75 | 3.644%
12 | 6800 | 34.1587 | 6765.8413 | 50.8853 | 85.044 | 1.251% | 1.286% | 6714.956 | 158.7273 | 6556.2288 | 15.2362 | 259.0074 | 3.809% | 6800 | 33662 | 8415.5 | 3.676%
13 | 7200 | 35.8376 | 7164.1624 | 57.0531 | 92.8907 | 1.29% | 1.331% | 7107.1093 | 161.7843 | 6945.325 | 17.0983 | 271.7733 | 3.775% | 7200 | 35329 | 8832.25 | 3.708%
14 | 7600 | 37.6125 | 7562.3875 | 63.5721 | 101.1846 | 1.331% | 1.375% | 7498.8154 | 165.011 | 7333.8044 | 19.0645 | 285.2601 | 3.753% | 7600 | 36996 | 9249 | 3.74%
15 | 8000 | 39.4833 | 7960.5167 | 70.4419 | 109.9252 | 1.374% | 1.42% | 7890.0748 | 168.4068 | 7721.668 | 21.1344 | 299.4664 | 3.743% | 8000 | 38663 | 9665.75 | 3.772%
16 | 8400 | 41.4501 | 8358.5499 | 77.6623 | 119.1124 | 1.418% | 1.464% | 8280.8876 | 171.9711 | 8108.9165 | 23.3073 | 314.3909 | 3.743% | 8400 | 40330 | 10082.5 | 3.804%
17 | 8800 | 43.5127 | 8756.4873 | 85.2331 | 128.7459 | 1.463% | 1.509% | 8671.2541 | 175.7034 | 8495.5508 | 25.5829 | 330.0322 | 3.75% | 8800 | 41997 | 10499.25 | 3.836%
18 | 9200 | 45.6714 | 9154.3286 | 93.154 | 138.8254 | 1.509% | 1.553% | 9061.1746 | 179.6029 | 8881.5717 | 27.9606 | 346.3889 | 3.765% | 9200 | 43664 | 10916 | 3.868%
19 | 9600 | 47.926 | 9552.074 | 101.4247 | 149.3507 | 1.556% | 1.598% | 9450.6493 | 183.6692 | 9266.9801 | 30.4399 | 363.4599 | 3.786% | 9600 | 45331 | 11332.75 | 3.9%
20 | 10000 | 50.2765 | 9949.7235 | 110.0451 | 160.3215 | 1.603% | 1.642% | 9839.6785 | 187.9017 | 9651.7768 | 33.0204 | 381.2436 | 3.812% | 10000 | 46998 | 11749.5 | 3.932%
21 | 10400 | 52.7229 | 10347.2771 | 119.0147 | 171.7376 | 1.651% | 1.687% | 10228.2624 | 192.2997 | 10035.9626 | 35.7014 | 399.7388 | 3.844% | 10400 | 48665 | 12166.25 | 3.964%
22 | 10800 | 55.2653 | 10744.7347 | 128.3335 | 183.5988 | 1.7% | 1.732% | 10616.4012 | 196.8628 | 10419.5385 | 38.4826 | 418.9441 | 3.879% | 10800 | 50332 | 12583 | 3.996%
23 | 11200 | 57.9036 | 11142.0964 | 138.001 | 195.9047 | 1.749% | 1.776% | 11004.0953 | 201.5902 | 10802.5051 | 41.3634 | 438.8583 | 3.918% | 11200 | 51999 | 12999.75 | 4.028%
24 | 11600 | 60.6379 | 11539.3621 | 148.0172 | 208.6551 | 1.799% | 1.821% | 11391.3449 | 206.4815 | 11184.8634 | 44.3434 | 459.4799 | 3.961% | 11600 | 53666 | 13416.5 | 4.06%
25 | 12000 | 63.4681 | 11936.5319 | 158.3817 | 221.8498 | 1.849% | 1.865% | 11778.1502 | 211.536 | 11566.6142 | 47.422 | 480.8077 | 4.007% | 12000 | 55333 | 13833.25 | 4.092%
26 | 12400 | 66.3942 | 12333.6058 | 169.0942 | 235.4884 | 1.899% | 1.91% | 12164.5116 | 216.7532 | 11947.7584 | 50.5988 | 502.8404 | 4.055% | 12400 | 57000 | 14250 | 4.124%
27 | 12800 | 69.4163 | 12730.5837 | 180.1545 | 249.5709 | 1.95% | 1.954% | 12550.4291 | 222.1325 | 12328.2966 | 53.8733 | 525.5766 | 4.106% | 12800 | 58667 | 14666.75 | 4.157%
28 | 13200 | 72.5344 | 13127.4656 | 191.5624 | 264.0968 | 2.001% | 1.999% | 12935.9032 | 227.6733 | 12708.2299 | 57.245 | 549.0151 | 4.159% | 13200 | 60334 | 15083.5 | 4.189%
29 | 13600 | 75.7483 | 13524.2517 | 203.3176 | 279.0659 | 2.052% | 2.043% | 13320.9341 | 233.3751 | 13087.559 | 60.7134 | 573.1544 | 4.214% | 13600 | 62001 | 15500.25 | 4.221%
30 | 14000 | 79.0582 | 13920.9418 | 215.4199 | 294.4781 | 2.103% | 2.088% | 13705.5219 | 239.2372 | 13466.2847 | 64.2781 | 597.9934 | 4.271% | 14000 | 63668 | 15917 | 4.253%
31 | 14400 | 82.4641 | 14317.5359 | 227.8689 | 310.333 | 2.155% | 2.132% | 14089.667 | 245.2592 | 13844.4079 | 67.9385 | 623.5307 | 4.33% | 14400 | 65335 | 16333.75 | 4.285%
AAL | 6461 | 32.8109 | 6428.1891 | 45.9331 | 78.744 |  |  | 6382.256 | 156.2697 | 6225.9863 | 13.7399 | 248.7536 |  | 13200 | 60341.853 | <--- Peak Scaling
[14 empty] | 13146 | 60095 | <--- Peak Load
| 400 | [12 empty] | 400
| Substation Transformers |  | Primary Conductor |  |  |  |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant |  |  |  | B Constant | A Constant | B Constant | A Constant | CNP |  |  | ERCOT |  | Loss Factor at AAL
| 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 |  |  |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | 6461 |  | 2003 AAL Hr | 32301 |  | 3.65%
[12 empty] | 1615.25 |  | 2003 AAL 15 Min | 8075.25 |  | 3.65%
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 |  |  |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
| 19.73 | 2.9981e-07 | 0 | 1.1116e-06 |  |  |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001
| 20.2955 | 2004 | [5 empty] | 133.2966 | 2004 |  |  | <--- 2004 Update
| 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [6 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004

## Loss Equations
System Loss Equations For CenterPoint Energy
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformer
| A = | 2.9981e-07
| B = | 20.295 | Total No-Load Losses For Substation Transformers = 20.29 MW
Primary Conductor
| A = | 1.1116e-06
| B = | 0
Distribution Transformers
| A = | 2.9981e-07
| B = | 133.3 | Total No-Load Losses For Distribution Transformers = 133.3 MW
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified