ERCOT Operating Guides

Section 2:  System Operations

ERCOT Control Area Authority Operation

April 1, 2006

Contents

2.	System Operations	2-5

2.1	Operational Duties	2-5

2.2	System Monitoring and Control	2-7

2.2.1	Overview	2-7

2.2.2	Security Criteria	2-8

2.2.3	Automatic Generation Control Systems	2-9

2.2.4	Automatic Voltage Regulators And Power System Stabilizers	2-11

2.2.5	Turbine Speed Governors	2-11

2.2.6	Performance/Disturbance/Compliance Analysis	2-12

2.2.7	Time Error And Time Synchronization	2-12

2.3	Dispatch Duties	2-15

2.3.1	Control Area Operator Authority	2-15

2.3.2	Dispatch Instruction Procedures	2-16

2.4	Scheduling	2-19

2.4.1	Day Ahead Scheduling	2-19

2.4.2	Adjustment Period Scheduling Process	2-21

2.4.3	Direct Current Tie Interconnection Day Ahead Scheduling Process	2-23

2.4.4	Temporary Deviations from Scheduling Procedures	2-23

2.4.5	Real-Time Schedules	2-24

2.5	Ancillary Services	2-31

2.5.1	ERCOT Responsibilities	2-31

2.5.2	Responsive Reserve	2-37

2.5.3	Non-Spinning Reserve Service (NSRS)	2-40

2.5.4	Replacement Reserve Service (RPRS)	2-41

2.5.5	Balancing Energy Service	2-42

2.6	Changes in System Status	2-45

2.6.1	Changes in Resource Status	2-45

2.6.2	Changes in Transmission Facility Status	2-45

2.7	Outage Coordination	2-46

2.7.1	ERCOT Control Area Authority Responsibilities	2-46

2.7.2	Forced Outages	2-46

2.7.3	Scheduled Outages	2-47

2.8	Congestion Management	2-48

2.8.1	Overview of ERCOT Coordinated Congestion Management	2-48

2.9	Requirements for Under-Frequency Relaying	2-50

2.9.1	Automatic Firm Load Shedding	2-50

2.9.2	Generators	2-51

2.10	System Voltage Profile	2-52

2.10.1	Introduction	2-52

2.10.2	Maintaining Voltage Profile	2-52

2.10.3	Special Consideration for Nuclear Power Plants	2-53

2.10.4	Reactive Considerations for Gas and Steam Turbine Power Plants	2-54

2.11	External Control Area Inter-Ties	2-55

2.11.1	Control Area Operations	2-55

2.11.2	Operation of DC Ties	2-55

2.12	Document Control	2-56

Protocol References

Reference:  Protocols Section 5.1.2, Operating Guides and North American Electric Reliability Council Guidelines	2-5

Reference:  Protocols Section 5.3, Routine Dispatch Duties of ERCOT	2-5

Reference:  Protocols Sections 6.1.2, Regulation Service – Down and 6.1.3, Regulation Service – Up	2-10

Reference:  Protocols Section 6.5.7.2, QSE Responsibilities	2-11

Reference:  Protocols Section 5.2.2, Operating Standards	2-15

Reference:  Protocols Section 5.4.2.1, Verbal Dispatch Instructions	2-16

Reference:  Protocols Section 5.4.2.2, Dispatch Instruction via the Messaging System	2-17

Reference:  Protocols Section 5.4.4, Compliance with Dispatch Instructions	2-17

Reference:  Protocols Section 4.2, Scheduling-Related Duties of ERCOT	2-19

Reference:  Protocols Section 4.4.2, Posting of Forecasted ERCOT System Conditions	2-19

Reference:  Protocols Section 4.4.4, Notification to QSEs of Ancillary Service Obligations	2-20

Reference:  Protocols Section 4.4.5,  Notification to QSEs of Mandatory Balancing Energy Service Down Bid Percentage Requirements	2-20

Reference:  Protocols Section 4.1.2, Adjustment Period Scheduling Process	2-21

Reference:  Protocols Section 4.4.18.1, Control Area Operations	2-23

Reference:  Protocols Section 4.4.18.2, Linkage of Schedules with Interconnected Non-ERCOT Control Area Schedules	2-23

Reference:  Protocols Section 4.4.18.3, Operation of DC Ties	2-23

Reference:  Protocols Section 4.8, Temporary Deviations from Scheduling Procedures	2-23

Reference:  Protocols Section 4.9, Dynamic Schedules	2-24

Reference:  Protocols Section 4.9.3, Principles for Dynamic Schedules	2-25

Reference:  Protocols Section 4.9.4, Responsibility Transfers (RspT)	2-26

Reference:  Protocols Section 6.5.9, Reliability Must Run Service	2-27

Reference:  Protocols Section 6.7.8, Deployment of RMR Service	2-29

Reference:  Protocols Section 6.3.1, ERCOT Responsibilities	2-31

Extracted from Protocols Section 6.1 in modified form	2-34

Reference:  Protocols Section 6.5.4, Responsive Reserve Service	2-37

Reference:  Protocols Section 6.5.4, Responsive Reserve Service	2-38

Reference:  Protocols Section 6.5.5, Non-Spinning Reserve Service (NSRS) (1)	2-40

Reference:  Protocols Section 6.5.5, Non-Spinning Reserve Service (NSRS) (1), (2), and (5)	2-40

Reference:  Protocols Section 6.5.6, Replacement Reserve Service (1), (2), and (6)	2-41

Reference:  Protocols  Section 6.5.2, Balancing Energy Service	2-42

Reference:  Protocols Section 6.10.3, Ancillary Services Qualification and Portfolio Test Methods	2-43

Reference:  Protocols Section 6.10.3.4, Balancing Energy	2-43

Reference:  Protocols Section 5.5.1, Changes in Resource Status	2-45

Reference:  Protocols Section 5.5.2, Changes in Transmission Facility Status	2-45

Reference:  Protocols Section 7.1, Overview of ERCOT Congestion Management	2-48

Reference:  Protocols Section 6.5.7.2, QSE Responsibilities	2-54

Reference:  Protocols Section 6.10.9, Reactive Power Supply from Generation Resources Required to Provide VSS Performance Criteria	2-54

Reference:  Protocols Section 4.4.18.5, Inadvertent Energy Account	2-55

# System Operations

## 2.1	Operational Duties

Reference:  Protocols Section 5.1.2, Operating Guides and North American Electric Reliability Council Guidelines

ERCOT will perform all Control Area functions as defined in the Operating Guides and the North American Electric Reliability Council (NERC) guidelines.

Reference:  Protocols Section 5.3, Routine Dispatch Duties of ERCOT

ERCOT is the regional security coordinator for the ERCOT Region and is responsible for all regional security coordination as defined in the NERC Operating Manual and applicable ERCOT operating manuals or Operating Guides.

The duties of the ERCOT Control Area Authority are described in relevant sections of the Protocols.  The following lists the primary operational duties to be performed by the ERCOT Control Area Authority.  Each of these duties as well as all other ERCOT responsibilities are to be executed in accordance with the applicable Protocols.  The ERCOT Protocols shall control the extent of any inconsistency between the Protocols and any of the following Operating Guides.

| CONTROL AREA AUTHORITY RESPONSIBILITY | CONTROL AREA AUTHORITY ACTION |
| --- | --- |
| Ensure the reliability of the ERCOT Transmission Grid in accordance with North American Electric Reliability Council/ERCOT reliability guidelines. | - Evaluate ERCOT Transmission Grid conditions on a continuous basis. - Oversee operation of the ERCOT Transmission Grid and act as the ERCOT Control Area Authority. - Serve as the point of contact for initiation of generation interconnection to the transmission system. - Implement Congestion Management of the ERCOT Transmission Grid on a nondiscriminatory basis. - Coordinate all Planned Outages of transmission system facilities. - Schedule ERCOT Interchange transactions across the DC Ties. - Deploy Ancillary Services - Compile a detailed operations plan to ensure that sufficient resources and required Ancillary Services have been provided for all expected load and transactions within the ERCOT Region. - Forecast the actual load, generation dispatch and transmission system operations for the next seven days and update total transmission capacity (TTC), as necessary. - Adjust resources in accordance with the ERCOT Protocols as needed to maintain ERCOT in a secure operating condition and meet NERC frequency control performance requirements. |
| Supervise the ERCOT System operational transmission planning | - Perform operational transmission system security studies, including those related to generation and load interconnection responsibilities. - Review outages of generating units and major transmission lines to identify constraints that may affect transfers. - Perform load flows and security analyses of Planned Outages submitted by TDSPs as a basis for approval or rejection. - Withdraw approval of a scheduled Transmission Facility Maintenance Outage if unable to meet the applicable reliability standards after all other reasonable options are exercised. |
| Collect and disseminate information | - Provide appropriate operational information to individual QSEs and TOs. - Provide relevant operational information to Market Participants over the ERCOT Market Information System. - Collect and maintain Control Area Authority operational data required by the PUCT and the NERC. - Receive reports from TOs and QSEs and forward them to DOE and/or NERC as required. - Submit Reliability Coordinator reports to DOE and/or NERC as required. - Record and report accumulated time error. |

## 2.2	System Monitoring and Control

### 2.2.1	Overview

The Control Area Authority will maintain continuous surveillance of the status of operating conditions within the ERCOT System and act as a system security central information collection and dissemination point for Market Participants.

The Control Area Authority is the designated coordinating authority to request and receive information required to continually monitor the operating conditions of ERCOT and to order individual QSEs and/or TOs make changes to assure ongoing security and reliability of the total ERCOT System.

The Control Area Authority shall maintain, monitor or direct the following in accordance with the ERCOT Protocols:

| CONTROL AREA AUTHORITY RESPONSIBILITY | CONTROL AREA AUTHORITY ACTION |
| --- | --- |
| Generation | - Monitor unit status and capability, - Monitor Automatic Voltage Regulator status, - Monitor unit commitment, - Balance system generation and loads, - Monitor Operating Reserves, - Monitor Forced Outages and capability limitations, - Maintain net capability test results, - Maintain LaaRs test results, - Compile Ancillary Services Plans, - Perform Ancillary Services deployment, - Collect data for Ancillary Services accounting, - Monitor maintenance schedules, and - Monitor Power System Stabilizer status. |
| Bulk-Power Transmission System | - Monitor line loading and power transfers, - Coordinate Planned Outages, - Monitor and detect Forced Outages, - Perform contingency analyses, - Maintain maintenance and construction schedules, - Monitor and control voltage levels, and - Monitor Reactive Power flows. |
| System Operation | - Monitor power transfers and interchange, - Maintain and monitor Ancillary Services Plans and delivery, - Maintain compliance with Transmission Security Criteria, - Monitor QSE providers of Regulation Service, - Manage inadvertent Energy Account balances, - Direct time error correction, - Issue and direct Operating Condition Notices, Advisories, Alerts and Emergency Notices - Direct Short Supply Operations, - Direct implementation of the Emergency Electric Curtailment Plan (EECP), and - Direct coordination of the Black Start Plan. |
| Reporting | - Monitor and coordinate information for daily planning, hourly reporting and minute-by-minute operation. - Verify the accuracy of the Real Time data. - Operate a Market Information System (MIS) and a Power Operations System (POS) to disseminate real time, hourly accounting, and operations plan data to and from the Control Area Authority and each QSE and TO Control Center. - Establish the procedure for each TO and QSE to report to the Control Area Authority. |

### 2.2.2	Security Criteria

Technical limits established for the operation of transmission equipment shall be applied consistently in TTC calculations, Engineering Studies, real-time security analyses, and operator actions.

Unless an Emergency Condition has been declared by ERCOT, the ERCOT System shall be operated in such a manner that the occurrence of a single contingency will not cause any of the following conditions:

a.	Uncontrolled breakup of the transmission system;

b.	Loading of Transmission Facilities above defined emergency ratings which can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures;

c.	Transmission voltage levels outside system design limits which cannot be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs; or

d.	Customer outages, except for high set interruptible and radially served loads.

A credible single contingency is defined as the Forced Outage of two generating units as defined in Section 5.1.4, Transmission Reliability Testing, item (2), in the ERCOT System within a short period of time, or the Forced Outage of any single transmission element (such as a circuit or transformer).  The Forced Outage of a double-circuit transmission line (DCKT) will be considered a credible single contingency during any ERCOT declared Alert or for any operating conditions characterized by high DCKT Outage probability or consequence.

### 2.2.3	Automatic Generation Control Systems

ERCOT shall operate the frequency control system to maintain the scheduled frequency at 60 Hz (correcting periodically for time error) and to minimize the use of energy from Resources providing Regulation Service.

The ERCOT frequency control system shall deploy Regulation and Responsive Reserve energy as necessary in accordance with the ERCOT Protocols to meet NERC requirements.

ERCOT will deploy resources via electronic instruction to QSEs that represent generators providing Automatic Generation Control (AGC) resources.  QSEs shall use AGC to direct the output of generation facilities within the response times described in the ERCOT Protocols and Operating Guide Section 8, Operational Metering and Communication.

#### 2.2.3.1	Bias Settings

In the Schedule Control Error equation, QSEs shall have bias settings that approximate the measured frequency response characteristic of their On-line Resources.  This bias setting should be changed when significant On-line generating capability changes or when their Resources’ frequency response characteristics change.  The ERCOT Control Area Authority will check the area frequency response characteristic each time a disturbance qualifies as a measurable event per Section 5.8.2 of the Protocols.  Information thus obtained will be used to evaluate ERCOT and QSE bias settings.

#### 2.2.3.2	Maintenance And Verification

Each provider of Regulation and/or Responsive Reserve ancillary service will properly maintain Automatic Generation Control equipment.

The ERCOT Control Area Authority will initiate a regulation survey to evaluate the performance of all Automatic Generation Control equipment in ERCOT.

#### 2.2.3.3	Regulation Provider Loss of AGC (Generator loses pulse signal)

If a QSE providing Regulation Services or Responsive Reserve Services loses its Automatic Generation Control for any reason, it will notify the ERCOT Control Area Authority as soon as practicable of the reason for and estimated duration of the loss.  The ERCOT Control Area Authority will assess whether additional action should be taken to maintain ERCOT System frequency.  Possible ERCOT actions include:

- Placing another QSE on Flat Frequency Control, and/or

- Opening the market for new Regulation or Responsive Reserve resource bids for the period of anticipated loss.

#### 2.2.3.4	ERCOT Control Area Authority loss of Automatic Control

The ERCOT Control Area Authority is obligated to have back-up facilities in place for loss of control systems.  In the event that these backup facilities also fail to perform, the ERCOT Control Area Authority shall direct specific QSEs providing frequency control to implement Flat Frequency Control.

If action is necessary, the ERCOT Control Area Authority will arrange for these QSEs to go on Flat Frequency Control (FFC) for the duration of the control loss and will define the ERCOT bias.  If a QSE on FFC develops a problem with regulating room, the ERCOT Control Area Authority will order additional balancing or regulation energy from another QSE to create regulation room.

#### 2.2.3.5	Changes in Control Mode

A QSE shall notify (telephone) the ERCOT Control Area Authority and obtain approval prior to changing control modes.  Valid QSE control modes are Normal (Ancillary Services control), Flat Frequency and Off control.

#### 2.2.3.6	Load and Frequency Regulation

Reference:  Protocols Sections 6.1.2, Regulation Service – Down and 6.1.3, Regulation Service – Up

6.1.2	Regulation Service – Down

As provided by ERCOT to the QSEs: Regulation-down power is deployed in response to an increase in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

As provided by a QSE to ERCOT: The provision of Generation Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

[PRR307:  Revise Section 6.1.2 as follows when system change implemented.]

As provided by a QSE to ERCOT: The provision of Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

6.1.3	Regulation Service-Up

As provided by ERCOT to the QSEs: Regulation up power is deployed in response to a decrease in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

As provided by a QSE to ERCOT: The provision of Generation Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

[PRR307:  Revise Section 6.1.3 as follows when system change implemented.]

As provided by a QSE to ERCOT: The provision of Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

The ERCOT Control Area Authority shall purchase sufficient Regulation resources to provide satisfactory control performance for ERCOT.  ERCOT shall determine the satisfactory amount of Regulation Service required by statistical analysis of possible unit outages and load forecast error to expect operation 95% of hours without deploying Responsive Reserve Service.

### 2.2.4	Automatic Voltage Regulators And Power System Stabilizers

Reference:  Protocols Section 6.5.7.2, QSE Responsibilities

(4)	Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) set to regulate generator terminal voltage in the voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On- or Off- line.  If the QSE changes the mode, other than under ERCOT direction, then the QSE shall promptly inform ERCOT. Any QSE-controlled power system stabilizers will be kept in service unless specifically permitted to operate otherwise by ERCOT.  QSEs’ control centers will monitor the status of their regulators and stabilizers, and shall report abnormal status changes to ERCOT.

Generator Automatic Voltage Regulators (AVR) and power system stabilizers (PSS) will be kept in service whenever possible.  Generation Resources (GR) shall notify their Qualified Scheduling Entity (QSE) who in turn will promptly notify the ERCOT Control Area Authority when a voltage regulator or stabilizer is taken out of service due to equipment maintenance or failure and when it is returned to normal operation.  ERCOT is responsible for notifying the appropriate TO of such AVR and PSS status changes.  QSEs shall supply AVR and PSS status logs to ERCOT upon request.

Performance tests shall be conducted on Automatic Voltage Regulators every five years or if equipment characteristics are knowingly modified.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

Excitation systems, including power system stabilizers, shall also be tested every five (5) years.

### 2.2.5	Turbine Speed Governors

All governors must be placed in-service.

Governor performance tests should be conducted at least every two years and results used in analysis as described in Section 6.2.1, Turbine Governor Speed Regulation Tests.  A sample of such tests may be found in Section 6.2.1.2, Example of a Turbine Governor Speed Regulation Test for Mechanical Hydraulic Governor.  Every effort should be made to maintain governors with a five percent (5%) droop characteristic.

There are other elements that can contribute to poor governor response.  These include:

- Governor dead band.  Maximum intentional dead band: +/- 0.036 Hz.

- Valve position limits

- Blocked governor operation

- Control mode

- Adjustable rates or limits

- Boiler/turbine coordinated control or set point control action

- Automated “reset” or similar control action of the turbine’s MW set point.

Every attempt should be made to minimize the effects of these elements on the governor operation for the duration of all frequency deviations.  Each QSE should monitor its units to verify that these elements do not contribute to a governor droop characteristic greater than five percent (5%).

### 2.2.6	Performance/Disturbance/Compliance Analysis

Performance/Disturbance/Compliance analysis shall be performed by the ERCOT Control Area Authority for the purpose of ensuring conformance to published control criteria of ERCOT.

The Control Area Authority shall make a regular report on selected system disturbances, documenting the response of individual Qualified Scheduling Entities together with an ERCOT summary.  In addition, Power Generation Companies, Qualified Scheduling Entities and individual members of the ERCOT Performance Disturbance Compliance Working Group (PDCWG) are encouraged to work within their respective companies to enhance the performance of individual generating units and control systems through application of the results of the Working Group studies.

ERCOT Compliance communicates with the Market Participants as appropriate to ensure compliance and improve performance.

As necessary, a Contingency Reserve Adjustment (CRA) will be calculated by the PDCWG and submitted to the Reliability and Operations Subcommittee for review and approval.  ERCOT will include the CRA in the daily Ancillary Service plan.

### 2.2.7	Time Error And Time Synchronization

#### 2.2.7.1	Time Error

Sustained frequency deviations from scheduled frequency result in time error.  Time error will be monitored and controlled in ERCOT as follows:

Time Error Monitoring

ERCOT will monitor accumulated time error and initiate time corrections.  The instantaneous time error is available to all ERCOT QSEs in the Market Information System (MIS).  When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction.  The correction will be terminated when the error is less than ±0.5 seconds.  The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction; however, at no time should the accumulated time error be allowed to exceed five (5) seconds.

Time Error Correction

When a time correction is necessary, ERCOT will adjust scheduled frequency in the following manner.  ERCOT shall adjust generation to achieve the correction frequency (59.98 Hz for fast and 60.02 Hz for slow) and shall immediately notify all QSEs of the frequency, start time, and end time. A time correction may be terminated after five hours or after any hour without a one-half second error reduction.

#### 2.2.7.2	Time Synchronization

In order to promote accurate data reporting during EECP and other system events, and to ensure transaction schedules are simultaneous, all QSEs and TOs, and the ERCOT Control Area Authority will maintain their control system time within +/-3 seconds of the National Bureau of Standards (NBS) time signal.  The NBS time signal shall set the time standard for ERCOT.  The ERCOT Control Area Authority, QSEs deploying Ancillary Services and TOs will follow written procedures to compare and reset their clocks and voice and data recording systems’ times with the NBS on at least a weekly basis.

## 2.3	Dispatch Duties

### 2.3.1	Control Area Operator Authority

ERCOT, as Control Area Operator (CAO), is authorized to take the following actions for the limited purpose of securely operating the ERCOT Transmission Grid in conformance with the standards specified in the Protocols, Section 5.2 and according to the ERCOT Protocols in general. Standards and practices used in the operation of the ERCOT Transmission Grid include but are not limited to:

- Direct the physical operation of the ERCOT System, including circuit breakers, switches, voltage control equipment, protective relays, metering and Load shedding equipment;

- Deploy Resources that have committed to provide Ancillary Services;

- Direct changes in the operation of voltage control equipment;

- Direct the implementation of OOM obligations and the use of RMR Service and transmission switching in order to prevent the violation of ERCOT System security limits; and

- Take those additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT System to a secure state in the event of an ERCOT System emergency.

Reference:  Protocols Section 5.2.2, Operating Standards

ERCOT and TDSPs shall operate the ERCOT System in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures. These Protocols shall control to the extent of any inconsistency between the Protocols and any of the following documents:

- Any reliability guides applicable to ERCOT, including the Operating Guides;

- The NERC Operating Manual and ERCOT procedures manual, supplied by NERC and ERCOT, respectively, as references for dispatchers to use during normal and emergency operations of the ERCOT Transmission Grid;

- Specific operating procedures, submitted to ERCOT by individual transmission Facility owners or operators to address operating problems on their respective grids that could affect operation of the interconnected ERCOT Transmission Grid; and

- Guidelines established by the ERCOT Board, which may be more stringent than those established by NERC for the secure operation of the ERCOT System.

### 2.3.2	Dispatch Instruction Procedures

Dispatch Instructions consist of Verbal Dispatch Instructions and Dispatch Instructions issued via the Messaging System.  The procedures for all Dispatch Instructions are as follows:

| TYPE OF INSTRUCTION | ERCOT CONTROL AREA AUTHORITY PROCEDURE |
| --- | --- |
| All Dispatch Instructions to Resources (whether for Dispatch of Ancillary Services, System Emergencies or any other reason) | Directed to the QSE responsible for the affected Resource, normally performed electronically via RTU or XML. |
| Resource or group of Resources has inadequately responded to a Dispatch Instruction | Notify the relevant QSE |
| Verbal communication of Dispatch Instructions | Record all voice conversations that occur |
| Written or electronic communication of Dispatch Instructions | Record or file all written or electronic Dispatch Instructions and acknowledgements as soon as practicable after the issuance of the Dispatch Instruction. |
| Recipient of Dispatch Instruction, by mutual agreement of the QSE and ERCOT or the TDSP and ERCOT | Dispatch Instructions to the QSE or TDSP may be provided to the QSEs or TDSPs or their Designated Agent. |

#### 2.3.2.1	Contents of Verbal Dispatch Instructions

Reference:  Protocols Section 5.4.2.1, Verbal Dispatch Instructions

Valid verbal Dispatch Instructions shall contain the following information:

- Identification of the responsible Entity and instructing authority (to include ERCOT operator’s and receiving operator’s names);

- Specific Resources or TDSP Facilities that are the subject of the Dispatch Instruction;

- Specific action required;

- Current operating level or state of the Resources or TDSP Facilities that are the subject of the Dispatch Instruction;

- Operating level or state to which such Resources or Facilities will be dispatched;

- Time of notification of the Dispatch Instruction;

- Time at which the QSE or TDSP is required to initiate the Dispatch Instruction;

- Time within which the QSE or TDSP is required to complete the Dispatch Instruction; and

- Other information relevant to the specific Dispatch Instruction.

#### 2.3.2.2	Dispatch Instruction via the Messaging System

Reference:  Protocols Section 5.4.2.2, Dispatch Instruction via the Messaging System

- Valid Dispatch Instructions issued via the Messaging System shall contain the following information:

- (1)	Identification of the responsible Entity;

- (2)	Specific Resources that are the subject of the Dispatch Instruction;

- (3)	Specific action required;

- (4)	Time of notification of the Dispatch Instruction via a timestamp on the Dispatch Instruction;

- (5)	Time at which the QSE is required to initiate the Dispatch Instruction;

- (6)	Time within which the QSE is required to complete the Dispatch Instruction; and

- (7)	Other information relevant to the specific Dispatch Instruction.

#### 2.3.2.3	Compliance with Dispatch Instructions

Reference:  Protocols Section 5.4.4, Compliance with Dispatch Instructions

- Each TDSP and each QSE within the ERCOT System shall comply fully and promptly with valid Dispatch Instructions, unless in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols.

- If the recipient of a valid Dispatch Instruction does not comply because in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols, then, the TDSP or QSE must immediately notify ERCOT and provide the reason for non-compliance.

- If the recipient of a Dispatch Instruction recognizes that the Dispatch Instruction conflicts with other valid instructions or is invalid, the recipient will immediately notify ERCOT of the conflict and request resolution.

- Upon receipt of notice of non-compliance or conflict with Dispatch Instructions, ERCOT may, but is not required to, issue new Dispatch Instructions in response to the TDSP or QSE’s notice.

- ERCOT’s final instruction in effect will apply for all Protocol-related processes. If the QSE does not comply after receiving the final instruction, the QSE shall remain liable for failure to meet its obligations under the Protocols and shall remain liable for any charges resulting from such failure.

- ERCOT’s final instruction to a TDSP in effect will apply for all Protocol-related processes. If the TDSP does not comply after receiving the final instruction, the TDSP shall remain liable for such failure under these Protocols in accordance with the TDSP’s Agreement with ERCOT.

- In all cases in which compliance with a Dispatch Instruction is disputed, both ERCOT and the QSE or TDSP shall document their communications, agreements, disagreements, and reasons for their actions, to enable resolution of the dispute through the ADR process in Section 20, Alternative Dispute Resolution.

## 2.4	Scheduling

Reference:  Protocols Section 4.2, Scheduling-Related Duties of ERCOT

ERCOT is responsible for administering the Day Ahead and Adjustment Period Scheduling Processes through which final schedules for energy and Ancillary Services are submitted by QSEs and a Current Operating Plan is developed for use in operating the ERCOT System in Real Time. To fulfill its responsibilities with respect to providing information to the market necessary for QSEs to schedule energy and Ancillary Services, ERCOT shall:

- Post forecasted ERCOT System conditions and Load for the next seven (7) days, by hour, by Congestion Zone; Post forecasted ERCOT System conditions and Load for the next seven (7) days by hour, by Congestion Zone. ERCOT will also post any area Load forecasts that were used to create the system Load forecast;

- Post forecasted Transmission Loss Factors and Distribution Loss Factors;

- Post Load Profiles for non-IDR metered Customers;

- Validate the QSEs’ energy schedules and make adjustments as necessary in accordance with the validation process;

- Validate the QSEs’ Ancillary Service schedules and Self-Arranged Ancillary Service Resources;

- Only accept schedules from a QSE; and

- Require all Loads and Resources be represented by a QSE.

### 2.4.1	Day Ahead Scheduling

The Control Area Authority is required to perform specific analysis of the ERCOT System and provide information to QSEs and others within the ERCOT System during specific periods of the day prior to the Operating Day, as follows:

| TIME PERIOD | ERCOT ACTION |
| --- | --- |
| Prior to 0600 | For each hour of the Operating Day, ERCOT shall post: Reference: Protocols Section 4.4.2, Posting of Forecasted ERCOT System Conditions No later than 0600 in the Day Ahead ERCOT shall post the following information for each hour of the Operating Day: - A forecast of conditions on the ERCOT System, including known transmission line and other Transmission Facility Outages; - A forecast of Total Transfer Capability including any relevant information describing forecasted transfers for each CSC. - Weather assumptions used by ERCOT to forecast ERCOT System conditions. |
| 0600 | Publish updated transmission system information: Reference: Protocols Section 4.4.4, Notification to QSEs of Ancillary Service Obligations ERCOT will notify QSEs by 0600 of the Day Ahead of the QSE’s Day Ahead Ancillary Service Obligations. The Day Ahead Ancillary Service Obligation will be assigned to each QSE by multiplying the ERCOT Obligation by the sum of the Load Ratio Shares, rounded to no fewer than six (6) decimal places, for the LSEs that a QSE represents. Reference: Protocols Section 4.4.5, Notification to QSEs of Mandatory Balancing Energy Service Down Bid Percentage Requirements ERCOT will make available via a programmatic interface and post by 0600 of the Day Ahead the percentage of mandatory Balancing Energy Service Down bids required by Congestion Zone for each hour of the Operating Day for each QSE. If ERCOT changes the percentage requirement for any hour for any Congestion Zone from the previous Operating Day, only then will ERCOT notify all QSEs by 0600 of the Day Ahead of the QSE’s percentage requirement for Balancing Energy Service Down bids by Congestion Zone for each hour of the Operating Day. The percentage of mandatory Balancing Energy Service Down bids required will be the same for all QSEs, but will not apply to energy scheduled by ERCOT from Resources under an RMR Agreement. |
| 1100 | Validate Schedules and notify affected Qualified Scheduling Entities (QSEs) of any invalid or mismatched schedules. |
| 1115 | - Review Schedules using the Commercial Model - Evaluate CSC Congestion - Notify QSEs of Congested CSCs - Post schedule impact on CSCs - Notify QSEs of any difference in ERCOT’s zonal Load forecast and the aggregate of QSE schedules in a zone. |
| 1300 | Validate Schedules and notify affected QSEs of any invalid or mismatched schedules |
| 1315 | Validate resubmitted schedules and adjust as necessary. |
| 1330 | - Purchase AS through ERCOT AS Market in order to complete ERCOT’s Day Ahead AS plan. - Review Day Ahead Market Clearing Prices for Capacity (MCPC) for each Day Ahead AS market operated by ERCOT. |
| 1500 | Review and validate AS schedules as necessary. |
| 1600 | Verify that Resource Plans are sufficient to meet the QSE schedule. If not, ERCOT will notify the QSE. |
| No later than 1800 | - Evaluate Resource Plans to determine system security - Evaluate RPRS needed to correct CSC, and Operational Congestion – Operational Model, and capacity insufficiency. - Create Merit Order of RPRS by Zone or operational constraint as applicable - Determine MCPC for RPRS by Zone as applicable and save RPRS energy bids for applicable balancing markets. - Close and clear Day Ahead RPRS market |

### 2.4.2	Adjustment Period Scheduling Process

Reference:  Protocols Section 4.1.2, Adjustment Period Scheduling Process

The Adjustment Period Scheduling Process will follow the following timeline with time T being the start of the Operating Hour:

| Adjustment Period | QSE Responsibility: | ERCOT Responsibility: |
| --- | --- | --- |
| Time = T minus 60 minutes | - Submit updated Balanced Schedule of Obligations and Supply for the hour beginning at Time T, and any hour after T. - Submit bids for Balancing Energy including any mandatory decremental Balancing Energy bids. - Submit updated Self-Arranged AS schedule for the hour beginning at Time T and any hour after Time T (the amount of Self-Arranged AS may not change from Day Ahead, however, the Resources supplying the Self Arranged AS may be altered. If ERCOT calls on additional AS in the AP, the allocated portion of the additional AS may be self- arranged). - Submit updates to Resource Plan. - Submit bids for RPRS. - Submit bids for additional Ancillary Services. - Submit bids for incremental and decremental Resource specific premiums. | - Review updated Balanced Schedule. - Review updated Resource Plans. - Review updated Self-Arranged AS Schedule. - Validate Schedules and notify affected Qualified Scheduling Entities (QSEs) of any invalid or mismatched schedules. - Identify CSC or OC Congestion or capacity insufficiency. |
| Time = T minus 45 minutes | - Resubmit corrected schedules. |  |

Any hour, on the hour, more than sixty (60) minutes prior to the Operating Hour, ERCOT Control Area Authority shall perform the following actions, based on QSE submissions:

- Review QSE Submitted updated Balanced Schedules

- Review QSE submitted updated Resource Plans

- Review QSE submitted updated Self-Arranged Ancillary Service Schedule

- Validate Schedules and notify affected Qualified Scheduling Entities (QSEs) of any invalid or mismatched schedules.

- Identify CSC or OC Congestion or capacity insufficiency and take action to maintain ERCOT security.

- Any hour, 15 minutes after the hour, more than 60 minutes prior to the Operating Hour, ERCOT will validate resubmitted schedules and adjust as necessary

### 2.4.3	Direct Current Tie Interconnection Day Ahead Scheduling Process

#### 2.4.3.1	Control Area Operations

Reference:  Protocols Section 4.4.18.1, Control Area Operations

Control Area schedules between the ERCOT Control Area and interconnected non-ERCOT Control Area(s), through the use of schedules over Direct Current Tie(s), will be implemented in accordance with these Protocols, North American Electric Reliability Council (NERC) scheduling protocols, and in compliance with NERC operating policies.  Scheduling must also be in accordance with any applicable Federal Energy Regulatory Commission tariffs.

ERCOT will perform schedule confirmation with the applicable interconnected non-ERCOT Control Area(s) and, if appropriate, will coordinate the approval process for the NERC tags as both the ERCOT Control Area and on behalf of ERCOT TSPs.

#### 2.4.3.2	Linkage of Schedules with Interconnected Non-ERCOT Control Area Schedules

Reference:  Protocols Section 4.4.18.2, Linkage of Schedules with Interconnected Non-ERCOT Control Area Schedules

ERCOT will match the Supply and Obligation schedules submitted by the QSEs with interconnected non-ERCOT Control Area schedules obtained through the NERC Scheduling Process to confirm schedules and perform checkouts with adjacent interconnected non-ERCOT Control Areas.  ERCOT will determine the linkage between interconnected non-ERCOT Control Area schedules and Supply and Obligation schedules submitted by QSEs. QSE schedules into the DC Tie are an Obligation.  QSE schedules from the DC Tie are a Supply.  If a match does not exist between the interconnected non-ERCOT Control Area schedule and the QSE schedule to or from the DC Tie, then ERCOT will deny the interconnected non-ERCOT Control Area schedule with the applicable interconnected non-ERCOT Control Area(s).  Any QSE’s Supply or Obligation schedule indicated as being received or delivered to or from a DC Tie that cannot be confirmed or linked by ERCOT, will be declared a mismatch and set to zero as described in Section 4.7.2, Schedule Validation Process.

#### 2.4.3.3	Operation of DC Ties

Reference:  Protocols Section 4.4.18.3, Operation of DC Ties

ERCOT will confirm interconnected non-ERCOT Control Area schedule profiles with the DC Tie operator, who will control the tie to the schedules agreed to by both the designated Security Coordinator for the interconnected non-ERCOT Control Area and ERCOT.

### 2.4.4	Temporary Deviations from Scheduling Procedures

Reference:  Protocols Section 4.8, Temporary Deviations from Scheduling Procedures

If ERCOT is unable to comply with any of the deadlines in Sections 4.4, Day Ahead Scheduling Process, or Section 4.5, Adjustment Period Scheduling Process, it may temporarily deviate from those timing requirements to the extent necessary to ensure the secure operation of the ERCOT System. Temporary measures may include varying the timing requirements as specified in Section 4.4.19, Decision to Extend Day Ahead Scheduling Process to Two Day Ahead Scheduling Process, or omitting one or more procedures in the Scheduling Process. In such an event, ERCOT shall immediately declare an Emergency Condition and notify all QSEs of the following:

- Details of the affected timing requirements and procedures;

- Details of any interim requirements;

- An estimate of the period for which the interim requirements will apply; and

- Reasons for the temporary variation.

If, despite the variation of any time requirement or the omission of any procedure, ERCOT is unable to operate the Day Ahead Scheduling Process, ERCOT may abort the Day Ahead Scheduling Process and require all schedules to be submitted in the Adjustment Period.

If, despite the variation of any time requirement or omission of any step, ERCOT is unable to operate the Adjustment Period Scheduling Process, ERCOT may abort the Adjustment Period process and operate under its Operating Period procedures.

If ERCOT implements a Two Day Ahead Scheduling Process, that process shall be as described in Section 4.4.19, Decision to Extend Day Ahead Scheduling Process to Two Day Ahead Scheduling Process.

### 2.4.5	Real-Time Schedules

#### 2.4.5.1	Dynamic Schedule

Reference:  Protocols Section 4.9, Dynamic Schedules

Protocols Section 4.9.1	Dynamic Load Schedules

QSE’s may use dynamic power signals to control generation to match a metered Load in order to minimize the QSE’s exposure to the Balancing Energy market.  To implement the Dynamic Schedule the QSE will send Real Time telemetry to ERCOT that is equal to the metered Load, which the QSE wishes to follow.  ERCOT will integrate the signal for each Settlement Interval and provide the integrated signal to settlement as the scheduled Obligation for that metered Load.  Settlement will use this integrated value as a scheduled Supply for that interval for the QSE.  At settlement the integrated values will be used as a Supply or Obligation schedule.

The QSE’s schedule will include one Supply Resource (or fleet) designated to follow the Dynamic Schedule for a Load.  The designated Supply schedule will be estimated in the same manner as the designated Load.  At settlement, the estimated schedule for the designated Resource will be replaced with the integrated final power signal from the dynamic Load.

Protocols Section 4.9.2	Approval of the Use of Dynamic Load Schedules

(1)	Each QSE desiring to use Dynamic Load Schedules must submit a proposal of the Dynamic Schedule to ERCOT for analysis of Congestion impacts and reliability in accordance with the Operating Guides.

(2)	Subject to number (1) above, any QSE representing Non Opt-In Entities that own, had under construction, or had contractual rights to Generation Resources, as of May 1, 2000, may use Dynamic Schedules.  Once a Non Opt-In Entity (NOIE) offers Customer Choice, it must submit a new proposal for Dynamic Load Scheduling to ERCOT.

(3)	ERCOT will approve dynamic scheduling proposals on a case-by-case basis.  Approval will be based on the schedule’s impact on ERCOT’s ability to determine and manage Congestion, ERCOT's ability to monitor Generation Resource and Load behavior associated with the schedule and the schedule’s impact on system reliability.  QSEs representing Non-Opt In Entities, which submit proposals in accordance with (1) and (2) above will be accepted by ERCOT.

(4)	New proposals for Dynamic Load Schedules within Congestion Zones will be considered after June 1, 2001 and across Congestion Zones after June 1, 2002.

Reference:  Protocols Section 4.9.3, Principles for Dynamic Schedules

- All power signals for Dynamic Schedules must be sent to ERCOT in Real Time via telemetry.

- Each Dynamic Load Schedule must be tied to a Load meter or group of Load meters.  This includes Load that is calculated by subtracting interchange telemetry from actual generation telemetry, appropriately adjusted for T&D Losses.  A Load or group of Loads that is/are dynamically scheduled can only be followed by Generation Resources represented by the same QSE as the Load.

- Each Dynamic Load Schedule will indicate the dynamic power signal that will be used to create the final schedule.

- Dynamic Load Schedules tied to Load meters (or groups of Load meters) may be used between Congestion Zones.

- A QSE using Dynamic Load Schedules shall send a dynamic power signal or signals to ERCOT.

- Each QSE with a Dynamic Load Schedule will include in its schedules and plans submitted to ERCOT, an estimate for the integration of the schedule for each Settlement Interval.  These schedule integration estimates will be used for allocation of RPRS costs.

- ERCOT will integrate the dynamic power signal sent by a QSE for each Settlement Interval. This integrated signal shall replace the estimate and will be used in settlement as the final schedule. Dynamic Schedules do not alter the settlement process for metered Loads.

- If a signal is lost for any reason, ERCOT will use the final schedule for Settlement purposes.

- ERCOT will use the dynamic power signal in each of the applicable QSE’s SCE equation.

ERCOT may approve other Dynamic Scheduling proposals by QSEs on a case-by-case basis. Approval will be based on the Dynamic Schedule’s impact on ERCOT Control Area Authority’s ability to:

- Determine and manage Congestion,

- Monitor Generation Resource and Load behavior associated with the schedule, and

- Determine impact on system reliability.

#### 2.4.5.2	Responsibility Transfer (RspT) Schedules

Reference:  Protocols Section 4.9.4, Responsibility Transfers (RspT)

Protocols Section 4.9.4.1	Approval of the Use of Responsibility Transfers

(1)	Intra-zonal Responsibility Transfers (RspTs) will be approved unless ERCOT determines it cannot accommodate these transfers without compromising reliability or settlement accuracy.

(2)	Each QSE that proposes to use an RspT must submit a proposal of the RspT to ERCOT for analysis of Congestion impacts and reliability in accordance with the Operating Guides.  The proposal for each RspT shall identify:

(a)	Controlling Entity;

(b)	Following Entity;

(c)	Congestion Zone;

(d)	Maximum value;

(e)	Units supplying energy; and

(f)	Other information required by ERCOT.

Protocols Section 4.9.4.2	Principles for Responsibility Transfers

(1)	RspT may be used to shift responsibility for Supply of a defined maximum amount of MWs from one QSE to another QSE within the same Congestion Zone after the close of the Adjustment Period.  As the RspT changes the responsibility for Supply of one QSE there must be an equal and opposite change in the responsibility for Supply of the other QSE.

(2)	One of the QSEs will act as the controller of the Real Time Dynamic signal.  That Controlling Entity (CE) will send a Real Time power signal to ERCOT representing that QSE’s power commitment to the other QSE, the Following Entity (FE).

(3)	ERCOT will use the dynamic power signal from the CE in its calculation of the CE’s SCE.  ERCOT will also use the dynamic power signal from the CE to calculate an equal and opposite value to use in calculation of the FE’s SCE.  The FE will use a signal from the CE to calculate its (the FE’s) SCE.

(4)	ERCOT will integrate the dynamic power signal from the CE for each Settlement Interval and use this value as an offset in the CE’s settlement for Resource imbalance.  An equal but opposite offset will be used in the FE’s settlement for Resource imbalance.

(5)	If the signal from the CE is lost, ERCOT will use the last good value received from the CE until the CE manually replaces the value, or the signal is restored.

ERCOT may approve other Responsibility Transfers proposed by QSEs on a case-by-case basis.  Approval will be based on the impact of the Dynamic Schedule on the ERCOT Control Area Authority’s ability to:

- Determine and manage Congestion.

- Monitor Generation Resource and Load behavior associated with the schedule.

- Determine impact on system reliability.

#### 2.4.5.3	Reliability Must Run Units

The following is the ERCOT Control Area Authority Day Ahead Scheduling Process for Reliability Must Run Units (RMR) Units and Black Start Resources:

| DAY AHEAD HOUR | ERCOT RESPONSIBILITY |
| --- | --- |
| 0900 | Provide initial Delivery Plan to QSEs representing RMR and/or Synchronous Condenser Units where a Market Solution potentially cannot exist. |
| 1630 | Provide updated Delivery Plan to QSEs representing RMR and/or Synchronous Condenser Units where a Market Solution does not exist. |

Reference:  Protocols Section 6.5.9, Reliability Must Run Service

(1)	Upon receiving Notice from a Generation Entity as described in Protocols Subsection 6.5.9.1, Application and Approval of RMR Agreements, ERCOT may enter into RMR Agreements and begin procurement of RMR Service according to the provisions of this section.

(2)	Before entering into an RMR Agreement, ERCOT shall assess alternatives to the proposed RMR Agreement.  The list of alternatives ERCOT should consider include (as reasonable for each type of reliability concern identified):

a)	redispatch/reconfiguration through operator instruction;

b)	Remedial Action Plans;

c)	special protection schemes initiated on unit trips or transmission outages; and

d)	Load response alternatives once a suitable Load response service is defined and available.

(3)	ERCOT shall reasonably attempt to minimize the use of RMR Facilities.  ERCOT shall have the right to Dispatch an RMR Unit at any time for transmission reliability.  ERCOT will Dispatch the unit as early as possible once conditions are identified that require the use of the RMR Unit, as defined in Section 4, Scheduling and the RMR Agreement.

(4)	Each RMR Unit must meet technical requirements specified in Section 6.10 Ancillary Services Qualification, Testing and Performance Standards.

(5)	RMR Service is a contracted service between Generation Entities and ERCOT.  The term of any RMR Agreement shall not exceed 12 months except where a Generation Entity must make a significant capital expenditure to meet environmental regulations or to ensure availability in order to continue operating the unit so as to make an RMR Agreement in excess of 12 months appropriate, in ERCOT’s opinion.  The term of a multi-year RMR Agreement shall reflect the RMR Replacement Option determined in Section 6.5.9.1, Initiation and Approval of RMR Agreements, item (11).  The RMR Standard Agreement is included in Section 22, Protocols Agreements.

(6)	A Generation Resource is eligible for RMR status based on criteria established by ERCOT indicating its operation is necessary to support ERCOT System reliability.  A combined cycle Facility will be treated as a single unit for RMR purposes unless the combustion turbine and the steam turbine can operate separately.  If the steam turbine and combustion turbine can operate separately, and the steam turbine is powered by waste heat from more than one combustion turbine, the combustion turbine(s) accepted for RMR Service and a proportionate portion of the steam turbine will be treated as a single unit for RMR purposes.  If the combustion turbine accepted for RMR Service can operate separately from the steam turbine, and only the combustion turbine is accepted as an RMR Unit, the RMR Energy Price will be reduced by the value of the combustion turbine’s waste heat calculated at the Gas Price Index, except when the steam turbine is off-line.  ERCOT shall post the criteria upon which it evaluates whether an RMR Unit meets the test of operational necessity to support ERCOT System reliability.  A Generation Entity can obtain RMR Agreements only where necessary to ensure ERCOT System reliability according to the Operating Guides.

(7)	A Generation Entity cannot be compelled to enter into an RMR Agreement.  Owners of Generation Resources that are uneconomic to remain in service can voluntarily petition ERCOT for contracted RMR status by following the process in Subsection 6.5.9.1, Application and Approval of RMR Agreements.  ERCOT will be required to determine whether the unit is necessary for system reliability based on the criteria set forth in Subsection 6.5.9(6).  If ERCOT determines that the nominated unit is required for system reliability, the Generation Entity may request ERCOT to allow operation as a Synchronous Condenser in place of RMR operation.  If Synchronous Condenser operation is offered by the Generation Entity, ERCOT shall accept Synchronous Condenser operation unless ERCOT reasonably determines that a Synchronous Condenser operation is not adequate to meet system reliability according to the Operating Guides.

(8)	ERCOT must contract for the entire capacity of each RMR Unit.

(9)	RMR Units may not participate in the bilateral capacity and energy markets, including Self-Arranged Ancillary Services.  RMR Units may participate in the Balancing Energy Service market during times when ERCOT has requested the RMR Unit to run at less than full capacity, provided such participation does not limit availability to ERCOT to less than the Operational and Environmental Limitations as described in the RMR Agreement.  ERCOT will endeavor to Dispatch an RMR Unit prior to procuring OOMC, OOME, or Zonal OOME Services from other Generation Entities, if economic to do so, based on ERCOT’s knowledge at the time, and provided that the RMR Unit supplies equivalent reliability support as would the OOMC, OOME, or Zonal OOME Service, and further provided that the availability constraints of the RMR Unit are maintained.  Within two (2) weeks following any month in which an RMR Unit is dispatched, the owner/operator of the RMR Unit will inform ERCOT of the RMR Unit’s remaining availability.

(10)	RMR Units are dispatched by ERCOT when necessary to provide ERCOT System security, including any emergency situation.

(11)	ERCOT will treat the undeployed energy from RMR Units like any other unit for purposes of Balancing Energy Service Up provided the time of use constraints of the RMR Unit are maintained.

(12)	ERCOT will administer RMR Agreements in such a way as to minimize the use of RMR Units as much as practicable.  ERCOT will provide to all Market Participants all information relative to the use of RMR Units including energy deployed.

(13)	The Generation Entity which owns the RMR Unit may not use the RMR Unit for:

(a)	Participation in the bilateral energy market;

(b)	Self-provision of energy except for plant auxiliary Load obligations under the RMR Agreement;

(c)	Provision of Self Arranged Ancillary Services to any Entity; and

(d)	Ancillary Services markets, except for incremental bids into the Balancing Energy Services market to the extent allowed in the RMR Agreement.

Reference:  Protocols Section 6.7.8, Deployment of RMR Service

(1)	If Market Solutions are not available and in Emergency Conditions, ERCOT shall have the option to Dispatch a contracted RMR Unit at any time for voltage support or localized transmission limitations, but it must Dispatch the unit as early as possible (if conditions merit) once conditions are identified that require the use of the RMR Unit and only to the extent of megawatt loading necessary to correct the voltage support or localized transmission limitation.

(2)	ERCOT must elect to use Resources under an RMR Agreement or MRA Agreement before issuing an OOME or Zonal OOME Dispatch Instruction subject to the terms of the Agreement, if practical.

(3)	ERCOT will deploy RMR Units in accordance with the RMR Agreement and MRA Resources in accordance with the MRA Agreement.  RMR Agreements with ERCOT are expected to include limitations on the total service hours, megawatt-hour output, and the number of starts available to ERCOT for each RMR Unit.

(4)	ERCOT shall issue Dispatch Instructions via the Messaging System for any RMR Unit Dispatch or MRA Resource Dispatch.  Any revisions to those instructions must be communicated via revised Dispatch Instructions.

(5)	In the event that ERCOT orders an RMR Unit or MRA Resource to operate to sustain reliable ERCOT System operation in any Operating Day, ERCOT will post on the MIS as soon as possible, but no later than the next Business Day, for such Operating Day:

(a)	each Resource receiving an RMR or MRA Dispatch Instruction for each interval;

(b)	the amount of RMR or MRA energy ERCOT requested from each Resource for each interval; and

[PRR515: Upon system implementation, insert paragraph (c).] (c) the binding transmission constraint (contingency and/or overloaded element(s)) causing RMR or MRA deployments.

(6)	If ERCOT orders an RMR Unit or MRA Resource to operate to sustain reliable ERCOT System operation in any Operating Day, ERCOT will, on or before the Business Day following the day of issuance of the Initial Statement for the Operating Day on which ERCOT issued the Dispatch Instruction, as described in Section 9.2.3, Initial Statements, post on the MIS the amount of RMR or MRA energy actually provided by each RMR or MRA Unit for each interval of the subject Operating Day.

(7)	ERCOT shall publicly post an annual forecast of the Dispatch pattern it expects for each contracted RMR Unit and MRA Resource as well as monthly and week-ahead forecasts regarding its use of such Resources.

(8)	ERCOT will adjust the amount of Balancing Energy acquired due to the impact of RMR Energy deployed and energy deployed from MRA Resources.  If adjustments made by ERCOT would result in the QSE exceeding its scheduled amount of generation, then the affected QSE must not accommodate these changes by adjusting other Resources such that the Schedule Control Error is minimized.  ERCOT will not assess URC charges to the QSE as a result of these adjustments for the interval.  The RMR may implement a Responsibility Transfer between its QSE and ERCOT for energy delivered under an RMR Agreement to minimize the impact of RMR scheduling on its QSE.

## 2.5	Ancillary Services

### 2.5.1	ERCOT Responsibilities

Reference:  Protocols Section 6.3.1, ERCOT Responsibilities

(1)	ERCOT, through its Ancillary Services function, shall develop the Operating Day Ancillary Services Plan for the ERCOT System, and the Day Ahead Ancillary Service Obligation which will be assigned based on Load Ratio Share data, by LSE, aggregated to the QSE level.  Unless otherwise provided in these Protocols, a QSE’s allocation for Ancillary Service Obligation will be determined for each hour according to that LSE’s Load Ratio Share computed by ERCOT.  The LSE Ancillary Service allocation for the Day Ahead Ancillary Service Obligation shall be based on the hourly Load Ratio Share from the Initial Settlement data, for the Operating Day that is twenty-one (21) days before the day in which the Obligation is being calculated, as defined in Section 9.2, Settlement Statements, for the same hour and day of the week multiplied by the quantity of the service in the Operating Day Ancillary Service Plan.

[PRR451 & PRR426: Replace Section 6.3.1, item (1) above with the following upon system implementation:] (1) ERCOT, through its Ancillary Services function, shall develop the Operating Day Ancillary Service Plan for the ERCOT System., The Day Ahead Ancillary Service Obligation, except for Regulation Service, will be assigned based on Load Ratio Share data, by LSE, aggregated to the QSE level. The Day Ahead Regulation Service Obligation will be assigned based on Energy Ratio Share data, by LSE and Generation Resource, aggregated to the QSE level. Unless otherwise provided in these Protocols, a QSE’s allocation for all Ancillary Service Obligations except Regulation Service will be determined for each hour according to that LSE’s Load Ratio Share computation by ERCOT. For all Ancillary Services Obligations except Regulation Service, the LSE Ancillary Service allocation for the Day Ahead Ancillary Service Obligation shall be based on the hourly Load Ratio Share from the Initial Settlement data, for the Operating day that is twenty-one (21) days before the day in which the Obligation is being calculated, as defined in Section 9.2, Settlement Statements, for the same hour and day of the week multiplied by the quantity of the service in the Operating Day AS Plan. For Regulation Service, the LSE plus the Generation Resource Ancillary Service allocation shall be the hourly Energy Ratio Share of the Load data and the data from Uncontrollable Renewable Resources electing to utilize Renewable Production Potential for URC and OOME from the Initial Statement, as defined in Section 9.2, Settlement Statements, for the same hour and day of the week multiplied by the quantity of the service in the Operating Day Ancillary Service Plan.

[PRR568: Replace "twenty-one (21)" with "fourteen (14)" in paragraph (1) above (boxed and unboxed) upon completion of the transition plan.]

(2)	ERCOT shall procure required Ancillary Services not self-arranged by QSEs.

(3)	ERCOT accepts Ancillary Service bids only from QSEs.

(4)	ERCOT shall allow the same capacity to be bid as multiple Ancillary Services types recognizing that this capacity may only be selected for one service.

(5)	ERCOT shall ensure provision of Ancillary Services to all ERCOT System Market Participants in accordance with these Protocols.

(6)	ERCOT shall not discriminate when obtaining Ancillary Services from QSEs submitting Ancillary Service bids.  ERCOT shall not discriminate between Self-Arranged Ancillary Services and ERCOT-procured Ancillary Services when dispatching Ancillary Services.

(7)	For AS that are not self-arranged, ERCOT shall procure any additional Resources ERCOT requires during the Day-Ahead Scheduling Process, the Adjustment Period process, or the Operating Period.

(8)	ERCOT shall procure Resources that are used to provide Reliability Must-Run Service or Black Start Service through longer-term Agreements.

(9)	Following submission of QSE self-arranged schedules, ERCOT will identify the remaining amount of Ancillary Services that must be acquired in order to complete ERCOT’s Day-Ahead Ancillary Services Plan.  Regulation Up, Regulation Down, Responsive, and Non-Spinning services will be procured by ERCOT on the timeline described in Section 4, Scheduling.

(10)	ERCOT will not profit financially from the market.  ERCOT will follow the Protocols with respect to the procurement of Ancillary Services and will not otherwise take actions regarding Ancillary Services with the intent to influence, set or control market prices.

(11)	ERCOT will provide that Market Clearing Prices are posted on the Market Information System (MIS) in a timely manner as stated in Section 12.4.1, Scheduling Information, of these Protocols.  ERCOT will monitor Market Clearing Prices for errors and will “flag” for further review questionable prices before posting, and make adjustments or notations in the posting if there are conditions that cause the price to be questionable.  ERCOT may only correct the price consistent with these Protocols.

(12)	ERCOT shall post the aggregated ERCOT AS Bid Stacks in accordance with Section 12.4.2, Ancillary Service Related Information of these Protocols.

(13)	ERCOT will, through procurement processes specified in these Protocols, procure Ancillary Services as required and charge QSEs for those Ancillary Services in accordance with these Protocols.

(14)	ERCOT will ensure ERCOT electric network reliability and adequacy and will afford the market a reasonable opportunity to supply reliability solutions.

(15)	ERCOT will not substitute one type of Ancillary Service for another.

(16)	ERCOT shall strive to use Market Solutions to manage Congestion prior to using OOMC, RMR, or Zonal OOME Services.

(17)	ERCOT shall make reasonable efforts to minimize the use of OOMC, Zonal OOME, or contracted RMR Facilities.  This includes entering into MRA Agreements with Resources selected through the planning process, pursuant to Section 6.5.9.2, to provide services to meet reliability requirements at lower total expected costs than would otherwise be provided by RMR Agreements.

(18)	ERCOT will provide timely information to those Resource units providing OOMC and RMR Services as to the specific use of each unit dispatched.

[PRR413: Replace Section 6.3.1 paragraphs (16)-(18) with the following upon system implementation. (This effectively deletes paragraph (16) above.)] (16) ERCOT will make reasonable efforts to minimize the use of OOMC, Zonal OOME or contracted RMR Facilities. (17) ERCOT will provide timely information to those Resource units providing OOMC and RMR Services as to the specific use of each unit dispatched.

Extracted from Protocols Section 6.1 in modified form

The types of Ancillary Services required by ERCOT are described below.

| ANCILLARY SERVICE TYPE | DEFINITION | ERCOT CONTROL AREA AUTHORITY ACTION |
| --- | --- | --- |
| Regulation Service – Down And Regulation Service-Up | Generation Resource capacity provided by a QSE to control frequency within the ERCOT System which is controlled minute by minute (normally by an AGC System). | - Regulation-down power is deployed in response to a change in ERCOT System frequency above the target system frequency. - Regulation up power is deployed in response to a change in ERCOT System frequency below the target system frequency. |
| Balancing Energy Service | The provision of incremental or decremented energy dispatched by Settlement Interval to meet the balancing needs of the ERCOT System. | Deployed to: - Restore regulation control room by replacing Regulation Service energy with Balancing Energy Service. - To ensure that the net energy for Regulation Service up and down is minimized. - To ensure Zonal Congestion is managed |
| Responsive Reserve Service | Operating reserves ERCOT maintains to restore the frequency of the ERCOT System within the first few minutes of an event that causes a significant deviation from the standard frequency. The provision of power and energy by: - Unloaded Generation Resources that are On-line, - Resources controlled by high set under-frequency relays, or - Direct Current (DC) tie-line response. The DC tie-line response must be fully deployed within fifteen (15) seconds on the ERCOT System after the under frequency event. | Normally None – Responsive Reserve deploys automatically through governor action. Or Deployed for the Operating Hour in response to loss-of-Resource contingencies on the ERCOT System. |
| Non-Spinning Reserve Service | - Off-line Generation Resource capacity, or reserved capacity from On-line Generation Resources, capable of being ramped to a specified output level within thirty (30) minutes, or - Loads acting as a Resource that are capable of being interrupted within thirty (30) minutes and that are capable of running (or being interrupted) at a specified output level for at least one (1) hour. | Deployed for the Operating Hour in response to loss-of-Resource contingencies, load forecasting error, or other contingency events on the ERCOT System. |
| Replacement Reserve Service | Bringing into available service a Resource capable of providing additional Balancing Energy Service to ERCOT. (Normally forcing unit commitment) | Deployment of Loads or non-synchronized Generation Resources in order to make available additional Balancing Energy Service. |
| Voltage Support | The provision of Generation Resource capacity whose power factor and output voltage level can be scheduled by ERCOT to maintain transmission voltages within acceptable limits throughout the ERCOT System in accordance with Operating Guide 2.10. | Direct the scheduling of Voltage Profiles at the high voltage side of generator busses to maintain transmission voltages on the ERCOT System. |
| Black Start Service | The provision of Resources under a Black Start Agreement, which are capable of self-starting without support from the ERCOT System in the event of a blackout. | Provide emergency Dispatch Instructions to begin restoration of the ERCOT System to a secure operating state after a total or partial blackout. |
| Reliability Must-Run Service | The provision of Generation Resource capacity and/or energy Resources under a Reliability Must-Run (RMR) Agreement. | Direct the operation of units which otherwise would not operate and which are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria, where Market Solutions are not available or cost effective. |
| Out-Of-Merit Capacity Service | Generation or Loads acting as a Resource capable of providing additional Balancing Energy Service. | When capacity insufficiency, Congestion, or other reliability needs exist and a Market Solution does not exist: Deployed to ensure: - Regulation Service in either direction is not depleted during the interval, and - The net energy for Regulation Service up and down is minimized. |
| Out-Of-Merit Energy Service | The provision of incremental or decremented energy dispatched from a specific Resource by Settlement Interval in Real Time to meet the balancing needs of the ERCOT System when no Market Solution exists or in declared emergencies. | Dispatched to provide Balancing Energy Service when no Market Solution exists for resolving Congestion or if required in declared emergencies. |

ERCOT shall procure and deploy Ancillary Services on behalf of QSEs.

### 2.5.2	Responsive Reserve

#### 2.5.2.1	Obligation

The ERCOT Responsive Reserve Obligation is 2300 MW.

#### 2.5.2.2	Allocation Of Obligation

The daily Responsive Reserve Obligations will be available on the Operating Reserve Display on the ERCOT information system. The allocation of the Responsive Reserve Obligation (RRO) between Load Entities will be based on Section 6.3.1 of the Protocols.

#### 2.5.2.3	Types Of Responsive Reserve

Reference:  Protocols Section 6.5.4, Responsive Reserve Service

(1)	Responsive Reserve Service (RRS) may be provided by:  (a) unloaded Generation Resources that are On-line, (b) Resources controlled by high-set under-frequency relays, (c) hydro Responsive Reserves, or, (d) from DC Tie response that stops frequency decay.  The minimum amount of RRS provided by Generation Resources shall be as specified in the Operating Guides. QSE’s Generation Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment. The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides.

Responsive reserves provided by a QSE shall meet the following requirements:

- In no case shall more than 20% of the Net Dependable Capability for any thermal unit be used as Responsive Reserve.

- In no case shall more than 20% of the Net Dependable Capability for any hydro unit with a 5% droop setting operating as a generator be used as Responsive Reserve.

[OGRR149: Replace (1) and (2) above with the following upon system implementation of PRR502:] - (1) In no case shall more than twenty percent (20%) of the Net Dependable Capability for any non-Combined Cycle thermal unit be used as Responsive Reserve. - (2) In no case shall more than twenty percent (20%) of the combined Net Dependable Capability for any Combined Cycle Block with one or more CTs or GTs coupled to a Steam Turbine, with their net maximum capability aggregated together, be used as Responsive Reserve. - (3) In no case shall more than twenty percent (20%) of the Net Dependable Capability for any hydro unit with a five percent (5%) droop setting operating as a generator be used as Responsive Reserve.

Interruptible Responsive Reserve

Reference:  Protocols Section 6.5.4, Responsive Reserve Service

- A QSE’s Load acting as a Resource must be loaded and capable of unloading the scheduled amount of RRS within ten (10) minutes of instruction by ERCOT and by action of underfrequency relays as specified by the Operating Guides.

- Loads acting as a Resource providing RRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay.

  - The amount of Resources on high-set under-frequency relays providing RRS will be limited to fifty percent (50%) of the total ERCOT RRS requirement.  ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation to be deployed as prescribed in Section 6.4.1, Standards for Determining Ancillary Services Quantities.

Telemetered Interruptible Load controlled by under-frequency relays (UFR) for automatic interruption may be provisionally qualified and eligible to participate as a responsive reserve Resource as specified in Section 6.10.1, Introduction, of the Protocols.

To become provisionally qualified as a provider of Responsive Reserve Service (RRS), the Load shall complete the following requirements:

- Register as a Resource with ERCOT;

- Complete Asset Registration of LaaR;

- Provide ERCOT the appropriate UFR Load Affidavit;

- Provide ERCOT with a simplified one-line diagram between relay and operating device;

- Provide ERCOT with a UFR set point calibration documentation including: the relay used to shed Load at low frequency, the relay set point, the relay operating time, and the typical loads to be shed;

- Test to verify appropriate voice communications are in place for verbal Dispatch Instructions by ERCOT;

- Be capable of interruption by automatic operation of the under-frequency relay(s) set to initiate the interruption whenever system frequency reaches a specific value.  The initiation setting of the relay shall not be any lower than 59.7 Hz.;

- Have frequency measuring relays with a time delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles).  Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times.

- Be capable of interruption within 10 minutes of receipt of a verbal Dispatch Instruction from ERCOT;

- Be telemetered through the QSE to the ERCOT CAA with a real-time signal of total interruptible Load on high-set under-frequency relays, breaker status, the status of the high set under-frequency relay, and signals representing the Load Resource’s MW response to instruction; and,

- Be able to remain interrupted during actual event until replaced by other Net Dependable Capability.  In no case may interrupted Load be restored to service without the approval of the ERCOT operator;

To become and remain fully qualified as a provider of RRS, the Load shall complete the requirements above and the following:

- Pass simulated or actual testing according to ERCOT Procedure; and,

- Perform verification testing as described in Operating Guides Section 6, Reports and Forms.

DC Tie Responsive Reserve

A DC tie may be used as Responsive Spinning Reserve up to 30 MW subject to the following constraints:

- The tie shall respond with increased deliveries to ERCOT or decreased deliveries from ERCOT at an ERCOT frequency of 59.9 Hz;

- The response rate will not be less than 30 MW per minute;

- The response delay will not exceed 4 seconds;

- The response will be retained until the ERCOT frequency has recovered to a level at or above 60.0 Hz or as directed by the Control Area Authority;

- A QSE claiming DC Tie Responsive Reserve Service must demonstrate the existence of contracts agreeing to provide the required response with the DC Tie operator;

- A QSE claiming DC Tie Responsive Reserve Service must have agreement with the Control Area on the opposite side of the DC Tie involved approving the amount and conditions.

Hydro Responsive Reserve

Hydro Unit(s) operating in the synchronous condenser fast response mode may be designated as Hydro Responsive Reserve provided that:

- Only the amount of a hydro unit's demonstrated 10 second response may be used as Responsive Reserve subject to verification as described in Protocols Section 6.10;

- Automatic controls using the "fast response" mode must be in operation to initiate a move to the generating mode.  The initiation setting of the automatic controls shall not be any lower than 59.9 Hz and the unit must be generating within four (4) seconds of the set relay operation;

- A Real Time signal of the MW output of hydro units being operated in the synchronous condenser fast response mode is telemetered to the ERCOT.

### 2.5.3	Non-Spinning Reserve Service (NSRS)

#### 2.5.3.1	Types of Non-Spin Reserve Service

- As Provided by Generating Resources

Reference:  Protocols Section 6.5.5, Non-Spinning Reserve Service (NSRS) (1)

NSRS providers must be capable of being synchronized and ramped to their bid-specified output level within thirty (30) minutes. NSRS can be provided from unloaded on-line capacity that can ramp within thirty (30) minutes

Each Generating Resource providing NSRS must meet additional technical requirements specified in Section 6.10, Ancillary Service Qualification Testing and Performance.

As Provided by Loads acting as a Resource (LaaR)

Reference:  Protocols Section 6.5.5, Non-Spinning Reserve Service (NSRS) (1), (2), and (5)

Load acting as a Resource that is capable of unloading within thirty (30) minutes and that is not fulfilling any other commitment from the capacity, including participation in ERCOT markets, self-generation, or other energy transactions.

Loads providing NSRS must provide a telemetered output signals, including breaker status.

QSEs using Loads to provide NSRS must be capable of responding to ERCOT Dispatch Instructions in a similar manner to QSEs using Generation Resource to provide NSRS.

Telemetered Load available to be interrupted within 30 minutes of an ERCOT deployment may be provisionally qualified and eligible to provide non-spinning reserve as specified in Section 6.10.1, Introduction, of the Protocols.

To become provisionally qualified as a provider of NSRS, the Load shall complete the following requirements:

- Register as a Resource with ERCOT;

- Complete Asset Registration of LaaR;

- Provide ERCOT the appropriate Non-Spinning Load Affidavit;

- Test to verify appropriate voice communications are in place for verbal Dispatch Instructions by ERCOT;

- Be telemetered through the QSE to the ERCOT CAA with the Load MW of each LaaR breaker, breaker status, and signals representing the Load Resource’s MW response to instruction; and,

- Be able to remain interrupted during an ERCOT deployment for a minimum of one hour up to a maximum of the hours of service awarded.

To become and remain fully qualified as a provider of NSRS, the Load shall complete all the requirements for provisional qualification identified above and the following:

- Respond successfully to an actual ERCOT deployment; or pass simulated or actual testing according to ERCOT’s Procedure; and,

- Perform verification testing as described in Operating Guides Section 6, Reports and Forms.

### 2.5.4	Replacement Reserve Service (RPRS)

Reference:  Protocols Section 6.5.6, Replacement Reserve Service (1), (2), and (6)

Replacement Reserve Service (RPRS) is provided by Resources that may otherwise be unavailable to ERCOT in the hours that ERCOT requests RPRS.  These Resources may include Generation Resources that are expected to be off-line in the requested hours and Loads acting as a Resource that otherwise may be unavailable to be dispatched by ERCOT, i.e.  Loads not declared as an active Resource in the Resource Plan at the time of the RPRS procurement.

[PRR307: Revise Section 6.5.6(1) as follows when system change implemented.] Replacement Reserve Service (RPRS) is provided by Resources that may otherwise be unavailable to ERCOT in the hours that ERCOT requests RPRS. These Resources may include Generation Resources that are expected to be off-line in the requested hours and Loads acting as a Resource that are declared to be available in the Resource Plan but are not committed to any service Obligation.

Resources providing RPRS must provide a telemetered output signal, including breaker status.

Generation Resource and Loads acting as a Resource accepted for RPRS must be able to respond in the hours for which they have been selected to provide the Ancillary Service.

Each Generation Resource providing RPRS must meet additional technical requirements specified in Section 6.10, Ancillary Service Qualification Testing and Performance.

Telemetered Load available may be provisionally qualified and eligible to provide replacement reserve as specified in Protocols Section 6.10.1, Introduction.

To become provisionally qualified as a provider of RPRS, the Load shall complete the following requirements:

- Register as a Resource with ERCOT;

- Complete Asset Registration of LaaR;

- Provide ERCOT the appropriate Affidavit;

- Test to verify appropriate voice communications are in place for verbal Dispatch Instructions by ERCOT;

- Be telemetered through the QSE to the ERCOT CAA with the Load MW of each LaaR breaker, breaker status, and signals representing the Load Resource’s MW response to instruction; and,

- Be capable of interruption within 10 minutes of receipt of a verbal Dispatch Instruction from ERCOT;

To become and remain fully qualified as a provider of RPRS, the Load shall complete all the requirements for provisional qualification identified above and the following:

- Respond successfully to an actual ERCOT deployment; or pass simulated or actual testing according to ERCOT Procedure; and,

- Perform verification testing as described in Operating Guides Section 6, Reports and Forms.

### 2.5.5	Balancing Energy Service

Reference:  Protocols  Section 6.5.2, Balancing Energy Service

The Balancing Energy Service bids shall consist of Balancing Energy Service Up, Balancing Energy Service Down, and Balancing Up Load bids.  All Balancing Energy Service provider bids must be entered by the close of the Adjustment Period for the effective Operating Hour and shall become an Obligation at the close of the Adjustment Period.  However, Balancing Energy Service provider bids may be withdrawn at any time prior to the close of the Adjustment Period.  The portion of a QSE’s Balancing Energy Service Up bid deployable in one interval that may be provided by off-line Generation Resources shall be limited to no more than the aggregate of qualified output amounts from Quick Start Units which have been demonstrated via the qualification testing process described in the Operating Guides.  The QSE may utilize any remaining capacity from Quick Start Units in subsequent intervals once the Quick Start Units are online.

Reference:  Protocols Section 6.10.3, Ancillary Services Qualification and Portfolio Test Methods

Only QSEs that have been qualified and tested may be used to provide Ancillary Services.  ERCOT shall develop and operate its qualification and testing program to meet the following requirements for each Ancillary Service.

A QSE shall be qualified and tested to provide Service prior to initial operation and every five years thereafter.  ERCOT is authorized to call up to two unannounced, unscheduled qualification tests after presenting to the QSE supporting information of an indication that a Resource may not be able to meet its stated Net Dependable Capability during any calendar year.

QSEs may qualify by using either Generation Resource(s) or Load(s) Acting as a Resource (LaaR(s)).  If a QSE qualifies by using only a LaaR then the QSE may only provide Ancillary Services using LaaRs and will not be qualified to provide Ancillary Services using Generation Resources.  However, if a QSE successfully completes the qualification using Generation Resource(s), that QSE will be qualified to provide Ancillary Services from both Generation Resources and LaaRs.

ERCOT may grant a “Provisional Qualification,” for a period not to exceed ninety (90) days, to a QSE that has performed an Ancillary Service qualification test (or tests) in good faith but failed to qualify due to problems that, in the sole discretion of ERCOT, are determined to be non-critical for the purpose of providing one or more Ancillary Services.  Notwithstanding the failure of a QSE with Provisional Qualification to meet the applicable Ancillary Service criteria, such QSE may provide such Ancillary Service to the extent permitted by the terms of the Provisional Qualification.

Reference:  Protocols Section 6.10.3.4, Balancing Energy

(1)	Testing using Generation Resource(s)

(a)	A test for Balancing Energy Service shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE, ERCOT shall notify the QSE using ERCOT’s Messaging System requesting it to provide an amount of Balancing Energy.  The QSE shall acknowledge the start of the test.  During the sixty (60) minute duration of the test, within the limits of requested qualification, ERCOT will vary the requested amount of Balancing Energy requested.

(d)	On successful demonstration of all test criteria, ERCOT shall qualify the QSE is capable of providing Balancing Energy and shall provide a copy of the certificate to the QSE.

For purposes of testing Quick Start Units providing Balancing Energy Service, ERCOT will test each unit by issuing a unit-specific Dispatch Instruction for the MW amount that the QSE requesting to have the Quick Start Units be qualified to provide.  ERCOT’s procedures for testing Quick Start Units providing Balancing Energy Service shall be consistent with the ERCOT Protocols Sections 6.10.3, Ancillary Services Qualification Criteria and Portfolio Test Methods, and 6.10.3.4, Balancing Energy Qualification and Testing Criteria.  The Quick Start Units will be qualified to provide only the output amount observed at the end of the ten-minute Balancing Energy ramp period.

## 2.6	Changes in System Status

### 2.6.1	Changes in Resource Status

Reference:  Protocols Section 5.5.1, Changes in Resource Status

The QSE will notify ERCOT of an unplanned change in Resource status as soon as practicable following the change. The QSE representing the Resource will report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status.

### 2.6.2	Changes in Transmission Facility Status

Reference:  Protocols Section 5.5.2, Changes in Transmission Facility Status

The TDSP will notify ERCOT of any changes in status of Transmission Facility elements as provided and clarified in the ERCOT procedures.  The TDSP will notify ERCOT of any other Transmission Facility status as soon as practicable following the change.  In addition, any short-term inability to meet minimum TSP or DSP reactive requirements shall be immediately reported to ERCOT by way of the TSP.

## 2.7	Outage Coordination

### 2.7.1	ERCOT Control Area Authority Responsibilities

The following table outlines the action to be taken by ERCOT Control Area Authority as a result of various Outage events:

| EVENT | CONTROL AREA AUTHORITY ACTION |
| --- | --- |
| Submission of schedules for Planned Outages and Maintenance Outages of Transmission Facilities. | Evaluation of all Planned Outages and Maintenance Outages to ensure the Outage does not result in a violation of the security criteria. |
| Submission of Planned Outages and Maintenance Outages of Reliability Must Run (RMR) Units. | Evaluation of all Planned Outages and Maintenance Outages to ensure the Outage does not result in a violation of the security criteria. |
| Submission of Black Start Unit Outages | Evaluation of all requested Planned Black Start Outages to ensure that unavailability may not cause a violation of the security criteria and that a valid methodology of restoring ERCOT from black start conditions without the requested unit exists (Subject to the terms of the applicable Black Start Agreement) per Section 8.1.1 of the ERCOT Protocols. |
| Transmission Facility Forced Outages and resultant maintenance on related facilities. | Evaluate the impact of Forced Outage on the ERCOT System, perform constraint analysis and implement changes to generation or transmission to restore or maintain secure operating conditions. Previously approved transmission outages may be adjusted or withdrawn if necessary. (Per Section 8.5 of the ERCOT Protocols) |
| Receipt of schedules of Planned Outages for Resources; | Monthly – prepare an assessment of Load vs. Available capacity by Congestion Zone by week for the next 52 weeks, including the effects of commercial constraints. Post the adequacy of supply for each Congestion Zone on the MIS. |

### 2.7.2	Forced Outages

#### 2.7.2.1	Energy Resources

The Control Area Authority shall be advised of all Forced Outages of ANY energy resource with a capability greater than 10 MW within one minute.

#### 2.7.2.2	Transmission

Forced Outages of transmission lines and other lines or equipment that affect power flows or transfer capacity will be reported immediately by the TDSP to the ERCOT System Operator.

The TDSP may be required to provide ERCOT supporting information justifying the removal of transmission equipment from service according to Section 8.5 of the ERCOT Protocols.

When a Forced Outage affects ERCOT, ERCOT shall take immediate remedial steps to ensure that other facilities are not loaded beyond security limits.

#### 2.7.2.3	Sabotage Information Exchange

A TDSP, QSE, PGC or any ERCOT entity shall inform the ERCOT operator when:

- It is suspected or identified that multi-site sabotage has occurred

- It is suspected or identified that a single-site sabotage of a critical facility has occurred.

ERCOT shall inform NERC and governmental agencies of the threat in accordance with current laws and regulations.

The ERCOT operator may inform other TDSPs or QSEs of the event(s), if, in the opinion of ERCOT, the situation impacts ERCOT System reliability or security.

### 2.7.3	Scheduled Outages

#### 2.7.3.1	Generation

ERCOT Control Area Authority will record and monitor each Resource Entity’s annual maintenance schedule for all generating units owned or operated by the Resource Entity that are within the ERCOT System, as part of ERCOT Control Area Authority overall system reliability analysis.

ERCOT Control Area Authority shall have the option of approving or rejecting a Planned Outage or a Maintenance Outage, prior to the removal from service of a RMR, a Synchronous Condenser Unit or Black Start Resource.

#### 2.7.3.2	Transmission

ERCOT Control Area Authority shall coordinate all proposed maintenance of all lines or equipment that affects power flows or transfer capacity of the ERCOT System.

ERCOT Control Area Authority, jointly with TDSPs shall attempt to minimize the effect of simultaneous outages of lines on the reliability of ERCOT.  ERCOT Control Area Authority will establish priorities, when necessary, in accordance with the following to provide adequate time for required maintenance.

When a request for removal of transmission equipment from service is received, ERCOT should conduct studies prior to approval to demonstrate that:

- The capacity of remaining ERCOT transmission equipment shall not be exceeded.

- ERCOT shall remain single contingency secure.  Remedial Action Plans may be depended upon to recover from overloads under some contingency conditions.

- ERCOT may limit the loading on generating units to a value that can be delivered by remaining transmission lines.

## 2.8	Congestion Management

### 2.8.1	Overview of ERCOT Coordinated Congestion Management

Reference:  Protocols Section 7.1, Overview of ERCOT Congestion Management

ERCOT employs a Zonal Congestion management scheme that is flow-based, whereby the ERCOT Transmission Grid, including attached Generation Resources and Load, will be divided into a predetermined number of Congestion Zones.  Each Congestion Zone is defined such that each Generation Resource or Load within the Congestion Zone boundaries has a similar effect on the loading (Shift Factor) of Transmission Facilities between Congestion Zones.  For purposes of solving Zonal Congestion the Shift Factor will be assumed the same for: (i) all Generation Resources deemed likely to vary their output and (ii) Loads within a Congestion Zone.  Therefore any imbalance between Loads and Generation Resources in a Congestion Zone will be deemed to have the same impact on a given loading between Congestion Zones.

This Congestion management scheme applies zonal Shift Factors, determined by ERCOT, to predict potential Congestion on CSCs under the known topology of the ERCOT System.  The zonal Shift Factors determined by ERCOT should most closely represent the effect of Generation Resources deemed likely to vary their output and Loads in the Congestion Zone on the CSCs with the current topology of ERCOT System.  This scheme is used in the Day Ahead and Adjustment Periods to evaluate potential Congestion and notify Market Participants accordingly.  ERCOT also uses this scheme, along with other factors, to determine if it should procure Replacement Reserve Service in a Congestion Zone to provide additional Balancing Energy Service to solve expected Congestion.  ERCOT will use monthly zonal Shift Factors to post and analyze the Schedule impact on CSCs until it implements calculations of interval Shift Factors in the system.

ERCOT will manage transmission Congestion and categorize the cost of Congestion management as either Zonal Congestion management costs or Local Congestion management Costs.  Zonal Congestion management costs are those costs attributable to managing Congestion on CSCs or predefined Closely Related Elements (CRE).  The costs of managing Zonal Congestion will be directly assigned to QSEs based on the impact of each QSE’s portfolio on CSCs.  All other Congestion management costs are considered Local Congestion management costs.

ERCOT will use the Zonal Congestion management model with Shift Factors of Generation Resources and Loads on CSCs and zonal Balancing Energy Service MCPEs to determine the Shadow Prices of energy across corresponding CSCs.   In addition, ERCOT will directly assign to QSEs the costs of any Replacement Reserve Service procured on a zonal basis for Congestion management purposes.  ERCOT will use these Shadow Prices in settlement to directly assign to QSEs the cost of managing Zonal Congestion to QSEs.

The Local Congestion management scheme relies on a more detailed Operational Model to determine how each particular Resource or Load impacts the transmission system.  This model does not use portfolios and uses the current known topology of the transmission system.

ERCOT will uplift the cost to solve Local Congestion pro rata to each QSE based on its Load Ratio Share.

ERCOT will manage Congestion by:

(1)	Evaluating the levels of Zonal Congestion and any other Congestion during the Day Ahead, the Adjustment Period and the Operating Period using appropriate models of the ERCOT Transmission Grid;

(2)	Examining the impacts of QSE energy schedules on CSCs;

(3)	Posting on the MIS, the total megawatt quantity impacts on every CSC, and allowing QSEs to adjust schedules to mitigate potential Congestion on the CSCs;

(4)	Procuring during the Adjustment Period, as needed, Replacement Reserve Service (RPRS) to use with other Resources for which QSEs have submitted Balancing Energy bids to provide sufficient capacity for Balancing Energy flows in the Operating Hour while respecting operational limits of the ERCOT Transmission Grid;

(5)	Determining settlement for QSEs providing RPRS procured to manage Congestion; and

(6)	Determining settlement for QSEs providing Balancing Energy associated with resolving Zonal Congestion.

ERCOT will carry out these steps in accordance with this Section and the Scheduling and Ancillary Service Scheduling and Selection requirements in Sections 4 and 6, respectively.

## 2.9	Requirements for Under-Frequency Relaying

### 2.9.1	Automatic Firm Load Shedding

At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.  The under-frequency relays shall be set to provide load relief as follows:

| Frequency Threshold | Load Relief |
| --- | --- |
| 59.3 Hz | 5% of the ERCOT System Load (Total 5%) |
| 58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%) |
| 58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%) |

The Control Area Authority will, prior to the peak each year, survey each TDSP’s compliance with the automatic load shedding steps above, and report its findings to the Technical Advisory Committee of ERCOT.  For minimum compliance, TDSPs are obligated to meet the prescribed percent values at all times.  It is not permitted to use rounding off to meet the minimum.  ERCOT will direct a review of the automatic firm load shedding program whenever warranted by conditions in the ERCOT System.  At a minimum, this review will follow the Reliability and Operations Subcommittee (ROS) directed dynamic simulations of automatic firm load shedding conducted at five-year intervals beginning in the summer of 2001.

TDSPs shall ensure, to the extent possible, and under the direction of the Control Area Authority, that load equipped with under-frequency relays are dispersed geographically throughout the ERCOT System to minimize the impact of load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which LSE serves the customer.  TDSPs shall ensure that the under-frequency relays connected to each load will operate with a fixed time delay of no more than 30 cycles. Total time from the time when frequency first reaches one of the values specified above to the time load is interrupted should be no more than 40 cycles, including all relay and breaker operating times. If the frequency drops below 58.5 Hz, the ERCOT System Operator shall determine additional steps to continue operation.

If a loss of load occurs due to the operation of under-frequency relays, a TO may rotate the physical load interrupted to minimize the duration of interruption experienced by individual customers or to restore the availability of under-frequency load-shedding capability; however, in no event shall the initial total amount of load without service be decreased by a TO without the approval and direction of the ERCOT System Operator.  TOs, directed by the Control Area Authority, shall make every reasonable attempt to restore load, either by automatic or manual means, to preserve system integrity.  This will allow load equipped with under-frequency relays to be available for interruption should there be a  subsequent under-frequency event.  TDSPs shall exercise extreme caution in restoring load so that the capability limits of generating units and transmission lines are not exceeded.

Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of Step 4 of the Emergency Electric Curtailment Plan.

### 2.9.2	Generators

If under-frequency relays are installed, these relays shall be set such that the automatic removal of individual generating units from the ERCOT System meet the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (Continuous operation) |
| Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

No prearranged instruction that conflicts with the above limits will be given for the manual removal of an otherwise operable generating unit.  This Operating Guide is not intended to conflict with the plant operator's responsibility to protect generating units from potentially damaging operating conditions.  While this guide does not address the removal of generating units for frequency deviations above 60 Hz, it is realized that the generating unit operating restrictions below 60 Hz apply equally to operation of a generating unit above 60 Hz.

## 2.10	System Voltage Profile

### 2.10.1	Introduction

The System Voltage Profile is a predetermined distribution of desired nominal voltage set points across the ERCOT System.

ERCOT shall coordinate and conduct studies with the TDSPs to determine the normally desired Voltage Profile for all Generation Resource busses in the ERCOT System.

ERCOT shall establish and update Voltage Profiles at points of interconnection of Generation Resources to maintain system voltages within established limits.

### 2.10.2	Maintaining Voltage Profile

ERCOT has the responsibility for monitoring the Voltage Profile within their Transmission System.  ERCOT has the responsibility to control the Voltage Profile and should use the following guides to maintain the Voltage Profile:

| FUNCTION | ACTION |
| --- | --- |
| Operations Engineering | - All voltage limits must be based on sound engineering studies that use current network models. TDSP study results should be made available to the Control Area Authority. - Transfer limits shall reflect voltage and/or reactive restrictions. |
| Coordination | - Entities must coordinate high voltage limits in order to guarantee that the Maximum Continuous OverVoltage (MCOV) of equipment is not exceeded. TDSPs shall notify ERCOT of all limits. - Low voltage limits must be coordinated in order to prevent one Entity from being a burden to another. - Voltage limits shall not be violated during all normal and first contingency conditions. - The operation of all Reactive Power devices under the control of a Transmission Operator or a QSE will be coordinated under the direction of ERCOT to maintain transmission voltage levels established by ERCOT. Static reactive devices will be managed to ensure that adequate dynamic Reactive Reserves are maintained at all times. |
| Notification | - Generation Resources with voltage problems shall notify their host TDSP. TDSPs shall notify other affected TDSPs and the Control Area Authority for any voltage problem potentially affecting interconnected operations. - The Control Area Authority will monitor actions and may request assistance to solve the problems to assure the reliability of the interconnection. |
| Response | - When the voltage levels deviate from established limits, ERCOT Control Area Authority shall take immediate steps to relieve the condition using all available reactive resources. |
| Monitoring | - TDSPs shall provide telemetry to the Control Area Authority that monitors all major transmission bus voltages. A routine schedule shall be maintained by the TDSP to calibrate the telemetry. |
| Controls | - ERCOT Control Area Authority must be aware of the locations of available reactive capability. - ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows. - Controls to maintain Voltage Profiles may include capacitor switching, reactor switching, autotransformer tap changing, generator reactive Dispatch, transmission line switching, and Load shedding. |
| Documentation | - Each TDSP must maintain a voltage/reactive plan for normal and Emergency Conditions. This document shall be provided to adjacent TDSPs as well as ERCOT Control Area Authority. |
| Emergency or Abnormal Conditions | - Transmission systems shall be designed so that effective Reactive Reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions. - Major transmission lines shall be kept in service during light Load as much as possible. Lines can only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded. - Voltage reduction shall not be done on the transmission system unless coordinated with adjacent TDSPs. |

### 2.10.3	Special Consideration for Nuclear Power Plants

In all planning studies and Real Time operations, ERCOT and TDSPs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission.  ERCOT shall notify the QSE representing a nuclear power plant of the result of any studies where the voltage at the plant switchyard cannot be adequately maintained.  The TDSP shall monitor the voltage in Real Time and provide notice to the QSE representing the nuclear power plant of any voltage inadequacy at the plant switchyard that cannot be corrected within 30 minutes.  High and low limits on switchyard voltage at each nuclear power plant necessary to meet these requirements shall be specified in ERCOT Procedures.

### 2.10.4	Reactive Considerations for Gas and Steam Turbine Power Plants

Reference:  Protocols Section 6.5.7.2, QSE Responsibilities

(7)	QSE shall advise ERCOT Operations whenever their Generation Resources are not operating at a power factor level as specified in the Operating Guides.  Upon such notice, ERCOT Operations, in conjunction with the appropriate TSP, shall investigate the situation with the goal of restoring the reported unit’s operation to within the specified power factor range.  Actions that ERCOT may take include the addition or removal of transmission reactive devices to/from service or a request to another Generator Resource within electrical proximity for the production of leading or lagging VARS (as appropriate) so as to equitably share the need for voltage support among Generation Resources.  Requests arising within the context of this subsection may not result in the operation of a Generation Resource outside of the specified reactive operating range.  Accordingly, Generation Resources are expected to voluntarily comply with these requests.  Nothing in this subsection is meant to supersede ERCOT’s Dispatch authority in the event of emergency operations.

Reference:  Protocols Section 6.10.9, Reactive Power Supply from Generation Resources Required to Provide VSS Performance Criteria

(4)	Except under Force Majeure conditions or ERCOT-permitted operation of the generating unit, if a Generation Resource required to provide VSS fails to maintain transmission system voltage at the point of interconnection with the TSP within two percent (2%) of the scheduled voltage while operating at less than the maximum reactive capability of the generating unit, ERCOT may, at its discretion, report this to the ERCOT Compliance Office.

#### 2.10.4.1	Maintaining System Voltage

Each generator shall attempt to maintain the Voltage Profile. Although the generator shall maintain the voltage to the best of its ability within the limits of the individual machine, the TDSP, to which the generator is connected, shall monitor and direct, by communicating with the Generation Resource (at the discretion of the Generation Resource) or the QSE responsible for operation of the Generation Resource, the reactive output of the machines having direct effect on the local system voltage.  Under TDSP declared emergency conditions, TDSPs may directly dispatch the reactive output of the Generation Resource and follow up with notification of the QSE.  The TDSP will, using Good Utility Practices, equalize the reactive output of the generators based on size (net dependable MW capability), reactive capability, reactive limits and system voltage impact.

#### 2.10.4.2	Unit Dispatch Beyond the Unit Reactive Limit

Each generator shall respond to ERCOT instructed voltage control, including exceeding its URL, as specified in Protocol Section 6.8.4, Capacity Payments for Voltage Support Provided to ERCOT.  For multi-generator busses, ERCOT shall not instruct any single generator to operate beyond its URL until all generators on line and interconnected at the same transmission bus have been instructed to their respective URLs.

## 2.11	External Control Area Inter-Ties

Reference:  Protocols Section 4.4.18.5, Inadvertent Energy Account

Any difference between the net of deemed meter readings at the DC Tie and the actual metered value at the DC Tie will be tracked in an Inadvertent Energy Account between ERCOT and each interconnected non-ERCOT Control Area.  ERCOT will coordinate operation of the DC Tie(s) with the DC Tie Operator such that the Inadvertent Energy Account is maintained as close to zero as possible.  Corrections of inadvertent energy between ERCOT and the interconnected non-ERCOT Control Areas will be in accordance with the NERC scheduling protocols and the Operating Guides.

### 2.11.1	Control Area Operations

Control Area schedules between the ERCOT Control Area and interconnected non-ERCOT Control Area(s), through the use of schedules over Direct Current Tie(s), will be implemented in accordance with the ERCOT Protocols, North American Electric Reliability Council (NERC) scheduling protocols, and in compliance with NERC operating policies. Scheduling must also be in accordance with any applicable Federal Energy Regulatory Commission tariffs.

ERCOT Control Area Authority will perform schedule confirmation with the applicable interconnected non-ERCOT Control Area(s) and will coordinate the approval process for the NERC tags as both the ERCOT Control Area and on behalf of ERCOT Transmission Service Providers.

### 2.11.2	Operation of DC Ties

ERCOT Control Area Authority will confirm interconnected non-ERCOT Control Area schedule profiles with the DC Tie operator, who will control the tie to the schedules agreed to by both the designated Security Coordinator for the interconnected non-ERCOT Control Area and ERCOT.

Exports from ERCOT via DC Ties will be treated as a Load connected at transmission voltage.

Imports into ERCOT via DC Ties will be treated as generation injection located at the DC tie point.

Any changes in the interconnected non-ERCOT Control Area schedules due to a de-rating of the tie or other change within the NERC scheduling protocols will be communicated to ERCOT by the DC Tie Operator or designated security coordinator for the interconnected non-ERCOT Control Area.

ERCOT Control Area Authority will coordinate operation of the DC Tie(s) with the DC Tie Operator such that the Inadvertent Energy Account is maintained as close to zero as possible.

## 2.12	Document Control

Change History

| Issue/Date | Reason for issue |
| --- | --- |
| Version 0.1 November 30, 2000 | Draft for Review |
| Version 0.2 December 29, 2000 | Include Version 0.1 comments, Moved attachments to Appendix C, Discussion and Review by peer group |
| Version 0.3 January 19, 2001 | Include comments from seminar |
| Version 0.4 February 5, 2001 | Include comments from second seminar |
| Version 1.0 February 28, 2001 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee |
| February 1, 2003 | OGRR123 – Section 2.5.2.4, increases the amount of interruptible load on high-set under frequency relays (UFR) participation Resources can provide Responsive Reserve Service from 25% to 35%. |
| March 1, 2003 | Revised header to state “Section.” |
| April 1, 2003 | OGRR124 revised Sections 2.4.2 & 2.8 to update Protocols references. |
| May 1, 2003 | OGRR127 updated reference to Protocols Section 5.5.2 and deleted duplicate text after reference. Also update references to OG Section 6. |
| September 1, 2003 | OGRR130 updated Section 2.2.4; OGRR131 updated Section 2.5.2.3, adds Sections 2.5.3 and 2.5.4. |
| November 1, 2003 | OGRR137 deleted Section 2.5.2.4. |
| April 1, 2004 | OGRR141 updated all of Section 2 with corrections and clarifications. OGRR142 updated Section 2.1. |
| May 1, 2004 | OGRR144 updated Section 2.9.2. |
| June 1, 2004 | OGRR145 |
| February 1, 2005 | OGRR158 |
| April 1, 2005 | OGRR159 |
| May 1, 2005 | OGRR149 added as boxed language; OGRR156 |
| June 1, 2005 | Admin OGRR168 |
| July 1, 2005 | Admin OGRR170 |
| September 1, 2005 | OGRR167, OGRR173 |
| November 1, 2005 | Admin OGRR177 |
| December 1, 2005 | OGRR171 |
| February 1, 2006 | Admin OGRR180 |
| April 1, 2006 | OGRR174, Admin OGRR183 |