## Slide 1
Entergy Texas Integration Study
Status Report
TAC Briefing
4/7/2006
Bill Bojorquez
ERCOT

## Slide 2: Caveats
This status report on the initial studies is intended solely to provide an initial indication of the level of projects required; the information provided herein is preliminary and several additional studies are recommended
The integration of Entergy TX into ERCOT may defer or eliminate currently-planned standalone projects, the savings of which would offset the costs shown herein
This study does not address the requirements to integrate Entergy into ERCOT’s operations and market systems

## Slide 3: Scope of Study
Determine minimum set of upgrades necessary to integrate Entergy Texas system into ERCOT
  Meet ERCOT thermal reliability criteria
  Allow generation redispatch to resolve constraints where feasible
Evaluate costs and benefits of additional economically-driven transmission upgrades
  Minimize sum of cost of upgrades and dispatch
  With Lewis Creek and Sabine units available and unavailable
Voltage and transient stability studies will need to be performed to evaluate whether additional upgrades are required to meet reliability criteria

## Slide 4: Initially-Identified Upgrades
Nacogdoches-Lufkin
Lufkin-Cypress
150MW DC Tie at Crockett
Lewis Creek-Grimes (2)
Lewis Creek-Porter 230kV
China-Cedar Bayou
Cypress-China
300MW DC Tie
at Hartburg
Sabine-Hartburg
China-Sabine

## Slide 5: Study Outcome Summary
Close Breakers & 150MW Crockett tie
Insecure
Add LC-Grimes
No LC nor
Sabine -
Insecure
Secure
Other Options
Insecure
$141M Cap
Add Lufkin-Cypress &
CBY-China
$291M Cap
Add Naco-Lufkin
-$20 M PC
$10M Cap
Total Capital
$426 M
Secure
Add Lufkin-Cypress & Hartburg 300MW tie
$166M Cap
Add Cypress -China
-$8 M PC
$33 M Cap
Total Capital
$459 M
$18M Cap
$257M Cap
Total Capital
$325 M
w/LewisCk
& Sabine -
Secure
Add Naco-Lufkin-Cypress
-$28.5 M PC
$140 M Cap
Total Capital
$299 M
Add Cedar Bayou-China
-$48 M PC
$127 M Cap
Total Capital
$286 M
Add CBY-China and China-Cypress
-$34.5 M PC
$160 M Cap

## Slide 6: Initially-Identified Upgrades
Nacogdoches-Lufkin
Lufkin-Cypress
150MW DC Tie at Crockett
Lewis Creek-Grimes (2)
China-Cedar Bayou
Cypress-China
300MW DC Tie
at Hartburg

## Slide 7: Follow-Up Studies Recommended
If the PUCT directs ERCOT to perform additional studies, the following are recommended:
  Dynamic and voltage stability studies
  Evaluate alternative projects not included in initial analysis
  Longer-term study, including load growth
  Consider standalone projects that would be deferred or eliminated