## ERCOT Operations Report

## ROS & OWG

## April 2006

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 4/9/ 6:07 | 60.105 | 22538 | -683 | 933 | 2111 (607) |
| 4/13 16:50 | 59.829 |  |  |  | 3 units, 690 MW |
| 4/17 15:34 | 59.830 | 51900 | 1029 | -233 | Capacity |
| 4/17 16:13 | 59.782 | 52133 | 1030 | -689 |  |
| 4/28 5:41 | 59.854 |  |  |  | 540 MW unit |
| 4/29 3:09 | 59.855 |  |  |  | 540 MW unit |

Deployed Responsive (21) (Reported Above)

| 4/1 7:05 | 4/9 15:39 | 4/17 14:29 |
| --- | --- | --- |
| 4/2 18:02 | 4/9 21:22 | 4/17 16:04 |
| 4/2 22:03 | 4/9 22:05 | 4/23 6:04 |
| 4/3 6:24 | 4/13 6:09 | 4/23 22:04 |
| 4/6 19:58 | 4/13 16:50 | 4/26 22:00 |
| 4/7 14:02 | 4/15 22:00 | 4/28 5:41 |
| 4/8 22:04 | 4/16 16:05 | 4/29 3:09 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Apr 05 | Mar 06 | Apr 06 |
| --- | --- | --- | --- |
| DFW | 33 | 1 | 23 |
| E RIO | 40 | 85 | 166 |
| W RIO | 29 | 75 | 194 |
| Laredo | 37 | 59 | 66 |
| Bryan Area | 2 | 30 | 61 |
| Corpus | 30 | 1 | 1 |
| North | 0 | 0 | 9 |
| San Antonio | 1 | 26 | 17 |
| Western | 2 | 0 | 20 |
| Austin | 0 | 0 | 18 |
| Northeast | 0 | 0 | 12 |
| South | 0 | 0 | 19 |
| Houston | 2 | 0 | 49 |
|  | 176 | 297 | 655 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overload | Days |
| --- | --- | --- |
|  | South - Houston | 19 |
|  | Valley Import | 13 |
| Gibbons Creek - Bryan Greens Prairie & Gibbons Creek - East 138 kV | Dansby - Atkins 138 kV | 8 |
|  | North - Houston | 8 |
| Marion - Zorn & Clear Springs 345 kV | Seguin - Seguin West 138 kV | 7 |
| Parker Switch - Eagle Mountain & Parker Switch - Roanoke Switch 345 kV | Benbrook 345/138 auto #1 | 7 |
|  | Northeast - North | 7 |
| North Edinburg - Rio Hondo 345 kV | Mvec Weslaco- Weslaco 138 kV | 6 |
| Rio Hondo Auto 345/138 kV | MV Weslaco - MV Heidelburg 138 kV | 5 |
| Marion - Hill Country & Skyline 345 kV | Raymond Barker - Verde Creek | 4 |
| Odessa - Moss 138 kV | General Tire Switch - Olefin Switch | 4 |
| STP - Skyline & Hill Country 345 kV | Blessing - Lolita 138 kV | 4 |
| Bluff Creek - Oak Creek 138 kV | Abilene South - Buffalo Gap 138 kV | 3 |
| Menard Auto | Ballinger to Paint Rock 69 kV | 3 |
|  | North - West | 3 |
| Anna Sw-Valley SES 345 kV | Paris Ws 345/138 kV auto | 2 |
| Clearsprings - Marion - Zorn 345 kV | Henne - Comal 138 kV | 2 |
| Ennis Sws - Ennis West 138 kV | Ennis - Ennis West 138 kV | 2 |
| Hill Country & STP 345 kV | Marion - Skyline 345 kV | 2 |
| Morgan Creek Auto-1 345/138 kV | Morgan Creek Auto-2 | 2 |
| North Edinburg - Rio Hondo 345 kV | MVEC Weslaco - Heidburg 138 kV | 2 |
| Odessa EHV 345/138 kV auto | Nylon Tap - Olefin Switch 138 kV | 2 |
| San Angelo to Menard 138 kV | Ballinger to Paintrock 69 kV | 2 |
| Stryker - Trinidad 345 kV | Athens North Switch - Athens | 2 |
| Temple - Lake & Tradinghouse 345 kV | Goldthwaite 138/69kV auto | 2 |
| Zorn - Haysen 345 kV | Raymond - Verde Creek | 2 |
| Lake Pauline 138/69 kV auto | Chillicothe - Vernon 69 kV | 2 |
| Allen-Renner & Plano Tennyson 345 kV | Allen Sws - Plano Parker 138 kV | 1 |
| Bowie Auto overloads 138 kV | Rhome to Chisam 1 | 1 |
| Coleto Creek-Kennedy Sw | Leon Crk-Pleaston 138 | 1 |
| Comanche Peak 1- 2 | Uvalde - Asphalt Mines 138 kV | 1 |
| Eagle Mountain SES 345/138 T1 auto | Eagle Mountain - Azle | 1 |
| Fisher Road - Bowman 345kV | Wichita Falls - Grayback 138kV | 1 |
| Hamilton Rd-Sonora 138 kV | Ft Lancaster-Illinois 4 69 kV | 1 |
| Holly-Fiesta | Pedernales Xmfr. | 1 |
| Jack County - Bowie TMPP 138 kV | Azle - Eagle Mountain 138 kV | 1 |
| Jack County to Bowie 138 kV | Agnes Switch - Weatherford Tap | 1 |
| Jack County - Bowie TMPP 138 kV | Weatherford Switch - Flat Rock Tap | 1 |
| Lake Pauline - Vernon 138 kV | Chillicothe - Vernon 69 kV | 1 |
| Lytton Springs - Zorn & Austrop - Zorn 345 kV | San Marcos - Canyon LCRA | 1 |
| Marion - Hill Country - Skyline 345 kV | Verde Creek - Bandera LCRA 138 kV | 1 |
| Marion - Hill Country - Skyline 345 kV | Schertz - Parkway 138 kV | 1 |
| Marion - Zorn & Clear Spring 345 kV | Raymon Barker-Verde Creek 138 kV | 1 |
| North Edinburg - Rio Hondo 345 kV | South McAllen - Las Milpas 138 kV | 1 |
| Pleasanton - Moore 138 kV | Dilley - Pearsal 69 kV | 1 |
| Rio Hondo 345/138 auto | Weslaco - Weslaco Switch 138 kV | 1 |
| Sonora - Friend Ranch 138 kV | Friend Ranch - Crockett Heights 69kV | 1 |
| Sonora-Friend Ranch 138 kV | Ozona-Friend Ranch 69 kV | 1 |
| STP-Dow 345 kV | Macadonia - Seaway LCRA 138 kV | 1 |
| Stryker Creek - Trinidad 345kV | Stryker Creek - Summerfield Tap | 1 |
| Stryker Creek 345/138 auto | Stryker Creek - Dialville 138 kV | 1 |
| Vernon - Lake Pauline 138kV | Chillicothe - Vernon 69kV | 1 |
| Menard - Gillespie LCRA 138kV | Menard auto | 1 |
| Skyline - Marion and STP 345kV | Marion - Hill Country 345kV | 1 |
|  | West - North | 1 |

New RAP

- Goldthwaite – Evant 138 kV loads Goldthwaite 138/69 kV Tr.

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 04/18/2006 | SPS Intervention - Transmission & Security Desk | 256 |
| 04/12/2006 | Bulletin 255 - Shift Supervisor Desk V3R24 | 255 |
| 04/05/2006 | VDI - JOU - Frequency Control Desk | 254 |
| 04/05/2006 | VDI - JOU - Transmission & Security Desk | 253 |
| 04/03/2006 | New Generator Synchronization Procedure posted | 252 |

Blackout/Load Shed incidences

4/17	implemented EECP

Major system voltage problems

None

Voltage Instructions

4/18	14:20	Raise instruction given in the South Zone.

Corpus Christi RMR status summary

5/19	90-day Notification of RMR contract termination expires.

Major Computer Problems, Enhancements & Fixes

None

Communication

None

ERCOT peak (Unofficial)

4/18	52,228	17:00

Alerts, OCN, and Emergency Notices

| 1-Apr | 12:20 | 24:00:00 | Transmission Alert | Loss of North Edinburg - Rio Hondo 345 kV loads Mvec Weslaco- Weslaco 138 kV. |
| --- | --- | --- | --- | --- |
| 2-Apr | 10:00 | 24:00:00 | Transmission Alert | Loss of North Edinburg - Rio Hondo 345 kV loads Mvec Weslaco- Weslaco 138 kV. |
| 4-Apr | 2:00 | 3:00 | OCN | Capacity Insufficiency HE 15 to 23:00 |
| 4-Apr | 3:00 | 09:00 | Alert | Capacity Insufficiency HE 15 to 23:00 |
| 4-Apr | 19:00 | 22:00 | Transmission Emergency | Post Contingency Overload in Del Rio Area |
| 5-Apr | 19:00 | 22:00 | Transmission Emergency | Post Contingency Overload in Del Rio Area |
| 6-Apr | 19:00 | 22:00 | Transmission Emergency | Transmission Emergency Notice - Post Contingency Overload in Del Rio Area |
| 7-Apr | 15:00 | 24:00:00 | Transmission Alert | Loss of North Edinburg - Rio Hondo 345 kv overloads cross valley 138 kv. |
| 7-Apr | 17:00 | 23:00 | Transmission Alert | Loss of San Miguel 138/69 kV tr loads Derby-Pearsall 69 kV. |
| 11-Apr | 7:51 | 10:28 | Transmission Alert | Loss of BP Chemical Vistron to North Carbide 138 kV will result in islanding and possible loss of load at BP Chemical Vistron. |
| 11-Apr | 7:39 | 10:28 | Transmission Emergency | Loss of Amoco Chocolate Bayou to Webster 138 kv will result in an islanding and possible loss of load at Amoco Chocolate Bayou. |
| 11-Apr | 8:47 | 10:28 | Transmission Alert | Loss of Diamond Shamrock Battleground to SR Bertron 138 kV will result in islanding and possible loss of load at Diamond Shamrock Battleground. |
| 12-Apr | 19:00 | 23:00 | Transmission Emergency | Post Contingency Overload in Del Rio Area. |
| 16-Apr | 13:20 | 18:30 | Transmission Alert | Loss of Lake Pauline 138/69 kV tr overloads Vernon - Chillicothe 69 kV |
| 17-Apr | 15:25 |  |  | Implemented Step 1 of the Emergency Electric Curtailment Plan |
| 17-Apr | 15:34 |  |  | Step 2 of the Emergency Electric Curtailment Plan and deployed 1150 MW of LaaRs |
| 17-Apr | 16:13 |  |  | Step 4 of the Emergency Electric Curtailment Plan and shed 1000 MW's of firm load |
| 17-Apr | 18:10 |  |  | All firm load restored |
| 17-Apr | 18:26 |  |  | From Step 4 to Step 2 of the Emergency Electric Curtailment Plan and picked up LaaRs |
| 17-Apr | 18:48 |  |  | From Step 2 to Step 1 of the Emergency Electric Curtailment Plan |
| 17-Apr | 19:20 |  |  | Ended Emergency Electric Curtailment Plan |
| 17-Apr | 14:30 | 19:40 | Transmission Alert | Loss of Somerset - Lytle 138 kV loads Leon Creek - Pleasanton 138 kV |
| 17-Apr | 14:30 | 19:40 | Transmission Alert | Loss of Sterrett tr loads Corsicana - Rice 69 kV |
| 17-Apr | 14:30 | 22:50 | Transmission Alert | Loss of Pleasanton - Moore 138 kV loads Dilley - Pearsall 69 kV |
| 17-Apr | 14:30 | 19:40 | Transmission Alert | Loss of Parker - Eagle Mountain & Parker - Roanoke 345 kV loads Benbrook rr |
| 17-Apr | 14:30 | 22:50 | Transmission Alert | Loss of STP - Dow 345 kV loads Mill Creek - Gay Hill 138 kV |
| 17-Apr | 14:30 | 22:50 | Transmission Alert | Loss of North Edinburg - Rio Hondo 345 kV loads MVEC Weslaco - Heidburg 138 kV |
| 17-Apr | 14:30 | 24:00:00 | Transmission Alert | Loss of Lake Pauline - Vernon 138 kV loads Vernon - Chillicothe 69 kV |
| 17-Apr | 20:00 |  | Alert | Opened Adjustment Period Replacement Market |
| 18-Apr | 0:15 | 2:45 | Transmission Alert | Loss of Lake Pauline - Vernon 138 kV overloads Vernon - Chillicothe 69 kV |
| 18-Apr | 3:00 | 22:30 | Alert | Opened Adjustment Period Replacement Market for hours 1200 - 2400 |
| 18-Apr | 7:00 | 23:59 | Advisory | Issued due to Capacity Insufficiency. |
| 18-Apr | 13:44 | 22:30 | Transmission Alert | Loss of Parker - Eagle Mountain & Parker - Roanoke 345 kV loads Benbrook tr |
| 18-Apr | 13:44 | 23:40 | Transmission Alert | Loss of Lake Pauline - Vernon 138 kV loads Vernon - Chillicothe 69 kV |
| 18-Apr | 13:44 | 22:30 | Transmission Alert | Loss of Pleasanton - Moore 138 kV loads Dilley - Pearsall 69 kV |
| 18-Apr | 13:44 | 22:30 | Transmission Alert | Loss of Martin Lake to Shamburger loads Elkton to West Tyler. |
| 19-Apr | 13:45 | 20:30 | Transmission Alert | Loss of Pleasanton - Moore 138 kV loads Dilley - Pearsall 69 kV |
| 19-Apr | 13:45 | 20:30 | Transmission Alert | Loss of Lake Pauline - Vernon 138 kV loads Vernon - Chillicothe 69 kV |
| 19-Apr | 13:45 | 20:30 | Transmission Alert | Loss of Martin Lake to Shamburger loads Elkton to West Tyler. |
| 19-Apr | 13:45 | 20:30 | Transmission Alert | Loss of Roma Sw to Garza loads Garza tr |
| 20-Apr | 13:45 | 20:30 | Transmission Alert | Loss of Kingsville-Alice 138 loads Falfurrias 138/69 tr |
| 20-Apr | 15:16 | 20:10 | Transmission Alert | Loss of Dilley Sw- North Laredo loads N Laredo - Asherton |
| 20-Apr | 15:14 | 20:10 | Transmission Alert | Loss of South McAllen 138/69 tr loads La Palma - Rangerville |
| 20-Apr | 19:07 | 23:59 | OCN | Severe weather moving across Central Texas. |
| 25-Apr | 16:00 | 20:25 | Transmission Alert | Loss of San Miguel 138/69 kV tr and Dilley Sws tr loads Derby Pearsall 138 kV |
| 26-Apr | 16:30 | 21:00 | Transmission Alert | Loss of San Miguel 138/69 kV tr and Dilley Sws tr loads Derby Pearsall 138 kV |
| 28-Apr | 19:42 | 24:00:00 | OCN | Severe weather alert for North Central and Central Texas. |
| 29-Apr | 0:00 | 14:00 | OCN | Severe weather alert for North Central and Central Texas. |