## Slide 1: Voltage Reactive
Skits

## Slide 2: Skit 1
750 MVA
725 MW
192 MVAR
450 MVA
430 MW
133 MVAR
750 MVA
745 MW
086 MVAR
650 MVA
620 MW
195 MVAR
000 MVA
000 MW
000 MVAR
143.5 KV
144.2 KV
144.1 KV
142.9 KV
137.0 KV
.96 PF
.95 PF
.95 PF
.99 PF
.00 PF
Unit 1
Unit 2
Unit 3
Unit 4
Notes: Skit 1
Condition: Large generator trips causing local voltages to sag. TO calls QSE and requests a generator to raise the voltage. QSE doesn’t want to raise the voltage because his buss voltage and power factor are within limits.
TO: Calls to request to have the voltage raised.
QSE: Responds that he is not going to raise the voltage because he is within limits.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 3: ERCOT Protocols 6.5.7.3(1),6.5.7.2(5)
(1)ERCOT, in coordination with the TDSPs, shall establish, and update as necessary, Voltage Profiles at points of interconnection of Generation Resources required to provide VSS to maintain system voltages within established limits.
(5)QSEs shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.
Notes: Skit 1
Condition: Large generator trips causing local voltages to sag. TO calls QSE and requests a generator to raise the voltage. QSE doesn’t want to raise the voltage because his buss voltage and power factor are within limits.
TO: Calls to request to have the voltage raised.
QSE: Responds that he is not going to raise the voltage because he is within limits.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 4: Skit 2
+ -
+ -
+ -
+ -
+ -
+ -
Notes: Skit 2
Condition: TO places capacitors in service without regard to generator VAR loading. QSE contacts the TO because the generators are operating in an extremely under excited condition.
QSE: Calls TO to complain about the generators operating so far in a leading condition.
TO: Responds that he needs to get the reactors off and capacitors on before the load picks up and voltage starts to sag.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 5: ERCOT Protocols 6.5.7.3 (3)
6.5.7.3 ERCOT Responsibilities
(3) ERCOT, in coordination with the TDSPs, shall deploy static Reactive Power Resources as required to continuously maintain dynamic Reactive Reserves from QSEs, both leading and lagging, adequate to meet ERCOT System requirements.
Notes: Skit 1
Condition: Large generator trips causing local voltages to sag. TO calls QSE and requests a generator to raise the voltage. QSE doesn’t want to raise the voltage because his buss voltage and power factor are within limits.
TO: Calls to request to have the voltage raised.
QSE: Responds that he is not going to raise the voltage because he is within limits.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 6: Skit 3
750 MVA
725 MW
192 MVAR
450 MVA
430 MW
133 MVAR
750 MVA
745 MW
086 MVAR
650 MVA
620 MW
195 MVAR
143.5 KV
144.2 KV
144.1 KV
142.9 KV
.96 PF
.95 PF
.95 PF
.99 PF
Unit 1
Unit 2
Unit 3
Unit 4
Notes: Skit 3
Condition: Resource not sharing in voltage support/TDSP not equitably distributing voltage support.
TO: Calls specific generators repeatedly to make voltage adjustments.
Second TO: Asks why he calls the same generators instead of others.
TO: Responds that these generators always do what he asks and besides the smaller generators don’t offer as much support.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 7: Operating Guides 2.10.4.1
…Under TDSP declared emergency conditions, TDSPs may directly dispatch the reactive output of the Generation Resource and follow up with notification of the QSE. The TDSP will, using Good Utility Practices, equalize the reactive output of the generators based on size (net dependable MW capability), reactive capability, reactive limits and system voltage impact.
Notes: Skit 1
Condition: Large generator trips causing local voltages to sag. TO calls QSE and requests a generator to raise the voltage. QSE doesn’t want to raise the voltage because his buss voltage and power factor are within limits.
TO: Calls to request to have the voltage raised.
QSE: Responds that he is not going to raise the voltage because he is within limits.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 8: Skit 4
AUX TR
AUX BUSS
GSU
.95 PF
.97 PF
Notes: Skit 4
Condition: TO and QSE have differing perspectives of where the Power Factor should be measured.
TO: Calls the QSE to have the voltage raised.
QSE: Responds that he is already at a .95 power factor and shouldn’t have to raise the voltage any more without an ERCOT dispatch instruction.
ERCOT: Responds with the correct actions as per the Guides and Protocols.

## Slide 9: ERCOT Protocols 6.5.7.1 (2)
Generation Resources required to provide VSS except as noted below in items (3) or (4), shall have and maintain a URL which has an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP.
Notes: Skit 1
Condition: Large generator trips causing local voltages to sag. TO calls QSE and requests a generator to raise the voltage. QSE doesn’t want to raise the voltage because his buss voltage and power factor are within limits.
TO: Calls to request to have the voltage raised.
QSE: Responds that he is not going to raise the voltage because he is within limits.
ERCOT: Responds with the correct actions as per the Guides and Protocols.