## Slide 1: Reliability Management with Ancillary Service Deployments
23rd Annual
ERCOT Operations Training Seminar
March 27th – April 27th 2006

## Slide 2: Introduction
Brandon Whittle
bwhittle@ercot.com
Market Operations Support
System Operations
ERCOT

## Slide 3: Agenda
Acronyms
ERCOT Basics
Define Ancillary Services
Describe Dispatch Mechanisms
Explain Benefits and Use
Illustrate Use with Examples
Other Resources
Wrap Up

## Slide 4: Acronyms
LaaRs | Loads Acting as a Resource
CSC | Commercially Significant Constraint
XML | Extensible Markup Language
RTU | Remote Terminal Unit
ACE | Area Control Error
SCADA | Supervisory Control and Data Acquisition
SCE | Schedule Control Error
MW | Megawatt
URS | Up Regulation Service
OOME | Out-of-Merit Energy
UFR | Under Frequency Relay
QSE | Qualified Scheduling Entity
VDI | Verbal Dispatch Instruction
OOMC | Out-of-Merit Capacity

## Slide 5: ERCOT Basics – Zonal Vs. Local

## Slide 6: Balancing Energy
Energy used to meet variations in Load and ensure secure grid operations
Dispatch Instructions to QSEs
Dispatched using XML
15 minute intervals
Zonal dispatch
Resource-level dispatch
Notes: Zonal dispatch is the category 1 dispatch
Resource Level Dispatch for category 2,3,4 unit specific instructions for local congestion

## Slide 7: Balancing Energy
27500
28000
28500
29000
29500
30000
30500
31000
Load Forecast
Energy Schedule
Schedules and Balancing
1st Interval
2nd Interval
UBES
DBES
Notes: This example is based on the need for balancing energy for load balance

## Slide 8: Bilateral vs. Balancing Energy
When compared to overall energy requirements, Ancillary Services (including Balancing Energy Service) are a relatively small part compared to scheduled energy.

## Slide 9: Regulation Up
Service which raises power output in Resources to control system frequency
Dispatch Instructions to QSEs
Dispatched using RTUs
4 second intervals
Portfolio-wide dispatch

## Slide 10: Regulation Down
Service which lowers power output in Resources to control system frequency
Dispatch Instructions to QSEs
Dispatched using RTUs
4 second intervals
Portfolio-wide dispatch

## Slide 11: Regulation Up & Down
27500
28000
28500
29000
29500
30000
30500
31000
Load Forecast
Energy Schedule
Schedules and Balancing
1st Interval
2nd Interval
Regulation Down
Regulation Up
Notes: Regulation fills in the ‘gaps’ and fine tunes generation to match the current load.

## Slide 12: Regulation Process – Simplified
ACE used by ERCOT and used here is not the same as the NERC ACE definition which includes interchange
Regulation usually must be recalled before switching directions
ACE represents how many MWs it would take to restore scheduled frequency
Filters adjust the dispatch to ‘smooth’ the deployments and reduce oscillations
Bias and Filters are tuned as necessary
Notes: This explanation is simplified from actual frequency control systems and is intended only to help with the basic understanding of regulation control, not to be used as a reference to describe the details of ERCOT’s regulation deployment mechanisms.
Regulation does not have to be fully recalled when frequency is deviating significantly from scheduled frequency.

## Slide 13: Responsive Reserve
Reserves to restore frequency within the first few minutes of an event that causes a significant frequency deviation
“First responder”
Dispatch Instructions to QSEs
Generation Resources
  Dispatched using RTU 4 second intervals
  Portfolio-wide dispatch
LaaR
  Dispatched via UFR or VDI
  Resource-specific (UFR, VDI) or Portfolio wide (VDI)
Notes: LaaRs can be dispatched using voice and those can also be used for local congestion.

## Slide 14: Responsive Reserve
27500
28000
28500
29000
29500
30000
30500
31000
Load Forecast
Schedules and Balancing
(Expected Generation)
1st Interval
2nd Interval
Regulation Down
Regulation Up
Responsive Reserve

## Slide 15: Responsive Reserve Example
Notes: This event was caused by a trip at a large resource – notice how RRS was immediately deployed and stayed active for over 30 minutes until frequency was stabilized around 60.

## Slide 16: Non Spinning Reserve
Capacity capable of being ramped (or interrupted) within 30 minutes
Capacity or congestion
Dispatch Instructions to QSEs
Dispatched using XML
15 minute intervals, minimum 1 hour
Zonal dispatch
Step Change – NSRS is not ramped in

## Slide 17: Non Spinning Reserve
27500
28000
28500
29000
29500
30000
30500
31000
Load Forecast
Schedules and Balancing
(Expected Generation)
1st Interval
2nd Interval and Beyond
Regulation Down
Regulation Up
Responsive Reserve
Non Spinning Plus
Notes: This example is a purely hypothetical situation which illustrates how NSRS might be used. In real practice this situation is very rare – Usually after a trip balancing can be used to restore generation and relieve responsive reserve.

## Slide 18: Ancillary Service Procurements
Procurements change based on hour
DRS, URS, RRS standard by month/hour
NSRS also depending on weather conditions
Available on www.ercot.com
http://mospublic.ercot.com/ercot/jsp/ancillary_service_requests.jsp

## Slide 19: Out of Merit Energy
Dispatch of energy outside the bidding process
Power balance or congestion
Dispatch Instructions to QSEs
Dispatched using XML
15 minute intervals
Resource-level dispatch

## Slide 20: Out of Merit Energy
Post-contingency Overload
  Solve using market dispatch, if possible
  OOME
Notes: Market Dispatch is Local Balancing Energy using an OC2 or OC3.
This screenshot is from the Transmission and Security Desk’s RTCA program which continually checks for post contingency violations and publishes the results.

## Slide 21: Zonal Out of Merit Energy
Dispatch of energy outside the bidding process
Power balance or zonal congestion
Dispatch Instructions to QSEs
Dispatched using XML
15 minute intervals
Zonal-level dispatch

## Slide 22: Zonal Out of Merit Energy
2003
4 Zones, 3 CSCs
Reliability threatened with excessive North to Houston imports
OOME of entire fleets in North and Houston Zones was necessary
Led to Zonal OOME Ancillary Service
North to Houston CSC first created for 2004
Notes: This example is the most famous use of ZOOME, however a zonal or portfolio (all zones) OOME is commonly used when regulation supplies are exhausted.

## Slide 23: Out of Merit Capacity
Selection of Generation Capacity outside the bidding process
Capacity or congestion
Dispatch Instructions to QSEs
Dispatched using XML
One hour intervals
Resource-level dispatch

## Slide 24: Out of Merit Capacity
Day Ahead
  Contingency overload observed in analysis
  Capacity shortage expected
  RPRS is first option
  OOMC if not
Real Time
  Contingency overload observed in RTCA
  Capacity shortage
  Bid-based dispatch first
  OOME second
  OOMC if necessary

## Slide 25: Replacement Reserve
Capacity procured from Generation planned to be off-line and LaaR that are available for interruption
Capacity or congestion
Dispatch Instructions to QSEs
Dispatched using XML
One hour intervals, in advance
Resource-level dispatch

## Slide 26: Voltage Support
A service to maintain transmission and distribution voltages
Dispatch Instructions to QSEs
Dispatched using VDI (Verbal Dispatch Instruction)
Resource-level dispatch

## Slide 27: Reliability Must Run
Resource operated under contract that would not otherwise be operated
Congestion, stability, and voltage support
Dispatch Instructions to QSEs
Dispatched using email or fax
Resource-level dispatch
7 RMR units (As of 2/12/06)

## Slide 28: Black Start
Contracted service provided by a Resource capable of starting without support of the transmission grid
Dispatched by QSE according to Black Start Plan
Resource-level
2006 has 15 Black Start Units

## Slide 29: Wrap Up
Overview
  Balancing Energy Service is used to get schedules closer to Load
  Regulation Service fine tunes the balancing deployment
  Responsive Service is for short-term frequency disturbances
  Non-Spin Service is for issues of longer duration – a “catch all” service
  RPRS brings on capacity
  OOME, OOMC, Voltage Support, RMR, Black Start are all ‘command and control’ measures used when bid-based solutions cannot fix the problem
Ancillary Services help keep ERCOT reliable

## Slide 30: Other Resources
Protocols
  Chapter 2 (Definitions)
  Chapter 6 (Ancillary Services)
Operating Guides
  Chapter 2 (System Operations)
  Chapter 8 (Operational Metering and Communications)
Operating Procedures
Other Seminar Presentations
ERCOT Wholesale Client Representative
  (512) 248-3900

## Slide 31: Questions
Questions?
Further Discussions?