## Slide 1: Texas Nodal Market
Joel Mickey
Manager, ERCOT Market Operations Support
23rd ERCOT Operations Training Seminar
March 30 – April 27, 2006

## Slide 2
CRR Congestion Revenue Right
DAM Day-Ahead Market
HA Hour-Ahead
LMP Locational Marginal Pricing/Locational Marginal Price
PTP Point-to-Point
RT Real-Time
RUC Reliability Unit Commitment
SASM Supplemental Ancillary Service Market
SCED Security Constrained Economic Dispatch
SCUC Security Constrained Unit Commitment
SFT Simultaneous Feasibility Test
SPP Settlement Point Price
TCR Transmission Congestion Right
TNM Texas Nodal Market
Acronyms

## Slide 3
What is Nodal?
Why Nodal?
Elements of Texas Nodal Market
Timeline for Implementation
Road Map

## Slide 4
I. What is Nodal?
A Nodal LMP Market is a centrally dispatched energy and ancillary services spot market based on nodal locational marginal pricing (LMP), with standard financial hedging instruments (such as CRRs).
Basics of a Nodal Model

## Slide 5
I. What is Nodal?
Locational Marginal Price (LMP):
The marginal cost of supplying the next increment of electric demand at a specific location (node) on the electric power network, taking into account both generation marginal cost and the physical aspects of the transmission system.
Congestion Revenue Rights (CRRs):
A CRR is a financial risk-hedging instrument that entitles the holder to be charged or receive compensation, depending on whether the CRR is an option or obligation, for congestion costs that arise when the transmission grid is congested.
Basics of a Nodal Model

## Slide 6
I. What is Nodal?
Two-Node LMP Example -- No Congestion
A
B
Bid Amount: 100 MW
Price: $30/MWh
Dispatch = 150 MW
LMP = $20/MWh
Dispatch = 0 MW
LMP = $20/MWh
150 MW
Bid Amount: 200 MW
Price: $20/MWh

## Slide 7
I. What is Nodal?
A
B
150 MW
Dispatch = 60 MW
LMP = $20/MWh
Dispatch = 90 MW
LMP = $30/MWh
60 MW
Constraint
Bid Amount: 100 MW
Price: $30/MWh
Bid Amount: 200 MW
Price: $20/MWh
Two-Node LMP Example -- No Congestion

## Slide 8
I. What is Nodal?
The current ERCOT system is actually a Zonal LMP model, i.e., LMP is calculated for each Congestion Management Zone. (In a Nodal LMP model, LMP is calculated for each node.)
The TCR in current ERCOT Market is also one kind of Congestion Revenue Right which helps hedge financial risks in current power market.
Basics of a Nodal Model

## Slide 9
I. What is Nodal?
  Bilateral + Ancillary Service
  No ERCOT-Run Day-ahead Energy Market
  Zonal Locational Model
  Portfolio Schedules
  Balancing Energy (Real-Time) Market
    (Inter- & Intra-zonal Congestion Management )
  Transmission Congestion Rights (TCRs)
  Single Control Area
ERCOT : Present Zonal Model (since 7/31/2001)

## Slide 10
W
H
S
N
NE
Zonal
Nodal
Commercially Significant Constraint

## Slide 11
I. What is Nodal?
Zonal
Nodal
No Day-Ahead Energy Market | With Day-Ahead Energy and A/S Market
Scheduling, Bidding, and Pricing at Zonal Level | Scheduling, Offering, and Pricing at Nodal Level (Gen at Node level, Load at Load-Zone level)
Portfolio Scheduling and Bidding | Resource-Specific Scheduling, Offering, and Dispatching
Six Flowgate Congestion Revenue Rights for crossing-zone CSCs | At least thousands of Congestion Revenue Rights (PTP Obligation, PTP Option, FGR)

## Slide 12
I. What is Nodal?
 | PJM | NE | MISO | NY | CA | ERCOT
Congestion Management | Nodal LMP | Nodal LMP | Nodal LMP | Nodal LMP | Inter/Intra-zonal | Zonal CSC/ Local
Transmission Rights | Financial | Financial | Financial | Financial | Physical | Financial
Markets | DA, RT, FTR | DA, RT, FTR | DA, RT, FTR | DA, RT, TCR | DA, HA, RT | RT, TCR
Bilateral Trans-action (Internal) | Financial | Financial | Financial / Physical | Financial | N/A | Physical
Location Model | Node, zone, hub | Node, zone, hub | Node, zone, hub | Node, zone, hub | Zone (no loop) | Zonal (meshed)
Resource Model | Unit Specific | Unit Specific | Unit Specific | Unit Specific | Portfolio & Unit Specific | Portfolio
Unit Commitment | Self + DA + RUC | Self + DA + RUC | Self + DA + RUC | Self + DA + RUC | Self + RUC | Self + RPRS
Nodal elsewhere
in transition

## Slide 13
What is Nodal?
Why Nodal?
Elements of Texas Nodal Market
Timeline for Implementation
Road Map

## Slide 14
II. Why Nodal?
Precise market-based pricing of energy
More granular price signals
Encourage Resource competition
  Nodal prices send proper price signals to encourage additional generation and/or transmission investment in proper locations.
Easier and more accurate management of congestion.
  More accurate Resource information. Market model and operations model are more consistent than current structure.

## Slide 15
What is Nodal?
Why Nodal?
Elements of Texas Nodal Market
Timeline for Implementation
Road Map

## Slide 16
III. Elements of
Texas Nodal Market
Bilateral Market
Forward
CRR Auction
Energy, A/S, & CRR Market
Day-ahead
RUC Market
RUC Market
HR-ahead
Energy Market
Real-Time

## Slide 17
III. Elements of
Texas Nodal Market
The Day-Ahead (DA) Market is a daily, co-optimized market in the DA for Energy, Ancillary Service capacity and certain Congestion Revenue Rights
The Primary purposes of DAM are:
  Arrange for energy and Ancillary Service for tomorrow
  Provide price discovery for tomorrow
  Provide price certainty for tomorrow
DAM is not necessary for reliability of the electric grid
Participation in DAM is voluntary, except for RMR units
Day-Ahead Market (DAM)
Notes: RMR unit offers
ERCOT shall decide, in its sole discretion, when to make an RMR Unit available for commitment in DRUC, HRUC, or DAM, considering relevant factors such as whether it is likely to be needed in Real-Time for reliability reasons, whether SCED will solve operating constraints, contractual constraints on the Resource, and any other adverse effects on the RMR Unit that may occur as the result of the dispatch of the RMR Resource.
By 0600 in the Day-Ahead, each QSE representing RMR units shall submit information to ERCOT indicating availability of RMR units for the operating day, and any other information that ERCOT may need to evaluate use of the units.
By 1000 in the Day-Ahead, ERCOT shall submit, in ERCOT’s sole discretion, Three-Part Supply Offers based on RMR Agreement rates and any other relevant information as provided under contract on behalf of RMR Units for any RMR Units to be considered in the DAM, DRUC, or HRUC.
ERCOT may submit Energy Offer Curves based on RMR Agreement rates and any other relevant information as provided under contract on behalf of RMR Units committed in the DAM, DRUC, or HRUC.

## Slide 18
(continued)
III. Elements of
Texas Nodal Market
Day-Ahead Market (DAM)
0600
1000
Execute
DRUC
ERCOT Activity:
Begin Execution of
DRUC at 1430
ERCOT Activity:
Publish system
conditions, forecasts,
AS Obligations,
losses
& other items
QSE Activity:
Update COP,
Submit Capacity
Trades &
Energy Trades
Day Ahead Operations
QSE Activity:
Update COP to
Reflect Awards
Execute DAM
1430
QSE Activity:
Submit DAM
Offers & Bids,
DRUC Offers
COP, Self
-
Arranged
AS Quantities
ERCOT Activity:
Communicate DAM
Awards, AS Capacity
Awards
ERCOT Activity:
Begin Execution of
DAM at 1000
Notes: How long will it take DAM to run?
-- About 1-2 hours?
Posting Forecasted ERCOT System Conditions:
No later than 0600 in the Day-Ahead, ERCOT shall post on the MIS Secure Area, and make available for download, the following information for the Operating Day:
The Network Operations Model topology that includes known transmission line and other Transmission Facilities Outages for the minimum Load hour and the peak Load hour;
Weather assumptions used by ERCOT to forecast ERCOT System conditions and used in the Dynamic Rating Processor;
Any weather-related changes to the transmission contingency list;
ERCOT System, Weather Zone, and Load Zone Load forecasts for the next seven days ;
Load forecast distribution factors;
Load Profiles for non-IDR metered Customers;
Distribution Loss Factors and forecasted ERCOT-wide Transmission Loss Factors;
Current Electrical Bus Load distribution factors;
A current list of all Settlement Points;
A mapping of Settlement Points to Electrical Buses in the Network Operations Model.
Ancillary Service Plan:
ERCOT shall analyze the expected Load conditions for the Operating Day and develop an Ancillary Service Plan that identifies the Ancillary Service MW necessary for each hour of the Operating Day.
Once specified by ERCOT for an hour and published on the MIS Public Area, Ancillary Service quantity requirements for an Operating Day may not be decreased.
ERCOT shall assign part of the Ancillary Service Plan quantity, by service, by hour, to each LSE based on Load Ratio Share and shall then aggregate those quantities, by service, by hour to the QSE level.
ERCOT shall base the LSE Ancillary Service allocation on the hourly Load Ratio Share from the Initial Settlement data for the Day-Ahead Market, for the same hour and day of the week, for the most recent day for which Initial Settlement Statements are available .
Wind Generation Resources:
ERCOT shall produce and update hourly a Short-Term Wind Power Forecast (STWPF) that provides a rolling 48-hour hourly forecast of wind production potential for each Wind-Powered Generation Resource (WGR).
Each Generation Entity that owns a WGR shall install and telemeter to ERCOT the site-specific meteorological information that ERCOT determines is necessary to produce the STWPF forecasts.
The WGR Production Potential (WGRPP) is an hourly 80% confidence level forecast of energy production for each WGR.
From the STWPF, ERCOT shall produce and update WGRPP forecasts each hour for each WGR to be used as input into each RUC process
Each QSE representing a WGR shall use the latest WGRPP forecast for each WGR published by ERCOT as the HSL for the WGR in the QSE’s COP.
To determine a QSE’s capacity shortage for RUC settlement purposes for each WGR, ERCOT shall use the COP and Trades Snapshot prior to the Day-Ahead RUC regardless of Real-Time capacity or actual generation.

## Slide 19
(continued)
III. Elements of
Texas Nodal Market
QSE activity:
  Submit DAM Offers & Bids, DRUC Offers, COP, Self-Arranged AS Quantities
  After execution of DAM, update COP
ERCOT activity:
  Publish system conditions, forecasts, AS Obligations, losses, & other items
  Begin execution of DAM at 1000
  After execution of DAM, communicate DAM Awards including AS Capacity Awards
Day-Ahead Market (DAM)
Notes: DAM Offers:
Three-part supply offers. Three-part supply offers that are not cleared by DAM are used by DRUC
DAM Energy-Only offers
Ancillary Service offers
CRR offers
DAM Bids
(1)Energy bids
(2)PTP Obligation bids
COP (Current Operating Plan)
A COP include:
  The name of the Resource
  The expected Resource Status (ONRUC – online and the hour is a RUC-committed interval; ONREG – online Resource with Energy Offer curve providing regulation service; ON – online Resource with Energy Offer Curve; etc.)
  HSL (High Sustained Limit)
  LSL (Low Sustained Limit)
  HEL (High Emergency Limit)
  LEL (Low Emergency Limit)
  Ancillary Service capacity in MW for Reg Up, Reg Dn, RRS, NSRS
  For combined-cycle Resources, the above items are required for each operating configuration.
Each QSE that represents a Resource must submit a COP to ERCOT that reflects expected operating conditions for each Resource for each hour in the Operating Day and the next seven Operating Days.
Each QSE shall update its COP reflecting changes in availability of any Resource as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change.
Self-Arranged Ancillary Service:
The QSE must indicate before 1000 in the Day-Ahead the of Self-Arranged Ancillary Service Quantities, by service, so ERCOT can determine how much Ancillary Service capacity, by service, needs to be obtained through the DAM.
At or after 1000 in the Day-Ahead, a QSE may not change its Self-Arranged Ancillary Service Quantities unless ERCOT opens a Supplemental Ancillary Service Market.
Before 1430 in the Day-Ahead, all Self-Arranged Ancillary Service Quantities must be represented by physical capacity, either by Generation Resources or Load Resources, or backed by Ancillary Service Trades.

## Slide 20
(continued)
III. Elements of
Texas Nodal Market
Day-Ahead Market (DAM)
Prior to execution of the DAM, ERCOT shall complete a Day-Ahead SFT.
The DAM maximizes bid-based revenues minus offer-based costs over the Operating Day, subject to security and other constraints and ERCOT A/S procurement requirements.
The DAM settlement is based on hourly MW awards and on Day-Ahead hourly Settlement Point Price (SPP).
Notes: SFT uses the Day-Ahead Updated Network Model topology and evaluates all CRRs for feasibility to determine hourly oversold quantities.
The bid-based revenues include revenues from DAM Energy Bids and PTP Obligation Bids.
The offer-based costs include costs from Three-part Supply Offers, DAM Energy-Only Offers, CRR Offers, and Ancillary Service Offers.
Security constraints include:
Transmission constraints
  Thermal constraints – protect transmission facilities against thermal overload
  Generic constraints – protect the ERCOT Transmission Grid against transient instability, dynamic stability or voltage collapse
  Power flow constraints – the energy balance at required Electrical Buses in the ERCOT Transmission Grid must be maintained
Resource constraints
  Resource output constraints – the minimum and maximum output levels of each Resource
  Resource operational constraints – includes minimum run time, minimum down time, and configuration constraints
Other constraints
  Linked offers – the DAM may not select any one part of that Resource capacity to provide more than one Ancillary Service or to provide both energy and an Ancillary Service in the same Operating Hour. The DAM may, however, select part of that Resource capacity to provide one Ancillary Service and another part of that capacity to provide a different Ancillary Service or energy in the same Operating Hour
  Block Ancillary Service Offers – For a Load Resource offering a block Ancillary Service Offer, the DAM must ignore the offer unless the entire block can be accepted

## Slide 21
III. Elements of
Texas Nodal Market
Security Sequence including RUC
Notes: The Security Sequence is a set of prerequisite processes for RUC that describes the key system components and inputs that are required to support the RUC process, the RUC process itself, and the ERCOT review of the Resource commitment recommendations made by the RUC process.
The Security Sequence uses a subset of the computational modules used by the Real-Time Sequence. The main distinction between the two models concerns inputs. The inputs into the Security Sequence are based on a snapshot of projected hourly system conditions and constraints.
The Security Sequence uses the status of all transmission breakers and switches(current status for HRUC and normal status for DRUC), updated for approved Planned Outages for equipment out of service and returned to service for building a representation of the ERCOT Transmission Grid for each hour of the RUC Study Period.
The weather forecast obtained by ERCOT must be provided to the Dynamic Rating Processor to create weather-adjusted MVA limits for each hour of the RUC Study Period for all transmission lines and transformers that have Dynamic Ratings.
ERCOT shall analyze base configuration, select n-1 contingencies and select n-2 contingencies under the Operating Guides.
ERCOT shall also post to the MIS Secure Area any contingencies temporarily removed from the standard contingency list by ERCOT immediately after successful execution of the Security Sequence.
As part of the Network Security Analysis, if there is an approved Remedial Action Plan (RAP) available, it must be used before considering a Resource commitment.
ERCOT shall model all approved Special Protection Systems (SPSs) and RAPs in the contingency analysis. The computational modules must enable ERCOT to analyze contingencies, including the effects of all approved automatically deployed SPSs.

## Slide 22
RUC is used to
  Ensure Transmission System reliability
  Ensure enough Resource capacity, including A/S capacity, is committed in the right locations to reliably serve the forecasted Load
RUC uses Security Constrained Unit Commitment (SCUC) algorithm
RUC in the Nodal system is similar to the current RPRS
The objective of the RUC process is to minimize costs based on Three-Part Supply Offers, substituting a proxy Energy Offer Curve for the Energy Offer Curve, over the RUC study period
Reliability Unit Commitment (RUC)
III. Elements of
Texas Nodal Market
Notes: Factors included in the RUC process are:
(a) ERCOT System-wide hourly Load forecast allocated appropriately over Load buses;
(b) Transmission constraints – Transfer limits on energy flows through the electricity network;
(i) Thermal constraints – protect transmission facilities against thermal overload;
(ii) Generic constraints – protect the transmission system against transient instability, dynamic instability or voltage collapse;
(c) Planned transmission topology;
(d) Energy sufficiency constraints;
(e) Inputs from the COP, as appropriate;
(f) Inputs from Resource Parameters, as appropriate;
(g) Each Generation Resource’s Minimum-Energy Offer and Startup Offer, from its Three-Part Supply Offer;
(h) Any Generation Resource that is Off-Line and available but does not have a Three-Part Supply Offer;
(i) Forced Outage information; and
(j) Inputs from the eight-day look ahead planning tool, which may potentially keep a unit online (or start a unit for the next day) so that a unit minimum duration between starts does not limit the availability of the unit (for security reasons).
To determine the projected energy output level of each Resource and to project potential congestion patterns for each hour of the RUC, ERCOT shall calculate proxy Energy Offer Curves based on the Mitigated Offer Caps for the type of Resource as specified in Section 4.4.8.4, Mitigated Offer Cap and Mitigated Offer Floor , for use in the RUC. Proxy Energy Offer Curves are calculated by multiplying the Mitigated Offer Cap by a constant selected by ERCOT from time to time and applying the cost for all Generation Resource output between HSL and LSL. The constant selected by ERCOT may not be more than 0.001.
ERCOT shall create Three-Part Supply Offers for all Resources that did not submit a Three-Part Supply Offer but are specified as available but Off-Line, excluding Resources with a Resource Status of EMR(Available for commitment only for ERCOT-declared Emergency Condition events). For such Resources, ERCOT shall use in the RUC process 150% of any approved verifiable startup and minimum-energy costs or if verifiable costs have not been approved, the applicable Resource Category Generic Startup Offer and Minimum-Energy Offer Costs. However for settlement purposes, ERCOT shall use any approved verifiable startup costs and verifiable minimum-energy cost for such Resources, or if verifiable costs have not been approved, the applicable Resource Category Generic Startup Offer Cost and Generic Minimum-Energy Offer Cost.
The RUC process must treat all Resource capacity providing Ancillary Service as unavailable for the RUC Study Period, unless that treatment leads to infeasibility (i.e., that capacity is needed to resolve some local transmission problem that cannot be resolved by any other means). In such cases, ERCOT shall inform each affected QSE of the amount of its Resource capacity that does not qualify to provide Ancillary Service, and the projected hours for which this is the case. In that event, the affected QSE may either:
(a) Substitute capacity from Resources represented by that QSE;
(b) Substitute capacity from other QSEs using Ancillary Service Trades; or
(c) Ask ERCOT to replace the capacity.

## Slide 23
(continued)
Reliability Unit Commitment
III. Elements of
Texas Nodal Market
Notes: ERCOT shall conduct at least one Day-Ahead RUC (DRUC) and at least one Hourly RUC (HRUC) before each hour of the Operating Day. ERCOT, in its sole discretion, may conduct a RUC at any time to evaluate and resolve reliability issues.

## Slide 24
(continued)
Reliability Unit Commitment
III. Elements of
Texas Nodal Market

## Slide 25
Day-Ahead RUC (DRUC) runs after the close of Day-Ahead Market.
The RUC study period for DRUC is the next Operating Day.
The output will be a list of Resources that need to be committed for tomorrow’s 24-hour Operating Period and the hours they need to be operated.
It is assumed that the Resources will operate at minimum output unless instructed otherwise by ERCOT.
(continued)
Reliability Unit Commitment
III. Elements of
Texas Nodal Market
Notes: The DRUC uses Three-Part Supply Offers submitted before the DAM by QSEs that were considered in the DAM but not awarded in the DAM. A QSE may not submit a Three-Part Supply Offer to be considered in the DRUC unless the offer was also submitted for consideration in the DAM.

## Slide 26
Hour-Ahead RUC (HRUC) runs every hour approximately one hour ahead of the Operating Period after the security analysis is run.
The RUC study period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the next Operating Day has been solved.
ERCOT will perform the Hour-Ahead RUC using its updated forecast of hourly Load.
(continued)
Reliability Unit Commitment
III. Elements of
Texas Nodal Market
Notes: ERCOT must initiate the HRUC process at least one hour before the Operating Hour to fine-tune the Resource commitments using updated Load forecasts and updated Outage information.
To participate in HRUC, each QSE must submit any Three-Part Supply Offers before the end of the Adjustment Period for each HRUC.

## Slide 27
ERCOT shall review the RUC-recommended Resource commitments to assess feasibility and shall make any changes that it considers necessary, in its sole discretion.
The RUC process can recommend Resource de-commitment. ERCOT may only de-commit a Resource to resolve transmission constraints that are otherwise incapable of resolution.
For each RUC, ERCOT shall use a snapshot of Resource Commitments from each QSE’s most recently submitted COP before RUC execution to settle RUC charges.
(continued)
Reliability Unit Commitment
III. Elements of
Texas Nodal Market

## Slide 28
III. Elements of
Texas Nodal Market
Real Time Network Security Analysis including SCED
Notes: The Real-Time Sequence consists of multiple interdependent processes that are driven by telemetry data and the network topology.
SCADA telemetry provides the actual Real-Time status and output of Resources and the status of observable Transmission Elements of the Network Operations Model.
The Network Topology Builder creates the Updated Network Model based on the observed topology of the ERCOT Transmission Grid. The Updated Network Model is then used as the basis for the State Estimator solution.
The State Estimator must use the forecasted Load coupled with the remaining telemetry of line flows and voltages to estimate the actual Load on each Electrical Bus.
The State Estimator must use the Bus Load Forecast and the remaining telemetry information of line flows and voltages to estimate all the transmission parameters needed to provide, on convergence, a mathematically consistent data set of constrained inputs to the Network Security Analysis (NSA) and the Topology Consistency Analyzer.
The Topology Consistency Analyzer identifies possibly erroneous breaker and switch status.
The Dynamic Rating Processor provides Dynamic Ratings for all transmission lines and transformer elements with Dynamic Ratings designated by the TSPs. ERCOT shall obtain Real-Time weather data, where available, from multiple locations and provide it to the Dynamic Rating Processor.
Using the input provided by the State Estimator, ERCOT shall use the Network Security Analysis (NSA) processor to perform analysis of all contingencies remaining in the active list. ERCOT may not allow any contingency anticipated to be active in SCED, identified by NSA, until it has verified that the contingency is accurate and appropriate given the current operating state of the ERCOT Transmission Grid. ERCOT may use the information provided by the Hour-Ahead or Day-Ahead Network Security Analysis to assist in determining which contingencies are candidates for activation.

## Slide 29
Real-Time Market
Security Constrained Economic Dispatch (LMP Calculator) is used to determine Resource Base Points and LMPs.
SCED will run every 5 minutes based on state estimator output, linearized binding constraints from security analysis and may include 5-minute Load forecast.
The SCED process uses a two-step methodology that applies mitigation prospectively to resolve Non-Competitive Constraints for the current Operating Hour.
Energy will be settled on a 15-minute interval based on net injection-weighted average of the LMPs calculated in the three 5-minute intervals.
III. Elements of
Texas Nodal Market
Notes: Real-Time energy settlements use Real-Time Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs for a 15-minute Settlement Interval, using the LMPs from all of the executions of SCED in the Settlement Interval. In contrast, the DAM energy settlements will use DAM Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs for a one-hour Settlement Interval.

## Slide 30
Real-Time Market
When the SCED process cannot reach a solution, ERCOT shall declare an Emergency Condition (EC).
Once ERCOT declares an EC, ERCOT may:
  Direct the SCED process to relax active transmission constraints and/or HASLs and LASLs and resume calculation of LMPs;
  Issue Emergency Base Points for Resources;
  Issue an instruction to hold the previous interval;
  Instruct a QF, Hydro or nuclear-powered Resource to operate below its Low Sustained Limit.
The EC continues until the SCED process can reach a solution without using measures listed above.
III. Elements of
Texas Nodal Market
(continued)
Notes: For intervals that the SCED process fails to reach a solution, then the LMPs for the interval for which no solution was reached are equal to the LMPs in the most recently solved interval.
ERCOT shall notify the market of the failure using the Messaging System and by posting on the MIS Secure Area.
Under an Emergency Condition, the ERCOT Operator may relax transmission constraints to provide additional generation at the expense of temporarily creating a security violation as long as the violation does not physically overload any single transmission element above its emergency limit, as defined in the ERCOT Operating Guides. ERCOT shall report any NERC or FERC penalties assessed for violating those constraints to Market Participants and the PUCT.
ERCOT relaxes HASLs and LASLs for specific Resources by reducing the Ancillary Service Schedules for the affected Resource, if sufficient supply exists to manage total system needs. LMPs calculated for the affected interval must be used for settlement.
ERCOT shall honor all Resource operating parameters in Dispatch Instructions under normal conditions and Emergency Conditions. During Emergency Conditions, ERCOT may verbally request QSEs to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request.
A Qualifying Facility (QF), a hydro-powered Resource, or a nuclear-powered Resource may be instructed by ERCOT to operate below its Low Sustained Limit only after all other Resource options have been exhausted.
High/Low Ancillary Service Limit (HASL/LASL) : A dynamically calculated MW upper/lower limit on a Resource to reserve the part of the Resource’s capacity committed for Ancillary Service, calculated as described in Section 6.5.7.2, Resource Limit Calculator.
Emergency Base Point: The target MW output level for a Resource that is selected by ERCOT during an Emergency Condition.
Emergency Condition is either:
(1) An operating condition in which the safety or reliability of the ERCOT System is compromised or threatened, as determined by ERCOT; or
The failure of the SCED process.
Ratings
Emergency Rating: Two-hour MVA rating of a Transmission Element.
15-Minute Rating: The 15-Minute MVA rating of a Transmission Element.
Normal Rating: The rating at which a Transmission Element can operate without reducing its normal life expectancy.

## Slide 31
Real-Time Market
Four levels of communication among ERCOT, TSPs and QSEs:
  Operating Condition Notice (OCN)
  Advisory
  Alert
  Emergency Notice
III. Elements of
Texas Nodal Market
(continued)
Notes: The type of communication ERCOT issues is determined primarily on the basis of the time available for the market to respond before an Emergency Condition occurs. The timing of these communications could range from days in advance to immediate. If there is insufficient time to allow the market to react, ERCOT may bypass one or more of the communication steps.
OCN:
ERCOT will issue an OCN to inform all QSEs of a possible future need for more Resources due to conditions that could affect ERCOT System reliability. OCNs are for informational purposes only.
Advisory:
ERCOT shall issue an Advisory when
  (a) When it recognizes that conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability;
  (b) When weather or ERCOT System conditions require more lead-time than the normal Day-Ahead Market allows;
  (c) When a Market Participant notifies ERCOT of fuel curtailment that could significantly impact available capability;
  (d) When communications or other controls are significantly limited; or
  (e) When ERCOT Transmission Grid conditions are such that operations within first contingency criteria as defined in the Operating Guides are not likely or possible because of Forced Outages or other conditions.
Although an Advisory is for information purposes, ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures.
Alert:
(1) ERCOT shall issue an Alert when ERCOT determines that:
  (a) Conditions have developed such that additional Ancillary Services are needed in the current Operating Period;
  (b) There are insufficient Ancillary Services or Energy Offers. in the Day-Ahead Market (DAM) or in a Supplemental Ancillary Services Market (SASM)
  (c) Market-based Congestion Management techniques embedded in SCED as specified in these Protocols will not be adequate to resolve transmission security violations;
  (d) Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission security violations
(2) With the issuance of an Alert, ERCOT may exercise its authority to immediately procure the following services from existing offers:
  (a) Regulation Services;
  (b) Responsive Reserve Services; and
  Non-Spinning Reserve Services.
Emergency Notice:
(1) ERCOT shall issue an Emergency Notice only for one or more of the following reasons:
  (a) ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practicably obtainable from the market;
  (b) ERCOT is in an unreliable condition, as defined below;
  (c) Immediate action must be taken to avoid or relieve an overloaded transmission element;
  (d) ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures;
  (e) ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process;
  (f) ERCOT determines that a fuel shortage exists that could significantly impact the available capacity to the grid, based on information provided by the Market Participants; or
  The SCED process fails to reach a solution, whether or not ERCOT is using one or both of the measures specified in paragraph (3) of Section 6.5.9.2, Failure of the SCED Process.
(2) If the Emergency Condition is the result of a transmission problem that puts the ERCOT System in an unreliable condition, then ERCOT shall act immediately to return the ERCOT System to a reliable condition, including instructing Resources to change output and instructing TSPs or DSPs to drop Load.
(3) If the Emergency Condition is the result of an Ancillary Service insufficiency, then ERCOT shall follow the Emergency Electric Curtailment Plan procedures.

## Slide 32
Real-Time Market
III. Elements of
Texas Nodal Market
(continued)
Do we need to monitor SCE in the Nodal Market? | 
Zonal Market | Nodal Market
Portfolio Scheduling, Bidding, Dispatching | Resource-Specific Scheduling, Offering and Dispatching
At Real Time, QSEs try to follow their portfolio schedules; ERCOT deploys BES to balance schl’d Gen and Load Forecast | At Real Time, Resources are economically dispatched to their base-points based on real time Load requirements
Uninstructed Resource Charge (URC) is calculated based on zonal Total Uninstructed Deviation | Generation Resource Base-Point Deviation Charge is calculated based on the Resource’s Dispatch Instruction and actual generation
Resource-specific performance cannot be monitored; SCE is needed to monitor portfolio performance | Compliance performance can be monitored at Resource-specific level; SCE is not needed in Nodal Market

## Slide 33
Real-Time Market
III. Elements of
Texas Nodal Market
(continued)
6AM
10PM
Why do we have big SCEs in current Zodal Market at 6AM and 10 PM?
In Zonal Market, QSEs try to follow their schedules to minimize SCE, but it is not easy due to the steep schedule changes at 6AM and 10 PM
ERCOT dispatches are based on scheduled generation, Load forecast, and zonal portfolio Ramp Rate
Zonal portfolio Ramp Rate cannot accurately reflect a QSE’s actual ramping capability in a zone
15-min dispatch
Scheduled
Generation
Load Forecast
Dispatches are based on difference between scheduled generation and Load forecast

## Slide 34
Real-Time Market
III. Elements of
Texas Nodal Market
(continued)
SCE is not applicable in the Nodal Market
In Nodal market, dispatches are based on SCADA data and forecasted Load requirement.
5-min dispatch.
Nodal has Resource-specific Ramp Rate Curve. Ramp Rate is modeled more accurately.
6AM
10PM
5-min ERCOT Dispatches
Load Requirement

## Slide 35
Ancillary Service needs are met at Day Ahead through co-optimization of energy and A/S offers and needs in DAM.
ERCOT evaluates and maintains A/S Capacity Sufficiency during the Adjustment Period and in Real-Time
  ERCOT increase the A/S plan
  Replacement of undeliverable A/S due to transmission constraints
  Replacement of A/S due to failure to provide
Supplemental A/S Market (SASM)
  ERCOT shall use SASM to procure the additional quantity required of each A/S, less the quantity self-arranged, if applicable
Ancillary Service Market
III. Elements of
Texas Nodal Market

## Slide 36
Load Zone Types
  Competitive Zones (as 2003 CSC zones)
  NOIE Load Zones
  DC Tie Load Zones
All NOIEs must be either assigned to an appropriate Competitive Load Zone or have made a choice to establish a NOIE Load Zone
The number of NOIE Load Zones may not exceed 20
A DC Tie Load Zone contains the Electrical Bus that connects the DC Tie and is used in the settlement of DC Tie Load in that zone
Load Zones
III. Elements of
Texas Nodal Market

## Slide 37
Load Zone Modifications
  NOIEs can make a one-time choice to establish a NOIE Load Zone 6 months before the Nodal Market implementation date
  Timeline for all other zone changes – 3 years with Board approval
ERCOT shall assign every Electrical Bus to a Load Zone for settlement purposes
New bus addition – assigned to the TNM Load Zone with the closest matching Zonal LMP to the new bus LMP.
SPP for each Load Zone is calculated as the Load-weighted average of LMPs at all Electrical Buses assigned to that zone
Load Zones
III. Elements of
Texas Nodal Market
(continued)

## Slide 38
Congestion Revenue Rights (CRRs) hedge the financial risks of congestion and provide a means to value grid upgrade investments as well.
  PJM: FTRs (Financial Transmission Rights)
  NYISO: TCCs (Transmission Congestion Contracts)
  New England: FTRs (Financial Transmission Rights)
CRRs do not represent a right to receive, or obligation to deliver, physical energy. Most CRRs are tradable in the CRR Auction, in the DAM, or bilaterally.
Congestion Revenue Rights
III. Elements of
Texas Nodal Market

## Slide 39
CRRs may be acquired as follows
  CRR Auction
  PCRR Allocations
  McCamey Area Flowgate Rights Allocations
  Bilateral Market
  DAM
Each CRR is one of these types
  Point-to-point (PTP) Option
  PTP Obligation
  PTP Option with Refund
  PTP Obligation with Refund
  Flowgate Right (FTR)
Congestion Revenue Rights
III. Elements of
Texas Nodal Market

## Slide 40
CRRs must be auctioned in the following blocks
  516 blocks for HE0700-2200, Mon-Fri, one-month strip
  216 blocks for HE0700-2200, Sat-Sun, one-month strip
  78 blocks for HE0100-0600 & HE2300-2400, Sun-Sat, one-month strip
  724 blocks for HE0100-2400, Sun-Sat one-month strip
Each CRR has the following characteristics
  A quantity of one MW
  A duration of one hour
  An ability to be fully tradable financial instruments, except for a PTP Option with Refund or a PTP Obligation with Refund
  A designated source and a designated sink, except for FGR
Congestion Revenue Rights
III. Elements of
Texas Nodal Market

## Slide 41
CRRs will be auctioned annually and monthly.
The CRR Network Model considers/uses
  The same topology, contingencies and operating procedures as used in the Network Operations Model
  Planned outages known to be 16 hours or longer
  Dynamic Ratings
  Peak Load conditions
The Simultaneous Feasibility Test (SFT) provides revenue adequacy by ensuring that the transmission system can support the awarded set of CRRs during normal system conditions.
(continued)
III. Elements of
Texas Nodal Market
Congestion Revenue Rights

## Slide 42
CRR auction revenues are distributed to all ERCOT QSEs representing Load on an ERCOT-wide Load Ratio Share basis
III. Elements of
Texas Nodal Market
(continued)
Congestion Revenue Rights

## Slide 43
What is Nodal?
Why Nodal?
Elements of Texas Nodal Market
Timeline for Implementation
Road Map

## Slide 44
V. Timeline for Implementation
Protocol Contested Case Completion
Telemetry Criteria Met
Outage Scheduler Ready
Network Model Avail. For MP Test
NSA Test Complete
SE 6-Mon Stability Test Criteria Met
CRR Auction Trial Completion
SASM Market Test Completion
SCED 6-Mon Posting of LMPs Criteria Met
2006.1 2007 2008 2009.1
168-Hour Real-Time Market Test Completion
Real-Time Market Operation Ready
RUC Test Completion
DAM Test Completion
Nodal Go-Live