## Slide 1
Creating Reliability in ERCOT through Design

## Slide 2: The Electric Power System
Load
Load
Gen Station
Wind Farms
Gen Station
Gen Station
Line

## Slide 3: Outline
Authority/Responsibility
Transmission Planning
  TDSP
  ERCOT Transmission Services
Operations Planning
  ERCOT Operations Planning
  QSE Operations
Real-time Operations

## Slide 4: What is ERCOT?
Electric Reliability Council of Texas, Inc.
A single point of control, intrastate Electric Interconnection
Public Utility Commission of Texas (PUCT) jurisdictional
82,000 MW of generation
37,000 Miles of transmission
60,157 MW Peak Demand
In existence since 1941
ERCOT is an independent, third party, not for profit organization

## Slide 5: Processes Supporting Reliability

## Slide 6: Authority/Responsibility
  Energy Policy Act of 2005
  FERC & the ERO
  NERC Reliability Authority
  Section 39.151 of PURA requires that Market Participants comply with all “scheduling, operating, planning, reliability, and settlement policies, rules, guidelines, and procedures” established by ERCOT, Inc.
  PUCT Rules – Designated ERCOT, Inc.
  Protocols – Standard form Market Participant agreements require that ERCOT and Market Participants must comply with the Protocols
  Guides – must be followed by Market Participants

## Slide 7: Energy Policy Act of 2005
  16 U.S.C. §824o…:
  “The Commission shall have jurisdiction, within the United States, over the ERO certified by the Commission….”
  “The Commission may certify one such ERO if the Commission determines that such ERO –
    (1) Has the ability to develop and enforce, subject to subsection (e)(2), reliability standards that provide for an adequate level of reliability of the bulk power system…”
FERC-Energy Policy Act of 2005

## Slide 8: Energy Policy Act of 2005
The Electric Reliability Organization shall file each reliability standard or modification to a reliability standard that it proposes to be made effective under this section with the Commission…
The ERO may impose, subject to paragraph (2), a penalty on a user or owner or operator of the bulk-power system for a violation of a reliability standard approved by the Commission under subsection (d) if the ERO, after notice and an opportunity for a hearing-
  (A) finds that the user or owner or operator has violated a reliability standard approved by the Commission under sub-section (d); and
  (B) files notice and the record of the proceeding with the Commission.
FERC-Energy Policy Act of 2005

## Slide 9: FERC-Energy Policy Act of 2005
February 2006 – Commission Finalizes Electric Reliability Rulemaking pursuant to the Energy Policy Act of 2005
  Criteria an entity must satisfy to qualify as ERO
  Procedures under which ERO may propose …standards
  .
  .
  .
  Procedures governing enforcement actions of ERO

## Slide 10: NERC
NERC is a non-profit corporation formed to:
  promote the reliability and adequacy of bulk electric supply by the electric systems of North America;
  develop, implement, and consistent with executed agreement(s) with Regional Councils, enforce standards that provide for an adequate level of reliability of the bulk electric power systems of North America;
  conduct inter-regional studies that relate to the reliability and adequacy of the bulk electric systems and to make information appropriately available;
  encourage and assist the development of inter-regional reliability arrangements …
  provide a voluntary, industry-based alternative dispute resolution mechanism for resolving disputes…
Notes: Note – FERC has already approved NERC’s reliability standards process. – Requires industry review.

## Slide 11: NERC
NERC’s goal is to become certified and begin operation as the ERO in the United States and Canada,
consistent with the Energy Policy Act of 2005 and the rules and requirements of FERC and provincial regulators….
These efforts will result in the formation of an independent, international ERO that will have the authority to develop and enforce reliability standards for the North American bulk electric system.

## Slide 12: Senate Bill 7
May 21, 1999, Senate Bill 7 was passed…
Mandated retail electric competition in Texas.
By January 1, 2002, customers (in some parts of the State) had to have the power to choose their Retail Electric Provider (REP).
Allowed the PUCT to certify ERCOT as the ISO –
  Overseeing grid reliability and operations

## Slide 13: Senate Bill 7; PURA – June 1999
Required a PUCT-approved Independent Organization to:
  ensure access to the transmission and distribution systems for all buyers and sellers of electricity on nondiscriminatory terms;
  ensure the reliability and adequacy of the regional electrical network;
  ensure that electricity production and delivery are accurately accounted for among the generators and wholesale buyers and sellers in the region; and
  ensure that information relating to a customer's choice of retail electric provider is conveyed in a timely manner to the persons who need that information.
Notes: Section 39.151 -

## Slide 14: ERCOT, Inc. (ISO)
ISO in Public Utility Commission regulations Chapter 25 – Substantive Rules applicable to Electric Service Providers:
(b) "Independent organization" means an independent system operator or other person that is sufficiently independent of any producer or seller of electricity that its decisions will not be unduly influenced by any producer or seller.
(c) The commission shall certify an independent organization or organizations to perform the functions prescribed by this section. …
(d) …An independent organization certified by the commission is directly responsible and accountable to the commission. The commission has complete authority to oversee and investigate the organization's finances, budget, and operations as necessary to ensure the organization's accountability and to ensure that the organization adequately performs the organization's functions and duties. The organization shall fully cooperate with the commission in the commission's oversight and investigatory functions. The commission may take appropriate action against an organization that does not adequately perform the organization's functions or duties or does not comply with this section, including decertifying the organization or assessing an administrative penalty against the organization.

## Slide 15: ERCOT Inc. (ISO)
The commission may not implement, by order or by rule, a requirement
that is contrary to an applicable federal law or rule. (d-1)
The commission may:
(1) require an independent organization to provide reports and information relating to the independent organization's performance of the functions prescribed by this section and relating to the organization's revenues, expenses, and other financial matters;
(3) conduct audits of an independent organization's performance of the functions prescribed by this section or relating to its revenues, expenses, and other financial matters and may require an independent organization to conduct such an audit;
ISO in Public Utility Commission regulations Chapter 25 – Substantive Rules applicable to Electric Service Providers:

## Slide 16: ERCOT Inc. (ISO)
The commission may not implement, by order or by rule, a requirement
that is contrary to an applicable federal law or rule. (d-1)
The commission may:
(4) inspect an independent organization's facilities, records, and accounts during reasonable hours and after reasonable notice to the independent organization;
(6) resolve disputes between an affected person and an independent organization and adopt procedures for the efficient resolution of such disputes. (e) The commission may authorize an independent organization that is certified under this section to charge a reasonable and competitively neutral rate to wholesale buyers and sellers to cover the independent organization's costs.
ISO in Public Utility Commission regulations Chapter 25 – Substantive Rules applicable to Electric Service Providers:

## Slide 17: ERCOT Inc. (ISO)
The commission shall investigate the organization's cost efficiencies, salaries and benefits, and use of debt financing and may require the organization to provide any information needed to effectively evaluate the organization's budget and the reasonableness and neutrality of a rate or proposed rate or to evaluate the effectiveness or efficiency of the organization. The commission shall work with the organization to establish the detail of information, both current and historical, and the time frames the commission needs to effectively evaluate a rate or a rate request.
(g) To maintain certification as an independent organization under this section, an organization's governing body must be composed of persons specified by this section and selected in accordance with formal bylaws or protocols of the organization. The bylaws or protocols must be approved by the commission and must reflect the input of the commission. The bylaws must specify the process by which appropriate stakeholders elect members and, for unaffiliated members, prescribe professional qualifications for selection as a member. The bylaws must require the use of a professional search firm to identify candidates for membership of unaffiliated members. The process must allow for commission input in identifying candidates.;
ISO in Public Utility Commission regulations Chapter 25 – Substantive Rules applicable to Electric Service Providers:

## Slide 18: REPs
Substantive Rules applicable to Electric Service Providers
  Technical and managerial resource requirements. As a requisite for providing retail electric service, a REP must have …Technical and managerial resource requirements include:
  (1) Capability to comply with all scheduling, operating, planning, reliability, customer registration and settlement policies, rules, guidelines, and procedures established by the ERCOT independent system operator (ISO), or other independent organization, if applicable, including any independent organization requirements for 24 hour coordination with control centers for scheduling changes, reserve implementation, curtailment orders, interruption plan implementation, and telephone number, fax number, and address where its staff can be directly reached at all times.

## Slide 19: REPs and PGCs
(g) Technical and managerial resource requirements. As a requisite for providing retail electric service, a REP must have technical resources to provide continuous and reliable electric service to customers in its service area and technical and managerial ability to supply electric service at retail in accordance with its customer contracts. Technical and managerial resource requirements include:
  (2) Capability to comply with the registration and certification requirements of the ERCOT ISO or other independent organization and its system rules, or contracts for the purchase of power from entities registered with or certified by the ERCOT ISO or independent organization and capable of complying with its system rules.
  (3) Purchase of capacity and reserves, or other ancillary services, as may be required by the ERCOT ISO or other independent organization to provide adequate electricity to all the applicant's customers in its certificated area…
(i) Suspension and revocation of power generation company registration and administrative penalty.
Pursuant to PURA §39.356,
  (2) For a PGC operating in the Electric Reliability Council of Texas (ERCOT), failure to observe all scheduling, operating, planning, reliability, and settlement policies, rules, guidelines, and procedures established by the independent system operator in ERCOT;

## Slide 20: Transmission
Substantive Rules applicable to Electric Service Providers
  (c) Nature of transmission service. Transmission service allows for power delivery from generation resources to serve loads, inside and outside of the ERCOT region. Service provided pursuant to Division 1 of this subchapter permits municipally-owned utilities, electric cooperatives, power marketers, power generation companies, qualifying scheduling entities, retail electric providers (REPs), qualifying facilities, and distribution service providers (DSPs) to use the transmission systems of the TSPs in ERCOT. Transmission service shall be provided pursuant to Division 1 of this subchapter, commission-approved tariffs, the ERCOT protocols and, for TSPs subject to Federal Energy Regulatory Commission (FERC) jurisdiction, FERC requirements…

## Slide 21: ERCOT Protocols
Each Market Participant in the ERCOT Region must comply with the ERCOT protocols and operating guides.
ERCOT protocols are specifically binding for Transmission providers by statute and PUCT rules.

## Slide 22: NERC Functional Model

## Slide 23: ERCOT Responsibilities – Functional Model
Reliability Authority
Planning Authority
Market Operator
Interchange Authority
Balancing Authority
Transmission Operations
Transmission Planner

## Slide 24: Transmission Planning
Transmission Planning encompasses procedures used to insure that a transmission system is built which meets the reliability standards specified by NERC, the Protocols and ERCOT Guides

## Slide 25: Transmission Planning
The ERCOT Planning Charter defines the planning responsibilities split between Transmission & Distribution Service Providers (TDSP’s) and ERCOT Transmission Services

## Slide 26: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Study and monitor the transmission system for current and future transmission constraints;
  Review generation additions and determine adequacy of generation reserve levels (currently 12.5% or greater);
  Support development and validation efforts for appropriate and accurate modeling of generation, Load and transmission equipment needed to support operations/planning studies and simulations.
  Gather Load data via the Annual Load Data Request (ALDR) process and independently develop its own monthly, annual and long-term Load forecasts;
  Gather generation data via the Generation Interconnection Request Procedures and keep track of existing generation and new generation additions to the ERCOT System;
  Prepare information, studies and reports for various governmental agencies (FERC, PUCT, etc.) and national organizations (NERC, etc.);

## Slide 27: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Perform simulations in order to determine the impact of various transmission line contingencies, Load and generation levels on the reliability of the ERCOT transmission system;
  Execute independent simulation and testing of the transmission system to help investigate possible impacts to reliability and system security;
  Review and assess possible impacts and approve remedial action plans (RAP) and special protection systems (SPS);
  Supervise the processing of all requests for interconnection to the transmission system from owners of proposed new or expanded Generation Resources, including performing or coordinating any applicable system security studies;
  Lead and supervise the three regional planning groups (North, South and West) in the consideration and review of proposed projects to address transmission constraints and other system needs;
  Conduct an open process of public review and comment on all proposed transmission facility additions;

## Slide 28: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Consider new transmission proposals submitted by all interested parties;
  Generate alternatives analysis, including estimated cost comparisons, and recommend beneficial projects/solutions;
  Recommend needed transmission facility additions that are reliability-justified by the ERCOT transmission planning criteria and/or economically-justified by the reduction of congestion and losses or required for integrating new Generation Resources into the ERCOT system;
  Submit all final recommended 345-kV transmission facility additions and, in some special cases, 138-kV additions to the ERCOT Board of Directors for review and concurrence;
  Determine the providers of transmission additions;
  Notify the PUCT of all Board-supported transmission facility additions and their designated providers;

## Slide 29: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Support, to the extent applicable, a finding by the PUCT that a project is necessary for the service, accommodation, convenience or safety of the public within the meaning of PURA §37.056 and PUCT Substantive Rule §25.101;
  Coordinate with the ERCOT Technical Advisory Committee (TAC) Reliability and Operations Subcommittee (ROS) in the performance of steady-state and dynamic simulation testing of the bulk power system to determine the impact on the planned system of occurrences of the types of contingencies listed in the North American Electric Reliability Council (NERC) Planning Standards;
  Work with the Steady-State Working Group (SSWG), Dynamic Working Group (DWG) and System Protection Working Group (SPWG) to model equipment, create databases, perform tests with the TDSPs to evaluate compliance of their transmission facilities with the ERCOT Planning Criteria and recommend further studies if needed;
  Post error correction files submitted by TDSP(s) as soon as reasonably possible;

## Slide 30: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Use a planning process and associated analysis tools that are flexible enough to accommodate the different internal planning, engineering, material procurement, capital budgeting schedules and financial structures of TDSPs;
  Post electronic versions of the annual Federal Energy Regulatory Commission (FERC) 715 Reports, annual FERC Form 1 reports and all annual reports of all planned transmission projects provided by the TDSPs.
  Maintain appropriate and cost effective computer hardware and software to perform all of the above responsibilities in a timely manner to meet stakeholder and ERCOT management objectives.
  Use a planning process and associated analysis tools that are flexible enough to accommodate the different internal planning, engineering, material procurement, capital budgeting schedules and financial structures of TDSPs;

## Slide 31: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Post electronic versions of the annual Federal Energy Regulatory Commission (FERC) 715 Reports, annual FERC Form 1 reports and all annual reports of all planned transmission projects provided by the TDSPs.
  Maintain appropriate and cost effective computer hardware and software to perform all of the above responsibilities in a timely manner to meet stakeholder and ERCOT management objectives.
  Perform Reliability Must-Run (RMR) studies when generation owners notify ERCOT of their intent to mothball, not run or retire existing generating units to determine if RMR status is required to maintain area reliability consistent with the ERCOT Transmission Planning Criteria. Additionally, ERCOT Staff will coordinate with affected TDSP(s) and other interested Market Participants to develop RMR exit strategies to ensure that an overall cost effective plan is developed, reviewed, approved and implemented in an expeditious manner;

## Slide 32: Transmission Planning - Charter
ERCOT Transmission Services shall:
  Facilitate the quarterly communication of changes to project status via the ERCOT Transmission Project & Information Tracking (TPIT). The quarterly updates will be posted on the ERCOT website on March 1, June 1, September 1 and December 1 of each year;
  Facilitate the quarterly update and posting of the SSWG Dataset A and B cases to reflect changes to project status communicated in TPIT. The quarterly updates will be posted on the ERCOT website on March 1, June 1, September 1 and December 1 of each year;
  Post error correction files submitted by TDSP(s) as soon as reasonably possible;

## Slide 33: Transmission Planning - Charter
TDSPs shall:
  Propose appropriate solutions for issues identified by ERCOT including RAPs and SPSs;
  Support analysis and reports needed for the ERCOT Board to make the final decisions on the projects necessary to fulfill PURA and PUCT Substantive Rules obligations;
  Be responsible for obtaining the Certificate of Convenience and Necessity (CCN) and all other required regulatory approvals;
  Make a firm commitment to construct at least three years ahead of required in-service dates for most transmission line projects recognizing that some projects could take five to eight years to accommodate the time for routing studies, CCN approval, right-of-way acquisition and construction.
  Make every effort to adhere to the project schedule to meet the needs as determined by TS and the RPGs;

## Slide 34: Transmission Planning - Charter
TDSPs shall:
  Provide quarterly updates to ERCOT of all transmission project status changes recognizing that transmission planning is a continuous process. The development of any particular project may occur over several months or even years often influenced by unpredictable events;
    Report quarterly and keep up to date all information/documentation relating to its transmission projects (previous, new, and future) in TPIT. These quarterly updates are due one month prior to the dates that ERCOT Staff will post the updates (i.e., February 1, May 1, August 1, and November 1);
    Provide quarterly PTI PSS/E IDEV updates (or PowerWorld® Simulator Auxiliary Files) to the SSWG Dataset A and B cases that reflect the timing and scope change of projects using the most accurate information available to reflect current plans, actual conditions, and ongoing construction activities. These quarterly updates will be due one month prior to the dates that ERCOT Staff will post the updates (i.e., February 1, May 1, August 1, and November 1);

## Slide 35: Transmission Planning - Charter
TDSPs shall:
    Use the most accurate information available to annually assist in building accurate base cases (steady-state, stability and system protection) reflecting actual conditions, on-going construction activities and future additions;
    Submit error corrections to ERCOT as they are identified, with a description and associated PTI PSS/E IDEV file (or PowerWorld® Simulator Auxiliary Files);
  Provide to ERCOT electronic copies of planning criteria (or any basis document or philosophy used to justify transmission additions) and notify ERCOT of any changes within 30 days;
  Provide electronic copies of all generation interconnection requirements and notify ERCOT of any changes within 30 days;
  Provide to ERCOT annual reports of all planned transmission projects;

## Slide 36: Transmission Planning - Charter
TDSP’s shall:
  Provide to ERCOT complete paper and electronic copies of annual FERC Form 1, FERC 714 and FERC 715 filings;
  Provide to ERCOT and other interested Market Participants (upon request) annually updated paper and electronic copies of complete system oneline diagrams. The TDSP may require Market Participants to enter into confidentiality agreements before providing complete system oneline diagrams in order to ensure the protection of this critical energy infrastructure information.

## Slide 37: Regional Planning Groups
ERCOT leads and facilitates three Regional Transmission Planning Groups (North, South and West)
The groups are open to all ERCOT stakeholders
Information about planned transmission projects is distributed to and among members of these groups
These groups provide the means for stakeholders to participate, express concerns, share alternatives and provide input to the ERCOT staff independent recommendation

## Slide 38: Transmission Planning
ERCOT Transmission Services creates base cases in conjunction with TDSP’s modeling the ERCOT transmission system for future years.
The ERCOT Steady State Working Group (SSWG) and Dynamic Study Working Group (DSWG) review and validate these study cases.
TDSPs perform reliability studies on their service areas for future years using these study cases.
TDSPs propose transmission improvement projects to maintain adherence to the ERCOT Guides and NERC planning criteria.

## Slide 39: PLANNING PROCESS
Small Projects - “Tier 1” (60 kV to 138 kV projects)
  Projects requiring a Certificate of Convenience and Necessity (CCN) from the PUCT
    Includes exempt municipal and electric cooperatives projects under what-if test
    Except for any project for which the CCN has been approved or a Public Participation Meeting has already been conducted prior to August 15, 2004
  Projects that have an estimated capital cost greater than $10 million
    To facilitate communication and coordination of projects among the RPG members, members can individually request and review any project below this level
  Projects having a projected in-service date after June 1, 2006
Exempt Projects
  Construction to connect a new substation or accommodate Load growth in an existing substation
  Replacement of line terminal equipment, such as switches, current transformers, circuit breakers and wave traps
  Addition or replacement of reactive power sources (capacitors and reactors) not capable of dynamic response

## Slide 40: PLANNING PROCESS
Large Projects - “Tier 2” (345 kV and higher projects)
  Any projects requiring PUCT certification (CCN)
    Includes exempt municipal and electric cooperatives projects under what-if test
    Except for any project for which the CCN has been approved or a Public Participation Meeting has already been conducted prior to August 15, 2004
  ERCOT Staff independent review/study
  Submit to ERCOT Board for endorsement
Exempt Projects
  Construction to connect a new substation or accommodate Load growth in an existing substation
  Replacement of line terminal equipment, such as switches, current transformers, circuit breakers and wave traps
  Addition or replacement of reactive power sources (capacitors and reactors) not capable of dynamic response

## Slide 41: Deliverable
The Planning process delivers to Operations a transmission system which meets the NERC and ERCOT reliability standards

## Slide 42: Operations Planning
Operations Planning begins each year asking the question: What do we need to do to operate the transmission system securely.
  Looks ahead to the coming seasons and reviews:
    RAPS
    SPS
    RMR contracts
    Procures Black Start Resources
Operations planning examines the transmission system using a power-flow model completely independent of the planning model. Much work is done to provide consistency between these models

## Slide 43
BREAK TIME

## Slide 44
Months - Weeks
Ahead

## Slide 45: ERCOT Operations Support Security Activities
MAR
JUN
AUG
Review Remedial Action Plans and Mitigation Plans
Summer Voltage Set-points sent
Winter Voltage Set-points sent
JAN
Black Start RFP sent
Timeline
T-60
T+60
1800
Day Ahead
OCT
DEC
Monthly Adequacy Assessments
Notes: <number>
<footer>
<header>
<date/time>

## Slide 46: (Operations) Network Modeling
Network Modeling accepts TDSP changes to the network model describing changes taking place to the ERCOT Transmission Grid
The Operations Network Model created by this group is created independently of the planning model

## Slide 47: Network Modeling

## Slide 48: Network Modeling

## Slide 49: Database Load
Database loads are roughly every 2 weeks and require about 60 man-hours /load

## Slide 50: Operations Support
Each Season, analyzes voltage set points using planning cases and minimizing the post-contingency voltage violations for expected conditions
Each year, reviews all existing Remedial Action Plans (RAPS), validates, and determines if new RAPs should be proposed using both operations and planning power flow analysis of peak case
VOLTAGE SETPOINTS & RAP REVIEW

## Slide 51: Operations Support
Each year, ERCOT uses a Black Start RFP to solicit interest of Market Participants in providing Black Start service
Operations Support reviews each response, programs the proposal into an assessment program and identifies the least-cost method of meeting ERCOTs Black Start requirements
Operations Support recommends procurement, drafts black start plan, directs/observes Black Start Resource testing and issues certificates
BLACK START

## Slide 52: Operations Support
After each database load, prepares Load flow base cases for use by outage coordinators in analyzing planned outages
  - Confirms that contingency analysis results are reasonable and that no N-1 contingency violation that cannot be relieved by a documented RAP exists with an intact transmission system
Validates Contingency lists
Validates State Estimator results
DATABASE LOAD & CASE PREPERATION

## Slide 53: Outage Coordination
Uses the base case provided after each database load to generate cases describing expected conditions
  45 days out
  9 days out
  3 days out
These cases are used to study planned outages under N-1 contingency outage conditions
  If post-contingency overloads appear:
    RAPs
    Investigates re-dispatching Generation Resources
Notes: State importance of “good faith” outage estimating.

## Slide 54: Operations Support
EACH MONTH –
  Analyze Regulation Service deployments over the last month and the equivalent month from the previous year and determine how much Regulation Service needed hour-by-hour to be sufficient for that hour 98.8% of the time (2.5 standard deviations)
  Perform similar calculation for down balancing calculation with a target of avoiding running out 99.9% of intervals
  Calculate maximum LAAR contribution towards RRS
  Post requirements
ANCILLARY SERVICE REQUIREMENT CALCULATION

## Slide 55: Review Regulation Calculation
U = 60.85, Std dev = 372.32

## Slide 56
Day Ahead

## Slide 57: ERCOT Market Activities
1300
1330
1600
1800
QSEs submit schedules & bids
ERCOT validates
AS Bid Clearing
Resource Plan Validation
Close RPRS market
0600
AS Bid process closes
AS Process Starts
QSEs update schedules & Resource Plans
Day Ahead Timeline
CSC Limit Calculation
In the Day-Ahead, ERCOT:
  Procures Ancillary Services
  Validates Resource Plans
  Arranges for additional capacity
  Calculates CSC limits based upon planned outages & generation plans
  Executes voltage stability studies on vulnerable areas
  Executes Transient Stability studies on vulnerable areas (currently developing implementation)
Notes: <number>
<footer>
<header>
<date/time>

## Slide 58: Operations Support
Each Day, ERCOT operations support
  Generates a power flow case predicting conditions for the next day
  Performs contingency analysis on this power flow
  Increases stress (transfers) from
    South-North
    West-North
    NE-North
    South-Houston
    North-Houston
    Getaway from McCamey
  Repeating N-1 contingency analysis for each case until a post-contingency violation is detected
    this sets the CSC transfer limit
Daily CSC Limit Calculation

## Slide 59: Operations Support
Each Day, operations support
  Performs repeated import studies into the Corpus Christi area, Houston area, Rio Grande Valley and Dallas area to determine if the planned generation pattern leaves these areas exposed to voltage collapse risk
Voltage Stability Calculation

## Slide 60
Adjustment Period

## Slide 61: During the Adjustment Period
Day-ahead operators create power-flow studies of expected peak conditions for the next day and perform contingency analysis on these cases
Operators monitor projected reserves for the next 24 hours and expected Balancing Energy capacity available

## Slide 62: During the Adjustment Period

## Slide 63: Monitor Reserves

## Slide 64
Current Day

## Slide 65: Operating Period Time Line - ERCOT Functions
ERCOT Activities
Review MAI (Capacity)
Arrange for additional AS & capacity, if needed
Operator Power flow studies
Perform system analysis to forecast security problems
Issue Dispatch Instructions for reserves and congestion relief
Real-time Balancing Energy deployment
Regulation Service deployment
15 min. real time interval
Hour Ahead
Operating Hour
Operating Period
1800 Day Ahead
0900
1000
1100
Adjustment Period
. . .
Day Ahead
1015
1030
1045
Notes: For the operating day, the EMMS is used as follows:
Adjustment period:
  Verify adjusted schedules
  Analyze need for additional AS and Replacement Reserve and procure
Operating period
  Hour ahead
    Perform forecast system security analysis
    Issue deployment instructions for reserves and congestion relief
  Operating hour
    Execution of real-time balancing market clearing for subsequent interval
    Regulation for current interval (AGC)

## Slide 66: Hour Ahead Study
Each hour, a study of the 4 approaching dispatch periods is performed and reviewed for shortages of required Ancillary Services or energy

## Slide 67: Hour Ahead Study

## Slide 68: Balancing Energy Service Deployment
From short-term Load forecast, the estimated Load for the next interval is obtained
From the Resource Plans, all Generation Resources are mapped into the constraint equations
Balancing Energy is deployed to make the sum of generation match the forecast Load plus offset and satisfy congestion constraint equations
How Balancing Energy Service Deployment Works

## Slide 69: Real-time Balancing

## Slide 70: Why State Estimator?
Early in the history of using digital computers for control of transmission systems, it was envisioned that a “real time” power flow could be created to take the existing SCADA measurements and create a power flow study which closely matched actual conditions
  - Most of these attempts failed
Analysis revealed that many of the SCADA measurements were in error
  - No valid power flow solution could match all of the SCADA measurements
State Estimators were designed to resolve these differences and produce a set of “states” (i.e. voltage and angles) reflecting the current state of a transmission system

## Slide 71: State Estimator Support
From SCADA, a set of measurements is developed which should be consistent with power flow topology
Mathematically, we set each bus with an estimated Voltage and Angle and calculate the flows between the buses
We move the estimated voltage and angle to minimize the difference between the “estimated” flow and the SCADA-measured flow until the sum of differences is a minimum
How State Estimator Works

## Slide 72: State Estimator Support
20 MW m1
20 MW SE1
18 MW m3
23 MW SE3
18 MW m2
20 MW SE2
43 MW m4
43 MW SE4
47 MW m5
43 MW SE5
A
B
C
Using power flow equations, estimate the voltage and angle at each bus.
Calculate the difference between SCADA flow and estimated flow – this is the residual
Adjust the voltage & angles to minimize the sum of the residuals
In this example: Bus B is initially estimated as 137.4 < -2.47, Bus A is initially estimated as 137.15 < -3.52 kV
With this estimate, the residual of m1 is 2 mw, m2 is 0 mw, m3 is 7 mw, m4 is 0 mw, and m5 is 4 mw; for a sum of residuals of 13 MW
But: if we estimate m1 as 20 mw, m2 as 20 mw, m3 as 23 mw, m4 as 43 mw, and m5 as 43 mw, the residuals are 0, 2, 5, 0 and 4, for a sum of 11 MW.
How State Estimator Works

## Slide 73: State Estimator/RTCA
Given this State Estimator solution, it is fairly simple to create a power flow consistent with this set of “states”
That power flow may now be used to perform repeated power flow studies or “contingency analyses”
We refer to the process of analyzing the N-1 security of the real-time transmission system for outage of each defined contingency - one at a time - as “real-time contingency analysis”

## Slide 74
State Estimator Views

## Slide 75
State Estimator Anomalies

## Slide 76: State Estimator Mismatch

## Slide 77: RTCA with SPS & RAP

## Slide 78: RTCA with SPS & RAP

## Slide 79: Real-Time Voltage Stability Analysis
Using the State Estimator solution, ERCOT analyzes vulnerable areas for potential voltage collapse as a part of the real-time sequence
Vulnerable areas (Houston, DFW, Corpus, Rio Grand Valley) are studied under increasing stress conditions until a post-contingency voltage collapse is detected

## Slide 80: Real-Time Voltage Stability Analysis

## Slide 81: What the TO Does
Monitor voltage and direct switching of reactive devices
Direct changes to voltage set points in real-time
Monitor line loading and alert ERCOT to real-time problems
Advise ERCOT on reliability issues
Operate Switching equipment
Design/Maintain transmission equipment including protective relaying
Install and maintain SCADA
Schedule transmission outages

## Slide 82: Post Analysis
Event Investigation Trigger
  After specified events, an investigation by operations staff is automatically triggered and a report generated
Repeated Congestion investigation
  If congestion occurs more than twice on a single element, an investigation of ratings and root cause is triggered
Monthly Congestion report
Daily operations report
Daily Market operations report

## Slide 83: Other Items
Stakeholder Interface
  ROS discussion of reliability impact
  WMS discussion of market impact
  PRS discussion of proposed Protocol and guides changes
  Working groups: SSWG, DWG, OWG…
Projects
Market support and training

## Slide 84: Someone is watching us…
Compliance Audits
NERC audits
SAS 70 audits
PUCT review
Market Monitor
Internal Audits