## Slide 1: QSE Roles & Responsibilities
Voltage/Reactive - Support & Control
Jason Sweeney, Suez Energy

## Slide 2: KEY DEFINITION #1
“Qualified Scheduling Entities”…
MPs qualified by ERCOT in accordance with Protocol 16 (“Registration and Qualification of Market Participants”), to submit Balanced Schedules and Ancillary Services bids…
[Protocol 2.1]

## Slide 3: KEY DEFINITION #2
“Ancillary Services”…
Those services (described in Protocol 6) necessary to support transmission of energy from Resources to Loads, while maintaining reliable operation of…transmission systems, in accordance with Good Utility Practice.
[Protocol 2.1]
Notes: (…by the way, do keep this “Good Utility Practice” reference in mind…we will be re-visiting that concept later on.”)

## Slide 4: KEY DEFINITION #3
“Voltage Support Service”…
An Ancillary Service…required to maintain transmission/distribution voltages on the ERCOT Transmission Grid, within acceptable limits.
[Protocol 2.1]

## Slide 5: KEY DEFINITION #4
“Reliability Must Run (RMR) Unit”…
A Generation Resource…operated under…an Agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability, or management of localized transmission constraints…where Market Solutions do not exist.
[Protocol 2.1]
Notes: (“Now, my point in going through these four definitions is to show at the very outset a key common thread, here…
…QSEs – which all tolled number ~150 – provide the A/S that are critical to system reliability, overall…
…and two of these services – VSS and closely related RMR – are critical to system voltage, specifically…
…so, it is this common thread between QSEs and voltage stability that I will be explaining in depth today…
…but first, I do want to press on with the background discussion we’ve started…”)
(“Now, a little history on reactive power in ERCOT…”)

## Slide 6: REACTIVE POWER – THEN & NOW
Before ERCOT shifted to Single CA (01 Aug 2001), voltage stability locally managed by the 10 different CAs
After Aug/01, voltage stability market-managed, with ERCOT in the lead, and TOs coordinating daily/directly with QSE-Generation
ERCOT now requires QSE-Generation to be available for Voltage Support; when/if the QSE cannot perform, it strains the system
Notes: (“So, its important to emphasize that ERCOT expects QSE generation to respond when TOs call for voltage support…
…and speaking of QSE’s and their generation, some discussion is warranted now on the sizable footprint they have come to represent in Texas…”)

## Slide 7: QSE FUNDAMENTALS
QSE-generation capacity has increased by 47.5% since 1996
[PUCT’s “2003 State of the Market Report for the ERCOT Wholesale Electricity Markets”, August 2004]
~30 QSEs own and/or operate the ~78,000 MWs of installed capacity in ERCOT
[ERCOT System Planning’s “Report on Capacity, Demand, and Reserves in the ERCOT Region”, June 2005]

## Slide 8: VOLTAGE MGMT vs. FREQUENCY MGMT
Basic difference…
Voltage management is at the local level, between QSEs & TOs
Frequency management is system-wide, between QSEs & ERCOT
Notes: (“Moving on to our Second Course Objective, identifying the basic relationship between managing voltage versus managing frequency…
…now the reason I bring up frequency in a presentation on voltage is because more folks seem familiar with frequency than with voltage, probably because the majority of A/S are geared toward frequency…
…so by comparing the two, I expect folks to get their arms around voltage a little better…”)

## Slide 9: VOLTAGE MGMT vs. FREQUENCY MGMT (cont)
Similarities…
QSE-Resources’ Automatic Voltage Regulators (AVRs) are the most important tool in TOs controlling voltage
QSE-Resources’ Governors are the most important tool in ERCOT controlling frequency

## Slide 10: VOLTAGE MGMT vs. FREQUENCY MGMT (cont)
More similarities…
All QSE-Resources’ AVRs must be in-service …QSEs must notify ERCOT anytime AVRs are taken out-of-service
All QSE-Resources have a governor response requirement…QSEs must notify ERCOT anytime Generation Resources go off AGC

## Slide 11: REACTIVE POWER – PROVIDERS
QSE-Generators are ERCOT’s primary source of dynamic reactive power
TOs are ERCOT’s primary source of static reactive power
Between the two…QSE-Generators are faster, more responsive source of reactive power
Notes: (“We’re now going to turn to the First Course Objective, identifying the primary source of reactive power in ERCOT…”)
(“and just what makes these generators the “primary” source of dynamic reactive power?”)
(“recalling my 3-legged barstool, though, I want to point out that QSEs are hardly alone in providing reactive…
…TDSPs meanwhile are helping the cause, too, deploying their own capacitive or inductive devices to generate or absorb reactive power, respectively.”)

## Slide 12: VSS – who is “draft-eligible”?
All QSE-Generators…
    greater than 10 MWS & 20 MVA
    that supply power to the ERCOT System
    that are online
…are required to provide VSS, and collectively share in reactive support and voltage reliability
[Protocols 6.5.7, 6.5.7.2(6) and Guides 3.1.4, 3.1.4.1]

## Slide 13: VSS – a collective effort
Generation Resources should bear only their “approximate proportion to their respective installed reactive capability requirements” of reactive support because…
…ERCOT & TOs are to “minimize dependence on generation-supplied reactive Resources”
[Protocols 6.7.6(3), 6.7.6(2)]

## Slide 14: VSS – The Voltage Profile
Voltage Profile…
Generation Resources’ individual reactive performance profiles
ERCOT requires VPs for all Generation Resources, in order to maintain proper system voltages
Calculated by ERCOT & TOs at the high-voltage side for all generation busses
ERCOT posts on MIS, so QSEs know ERCOT’s desired voltage/reactive, for specific Generation Resources
[Guides 2.10.1, 2.5.1 and Protocols 6.4.2(6), 6.5.7.3(2)]

## Slide 15: VSS – The Unit Reactive Limit
URLs…
Generation Resources’ reactive capability is measured by URL
URL is a given quantity of reactive produced at a given quantity of active – Resource-specific
URL is calculated/derived at the Generation Resource’s maximum net power, during the Generation Resource’s Reactive Capability Test
[Protocols 6.5.7.1(1), 6.5.7.1(2) and Guide 3.1.5]

## Slide 16: VSS – The URL (cont)
URLs…
URLs are calculated twice during the Reactive Capability Test…
  at over-excited (lagging) power factor of 95% or less
  at under-excited (leading) power factor of 95% or less
ERCOT uses Generation Entity-supplied URLs to formulate the Voltage Profile for that Resource
[Protocol 6.5.7.1(2) and Guide 3.1.5]

## Slide 17: VSS – QSE / Gen volume requirements
Generation Resources shall produce/maintain a minimum/defined quantity of Reactive Power, at rated MW-capability
Quantity is to be within design limits of machine, at/below URL
Quantity will be dictated by ERCOT, by way of the Voltage Profile ERCOT schedules for that Resource
[Protocols 6.1.7, 6.5.7.1(1), 6.5.7.2(1), 6.7.6(4) and Guides 3.1.5, 2.10.4.1, 3.1.4.1, 2.3]

## Slide 18: VSS – QSE / Gen response requirements
QSEs shall meet / respond to ERCOT’s temporarily modified Voltage Profiles (within Resource’s Reactive Power characteristics / tolerances / limits)
In the event of violation of “coordinated” Voltage / Reactive Criteria – ie, “stable” voltage / reactive criteria – ERCOT may modify Dispatch Instructions
[Protocols 6.5.7.2(5), 6.4.2(6) and Guides 3.1.5, 2.10.4.1, 2.3, 4.3]

## Slide 19: VSS – QSE / Gen response req’s (cont)
Generation Resources must respond to ERCOT or TO voltage adjustments, if deployed within URL capacity limits
Generation Resources/QSEs must also respond if reliability is at risk and ERCOT issues a VDI that violates URL, and/or reduces Active Power output
[Protocols 6.7.6(1), 6.8.4(1) and Guide 2.10.4.2]

## Slide 20: VSS – QSE / Gen response req’s (cont)
Generation Resources should expect reactive Dispatch Instructions direct from ERCOT anytime system voltage levels deviate from established limits
[Guide 2.10.2]
ERCOT-declared emergencies…at ERCOT’s direction, QSEs may issue manual voltage dispatches to Generation Resources (for reactive or active power)
Generation Resources must respond with “best efforts”
[Guide 3.1.4.1]

## Slide 21: VSS – QSE / Gen response req’s (cont)
TO-declared emergencies…at TO’s direction, Generation Resources must respond to TO voltage dispatches
QSEs to receive notification from TO, post-emergency
[Guide 2.10.4.1]

## Slide 22: VSS – Generation Resources operational req’s
Generation Resources must perform maintenance and operations consistent with Good Utility Practice
[Guide 3.1.4]
May not reduce high reactive capability during abnormal conditions without ERCOT pre-approval…and only in event of imminent equipment damage
[Protocol 6.5.7.1(9)]
May not replace/modify equipment that impacts Reactive capability without pre-approval by ERCOT…ERCOT & TO must be notified by QSE at least 60 days out
[Protocol 6.5.7.1(8) and Guide 3.1.4.1]

## Slide 23: VSS – Gen / QSE operational req’s
AVRs & Power System Stabilizers (PSSs) to be kept in service whenever possible
QSEs must promptly notify ERCOT as to change in status of AVRs & PSSs (i.e., going off-line/on-line, change from Voltage Control mode), and log accordingly
[Protocol 6.5.7.2(4) and Guides 2.2.4(4), 3.1.4.1, 3.1.4.5]
Generation Resources should understand that their AVR status & PSS status are monitored by ERCOT
[Protocol 6.10.9(2) and Guide 2.2.1]

## Slide 24: VSS – Gen/QSE op’l req’s (cont)
QSEs must meet VSS deployment performance requirements
Generation Resources with voltage performance problems must notify TOs immediately (so TOs can alert ERCOT to potential voltage problems)
[Guide 2.10.2 and Protocol 6.7.6(6)]
QSEs must advise ERCOT when Generation Resources not operating within Power Factor range (as required, specified in ERCOT’s Voltage Profile)
[Protocol 6.5.7.2(7) and Guide 2.10.4]

## Slide 25: VSS – Gen/QSE op’l req’s (cont)
Generation Resources with high reactive loads/oscillations must notify QSE, TO, and ERCOT immediately
Generation Resources that trip off-line due to voltage/reactive problems must notify ERCOT, TO and QSE immediately
[Guide 3.1.4.1]

## Slide 26: VSS – QSE data/telemetry req’s
QSEs must telemeter Reactive Power data to ERCOT on all its portfolio assets, in real-time…to include Generation Resource MVARs (gross or net), plus voltage at interconnection to Grid
[Protocols 6.5.1.1(1), 6.5.1.1(1)(b) and Guide 3.1.4]
Generation Resource has direct impact on local system voltage…Generation Resource therefore telemetered to TO, so TO may monitor/direct the Resource
[Guide 2.10.4.1]

## Slide 27: VSS – Testing req’s
Generation Resource VSS requirements actually begin at the site development stage, as the Guides state that the resource shall be “designed” consistent with its VSS obligations
[Guide 3.1.4.1]
Generation Resources must meet technical standards in Protocols 6.10 for A/S Qualification/ Testing & Performance
[Protocol 6.5.7.2(3)]

## Slide 28: VSS – Reactive Capability Tests
Generation Resources must verify/maintain Reactive Power capability, by way of Unit Reactive Capability Tests every two years (for both Lagging & Leading)
[Protocols 6.10.3.5(1), 6.10.3.5(2) and Guides 3.1.4.3(1), 3.1.4.3(2)]
Two types of Reactive Capability Tests…
  Non-Coordinated Reactive Test
  Coordinated Reactive Test

## Slide 29: VSS – Non-Coordinated Reactive Test
Non-Coordinated Reactive Test…
QSE requests ERCOT Operations Engineer to conduct test on 2 hours notice, for 15-minute duration (minimum)
[Guide 3.1.4.3.2]
Non-Coordinated/Lagging Test…conducted at/above 95% of max net output, during high System Loads at temps greater than 90F
[Protocol 6.10.3.5(3) and Guides 3.1.4.3(3), 3.1.4.3.2]
Non-Coordinated/Leading Test…conducted during low System Loads at off-peak hours in the Spring
[Protocol 6.10.3.5(4) and Guides 3.1.4.3(4), 3.1.4.3.2]

## Slide 30: VSS – Coordinated Reactive Test
Coordinated Reactive Test…
QSE requests ERCOT Operations Engineer and TO to conduct test on 48 hours notice, for 15-minute duration (minimum)
[Guide 3.1.4.3.3]
Coordinated/Lagging Test…conducted at/above 95% of max net output, during high System loads at temps greater than 90F
[Protocol 6.10.3.5(3) and Guides 3.1.4.3(3), 3.1.4.3.3]
Coordinated/Leading Test…conducted during low System loads at off-peak hours in the Spring
[Protocol 6.10.3.5(4) and Guides 3.1.4.3(4), 3.1.4.3.3]

## Slide 31: VSS – The “D-Curve”

## Slide 32: VSS – AVR & PSS Tests
Generation Resources must conduct new AVR Tests every five years
[Protocol 6.10.3.5(5) and Guide 2.2.4(4)]
Generation Resources must conduct new PSS Tests every five years
[Guide 2.2.4(4)]

## Slide 33: VSS – performance / compliance / enforcement
Performance measures for RPRS, Black Start, VSS treated separately from other A/S…
[Protocol 6.10.4.1]

## Slide 34: VSS – performance / compliance / enforcement (cont)
…QSEs must respond to ERCOT’s Voltage VDIs within 2 minutes
[Protocol 6.10.9(1)]
…QSE failures to perform to VSS instruction will be investigated by ERCOT-Compliance (for non-compliance vs. Force Majeure vs. ERCOT-permitted deviation)
[Protocol 6.10.9(3), 6.10.9(5), 6.5.7.3(4)]

## Slide 35: VSS – performance / compliance / enforcement (cont)
…Generation Resource AVRs (& PSSs) must be in-service and in “Voltage Control” Mode at least 98% of time the resource is on-line
(except when ERCOT directs QSE to be in “Manual Mode”, or when Unit is going online/offline)
[Protocols 6.10.9(2), 6.5.7.2(4) and Guides 2.2.4(4), 3.1.4.5]
…QSE failure to maintain voltage within 2% of scheduled voltage, when operating at less than URL, may be referred to ERCOT-Compliance
(except in event of Force Majeure or ERCOT-permitted deviation)
[Protocol 6.10.9(4) and Guide 2.10.4]

## Slide 36: VSS – performance / compliance / enforcement (cont)
…Reactive Capability Testing…Compliance Template on enforcement of Reactive Testing located at ERCOT-Compliance website
[Guide 3.1.4.3.5]
…AVR Testing…if QSE fails to conduct every five years, ERCOT to notify QSE…if QSE fails to respond within 30 days, ERCOT to notify PUCT
[Guide 3.1.4.4]

## Slide 37: PRR409 – “Voltage Support Service”
Generation Resources must provide VSS without compensation, whether deployments are within/outside resource URLs
Dispatches that actually reduce Active Power schedules are to be settled at OOME Down price
[Protocols 6.8.4(1), 6.8.4(2)]

## Slide 38: PRR409 (cont)
Generation Resources must provide VSS up to URL at 95% Power Factor, without compensation
[proposed in PRR409…for Protocol 6.8.4(1)]
Generation Resources responding to ERCOT Dispatch Instructions above URL would be compensated for avoided cost of VSS
[proposed in PRR409…for Protocol 6.8.4(2)]
Generation Resources reducing Active Power schedules to provide VSS would be compensated at OOME-Down
[proposed in PRR409…for Protocol 6.8.4(3)]

## Slide 39: Reliability Must Run
RMR…
Agreements between Resource Entity and ERCOT (12 mos max) for capacity/energy from otherwise uneconomic Resources
Generation Resources would not run if not necessary for voltage support, stability, local congestion management
  [Protocols 6.1.9, 6.3.1(8), 6.5.9(5) and Guides 2.4.5.3(5), 2.4.5.3(6), 2.4.5.3(10), 2.5.1, 2.5.1(8)]

## Slide 40: Reliability Must Run (cont)
QSE RMR Units…deployed/dispatched by ERCOT for Emergency Conditions or to prevent violating System security limits
ERCOT shall deploy RMR when no Market Solution exists, and only to extent necessary to correct voltage
[Protocols 6.1.9, 6.3.1(17), 6.5.9(3), 6.5.9(10), 6.7.8(1) and Guides 2.3, 2.3.1, 2.4.5.3(3), 2.4.5.3(12), 2.5.1(17)]
If QSE fails to perform “expected quality of firmness”, ERCOT to charge the QSE an “Unexcused Misconduct Amount” as defined in the RMR Agreement
[Protocol 6.8.3.8(1)]

## Slide 41: Reliability Must Run (cont)
QSEs submit RMR Availability Plan to ERCOT by 0600 Day-Ahead
QSEs receive ERCOT’s RMR Dispatch Instructions, via Messaging System…
  Initial Delivery Plan by 0900 Day-Ahead
  Updated Delivery Plan by 1630 Day-Ahead
[Protocols 4.5.11.1, 6.7.8(4) and Guide 2.4.5.3]
QSEs should follow Resource Plan SOP for registering Generation Resources, as related to RMR Units
[Protocol 4.5.11.2]

## Slide 42
ANY QUESTIONS???