## Slide 1
Black Start Plan
Stan Morris / Jack Thormahlen
2006 Annual Operations Seminar
Notes: Jack Thormahlen
Senior Power System Analyst
Lower Colorado River Authority
Welcome to the 2006 Seminar Black Start Presentation

## Slide 2
Introduction
What is this plan all about?
What are the Black Start Services?
What are the Black Start units?
How do we select these Black Start units?
How do we use them in the restoration process?
What shall I do during the restoration process?
And what are my responsibilities?

## Slide 3
Objectives
At the completion of this course you will:
Recognize the criteria used to select and qualify Black Start units.
Identify your roles as a market participant during the restoration process.
  Principles
  Strategies
  Priorities
  Responsibilities
Power System Concepts.

## Slide 4
Black Start Services
Black Start services are needed in the event of partial or complete collapse of electric system.
These services are provided by a set of contracted Black Start capable generation units.
These resources are re-evaluated annually.

## Slide 5
Black Start Units
These Black Start capable units are able to self-start without support from outside power.
Within close proximity of another power pools such as SPP, CFE, and WECC which are capable of starting from such power pool via a firm standby power supply contract can be qualified as a Black Start service.
Notes: Definition of Black Start Unit and Black Start Service that qualifies as a Black Start Unit.

## Slide 6
Black Start Unit Selection
Every year, black-start capable Resources entities submit their proposals to provide Black Start services for next year.
ERCOT uses the following selection criteria to select a set of units with minimum cost:
  Simulated restoration of 90% of ERCOT peak load within 48 hours.
Notes: Introduction of Jack and his presentation on the bidding, selection process.

## Slide 7: The Life and Times of a Black Start Unit
Bidding
Black Start Resource Awarding Process
Black Start Resource Testing
The Certificate
Notes: We will now review the overall process of ERCOT acquiring the necessary black start services.
We will review the bidding process, the evaluation and awarding, the testing requirements and the piece of paper that tells you that you were successful.

## Slide 8: Bidding
ERCOT Develops the RFP
  1) January 1 through March 31 of each year
  2) Based on latest Protocol language implementation
  3) Based on needed procedural improvements as developed by the BSTF and ERCOT
  4) Schedule –
      - April1 thru June 1 – Black Start Resources prepare RFP responsive bids
      - June 2 thru July 31 – ERCOT evaluates bid proposals
      - Aug 1 – Black Start Resources awarded
      - Aug 2 thru Dec 31 – Black Start Resource required testing
      - Jan 1 thru Mar 31 – ERCOT Prepares RFP
Notes: Jan thru Mar of each year ERCOT reviews and refines the RFP to acquire the necessary black start capable generators that will restore the ERCOT grid should a large area or state wide blackout occur. This acquisition is one of the requirements and principles stated in the NERC ELECTRIC SYSTEM RESTORATION
Reference Document written and approved by the NERC Operating Committee. The principle reads –
Each control area should have a readily accessible and sufficiently detailed current system restoration plan to guide in an orderly recovery. System restoration will be aided by communicating to neighboring control areas, and to Regional offices, an accurate assessment of system conditions throughout the restoration process. Communication must be established with power plants, critical substations, and neighboring operation centers. Mutual assistance and cooperation are essential and beneficial to prompt system restoration and to avoid the recurrence of a partial or complete electric system collapse.
In the event of an electric system collapse, each control area should use the following as guiding principles for the restoration process:
1. Take immediate steps to initiate internal system restoration plans.
2. Restore a high percentage of internal load in as little time as possible.
3. Provide assistance to any and all control areas as system conditions allow.
4. Supply neighboring control areas and Regional offices with information on electric system status.
Coordinate with neighbors the reconnection of control areas and/or islands.
One of the latest Protocol changes that has been implemented for the black start resources is the requirement for additional testing. This testing language grew out of discussions and concerns that the ERCOT black start plan could not actually start the next start unit.
Each year, ERCOT and the BSTF review and modify the RFP for such things as adding evaluation criteria. This was done in the RFP some two years ago after BSTF discussions with ERCOT. It should be said that the BSTF, because it is made up of Market Participants, can not make ERCOT change the RFP. If ERCOT decides that the suggestion is good for all including ERCOT, then they may make suggested changes.
As you can see by the schedule, it takes the entire year to request bids, evaluate bids and test the awarded resources. This is then the black start plan at the beginning of each year.

## Slide 9: Bidding
Prospective Black Start Supplier
  1) Prepares the RFP Response proposal between April 1 and June 1 of each year
  2) Evaluates the cost of the required testing
  3) Evaluates the serviceable schedule of the unit for the entire year
  4) Evaluates the marginal cost to provide the standby service required by the Black Start Contract
  5) By June 1 the Supplier will submit to ERCOT the Units being offered and the bid price in $ per hour stand-by price
Notes: When ERCOT sends the RFP out to prospective bidders, generation controlling QSEs, on April 1, the QSEs have till June 1 to prepare their bids for black start service, if they have a unit that meets the black start criteria. The black start criteria is specified under several Protocol sections, specifically Section 6.1.8, 6.10.3.6, 6.10.10 and Section 22A. In addition, specific guides for black start service are located in the Operating Guides Section 4.6 and Attachment 4A.
During the bidding process, the QSE and the black start resource must evaluate the different costs that will be encountered to meet all testing criteria and operational criteria. Assessing these parameters and evaluating their own risk profiles determines the marginal cost that the bidder will use for its bidding strategy.
Additionally, the resource will need to know its operational and maintenance schedule for the entire year that is bidding for. If a contracted unit exceeds more than 15 % of the year as unavailable, the Black Start Contract has language that reduces the payment that a black start unit receives. Also, if a black out occurs and the black start unit fails to start up and begin the restoration of the system, the contracted black start unit stops receiving its hourly payments from ERCOT and has to pay back all payments received for that contracted year.

## Slide 10: Black Start Resource Awarding Process
ERCOT Resource Evaluation
1) June 2 thru July 31 – ERCOT evaluates bid proposals
2) Black Start Resource Selection Criteria
      Group selection
        Bid price ($/hour)
        Amount of MW pickup (MW)
        Restoration time (hours)
      Specific resource selection
        Black Start MW, next-start MW capacity, start-up time
        Proximity to nuclear plant 2nd criteria
        Proximity to load centers 3rd criteria
Notes: After receiving the bids for black start service form the market participants, ERCOT has from then, June 1 till July 31 to evaluate all the bid proposals.
In order to more objectively evaluate the bid proposals, ERCOT has developed a program in Access. This program takes the data contained in the proposals and develops a set of black start units that will meet a pre-established set of criteria.
There are two distinctive parts to the evaluation. The first part is the group selection process. In this process it will pick the units by the least cost per MW, the amount of MWs that can be restored by that set of units in the quickest amount of time.
Once that is done, the evaluator checks to see that the nuclear plants can meet their 4 hour restart criteria and that all the major load pockets have black start units in relative close proximity.

## Slide 11: Black Start Resource Awarding Process
ERCOT Resource Evaluations
2) Black Start Resource Selection Criteria – cont.
      Example
Notes: Let’s look at the over view of the 2006 evaluation.

## Slide 12
Group Selection Results
This group selection has met the first and third criteria but it has not met the second criteria, they are :
  Simulated restoration of 57000 MW within 60 hours.
  Expected restoration off-site power to nuclear resources within 4 hours.
  Proximity of Black Start resources to major load centers.
2006 Black Start Services
Slide taken from ERCOT presentation to BSTF at its Aug 2005 meeting
Notes: This table is the Access generated list of black start units that met the initial evaluation criteria. As you can see, when ERCOT checked the list for the nuclear restoration criteria, it was found that Comanche Peak was not meeting that criteria. You can also see that the criteria of black start units in close proximity to major load centers was met.

## Slide 13
Tentative Transmission Corridor Map
2006 Black Start Services
Slide taken from ERCOT presentation to BSTF at its Aug 2005 meeting
INTENTIONALLY BLANK
Notes: This slide shows the area that is deficit

## Slide 14
Specific Resource Selection
The closest Black Start resource to
Comanche Peak plant is Decordova.
Plant | Black Start MW | Next-Start MW | Hot Start-up Time | Cold Start-up Time
DCSES | 70 | 1028 | 0.25 | 0.5
2006 Black Start Services
Slide taken from ERCOT presentation to BSTF at its Aug 2005 meeting
Notes: As is noted by this slide, the closest black start unit to Comanche peak is Decordova. This unit was put into the Access program as a no-cut unit and reran.

## Slide 15
Preliminary 2006 Black Start Services
2006 Black Start Services
This group selection has met all 3 criteria, they are:
  Simulated restoration of 57000 MW within 60 hours.
  Expected restoration off-site power to nuclear resources within 4 hours.
  Proximity of Black Start resources to major load centers.
Slide taken from ERCOT presentation to BSTF at its Aug 2005 meeting
Notes: The results of the rerun using Decordova as a must have unit yielded the results seen here. Now all the Group Criteria and the specific selection resource criteria are met.

## Slide 16: 2006 Black Start Services
Selection Results Comparison
Notes: As can be seen in this slide, the insertion of Decordova (DCSES) as a must have unit realigned the other black start units and removed LCSES, Spencer and WFcogen and the program added Amistad and Steam.
Because of this one must have insertion and rerunning the program, the total cost is about $ 2m less that the original selection.
Just as a comment, ERCOT attempted to the restoration in 48 hours and found that the total cost was much higher than the original total cost of the 60 hour restoration time.

## Slide 17
2006 Black Start Services
Slide taken from ERCOT presentation to BSTF at its Aug 2005 meeting
INTENTIONALLY BLANK
Notes: And here is the back bone black start system that ERCOT believes will be able to restore the system if a total black out occurs.

## Slide 18: Black Start Resource Testing
Procedure and Schedule
3) The test will be scheduled between September 1st, 2005 and November 1st, 2005. The remaining months are reserved for re-testing those resources fail at the first time.
2) All preliminary 2006 Black Start resources should submit their detailed test procedures and tentative test schedule, no later than August 31st, 2005.
1) All testing of Black Start Resources are to be completed between September 1 and December 31
Notes: There are a number of test that a black start unit must pass before an Agreement can be signed with ERCOT. The unit has from September 1 thru December 31 to pass these tests.
Each selected resource must submit the detailed test procedure and a tentative test schedule to ERCOT no later than August 31.
The test schedule for the initial testing should be between September 1 and November 1.
As a general rule, November is reserved for retesting those units that were unable to pass the tests the first time. This allows the unit to fix what ever the problem was.

## Slide 19: Black Start Resource Testing
Procedure and Schedule – cont.
4) ERCOT witnesses will be provided, by the plant testing coordinator, the following information:
● A briefing of the testing procedure provided prior to
August 31
● Location in the control room of equipment such as:
- Black Start unit terminal or high-side voltmeter
- Unit RPM meter
- Unit frequency meter
- Unit MW output meter or load pick-up meter.
Notes: During the black start test, there will be at least one ERCOT witness. The ERCOT witness will be briefed upon arrival about the testing procedure to make sure they are aware of all the details of the procedure.
There will be certain equipment and meters that the ERCOT witness will monitor during the test. The plant coordinator will be shown the location of those pieces of equipment and meters prior to the start of the test.

## Slide 20: Black Start Resource Testing
Types of Testing
Notes: Prior to the 2006 testing period, there had been three (3) required test that a black start unit had to perform. The three tests are not necessarily performed every year.
By Protocol the basic start test is performed each time a black start unit is selected.
The Line energizing test is performed every three (3) years.
And the load carrying test is performed every six (6) years.
For the first time, the 2006 testing requirements added the test that proves that the black start unit can start the largest motor of the next start unit or actuall start the next start unit. Either is acceptable.
The Protocols allow two ways of testing the largest motor of the next start unit or start the next start unit. That could either be accomplished by physically starting the largest motor of the next start unit or start the next start unit or providing an appropriate study that computer simulates the starting the largest motor of the next start unit or start the next start unit.
As can be seen in the table, all but three (3) units physically tested the black start and next start units.

## Slide 21: Black Start Resource Testing
Success Rate
    For 2003 the first-test success rate was 87.5% and the second-test success rate was 100%.
    For 2004 the first-test success rate was 100%.
    For 2005 the first-test success rate was 87.5% and the second-test success rate was 100%.
    For 2006 the first-test success rate was XXXX% and the second-test success rate was XXXX%.
Notes: The test success rate has been 100 % since the ERCOT market has been established. As you can see, 2003 and 2005 had some units that had to retest for one reason or other. There are some discussions within the BSTF to limit the number of time that a resource will be allowed to retest. Stay tuned for the results in 2006.

## Slide 22
Notes: This is the certificate that a black start resource receives when it successfully completes all the required testing for the contract year.

## Slide 23
?
Questions?
Notes: Questions????

## Slide 24
2006 Black Start Plan
In the event of a major system disturbance it is necessary to have procedures in place to cope with events and restore the system to normal state as quickly as possible.
ERCOT Black Start Plan incorporates restoration effort in case of partial or complete collapse of electric system.

## Slide 25
2006 Black Start Plan
What is in the Black Start Plan?
  Black Start map and transmission corridors
  Principles
  Strategies
  Priorities
  Responsibilities
    ERCOT
    TOs
    QSEs
    Resources
Notes: Physical makeup of the plan include these items

## Slide 26
Black Start Plan - Principles
Contracted Black Start Units
Local TO Plans
  Primary/secondary transmission corridors
  Designated synchronization points, primary and alternatives
Mutual assistance and cooperation
Restore the power system

## Slide 27
Black Start Plan - Principles
Example of Transmission Corridor
INTENTIONALLY BLANK

## Slide 28
Black Start Plan - Principles
Each contracted Black Start Plant and TO will have an internal Black Start Plan.
Plans identify Black Start units, primary and secondary Next-Start units, stabilizing loads, primary and secondary transmission corridors and synch points between islands.
The power system, not customers, is the principle focus during the restoration effort.

## Slide 29
Black Start Plan - Strategies
It is ERCOT’s opinion that all necessary information shared with affiliates for the restoration process is an allowed corporate support service under the provisions of PUCT rule 25.272.
In the event of total ERCOT blackout, the market is suspended.
28 contracted Black Start resources.
15 Black Start sites/islands.

## Slide 30
Black Start Plan - Strategies
The initial 15 islands will be built and maintained solely under the direction of the TOs as outlined in the TO Black Start Plans.
The TOs will be responsible for maintaining the appropriate voltage levels and reactive controls.
The TOs should periodically update ERCOT on the status of the islands during the restoration process.

## Slide 31
Black Start Plan - Strategies
These updates should coincide with the following events:
  A Black Start unit is brought on line.
  Any additional unit that is brought on line.
  A designated synchronization point between islands is reached.
  The TO needs to energize a piece of equipment that belongs to another TO.
  Any time a collapse or regression occurs in the restoration process.

## Slide 32
Black Start Plan - Priorities
Determine system conditions:
  Restore and maintain communications.
  Reliable communication will be the key to a safe and timely restoration.
If the primary communication is down, the backup system will be used.
Transmission corridors prepared to support restoration.
Secure and stabilize generating plants.

## Slide 33
Black Start Plan - Priorities
Communication paths:
ERCOT
TO
TO
PGC
TO
PGC

## Slide 34
Black Start Plan - Priorities
Contracted Black Start units will immediately bring their units on line.
Designated TOs will begin building islands to reach designated synch points.
Critical load priority:
  Nuclear generating facilities.
  Other generating units.
  ERCOT.
  Military and law enforcement facilities.
  Public health and communication facilities.

## Slide 35
Responsibilities - ERCOT
Maintain surveillance of ERCOT system status.
Central information collection and dissemination point.
Coordinate reconnection of transmission.
Direct the connection of separated islands.
Direct assistance for QSEs, TOs, PGCs, and market Particpants.

## Slide 36
Responsibilities - TO
Provide necessary personnel to assure capability of Black Start Plan restoration.
Coordinate communications for local Black Start units.
Coordinate switching to Next Start units and local load.
Act as a regional ERCOT representative in coordinating inter-connections of units.
Follow the direction of ERCOT for reconnection of islands.

## Slide 37
Responsibilities - QSE
Determine fuel options and capability of both Black Start units and Next Start units.
Supply ERCOT and/or local TO with information on the status of generation facilities that they represent.
Follow direction of TO or ERCOT in picking up load and starting Next Start units.
Provide assistance as directed by ERCOT or the local TO.

## Slide 38
Responsibilities - PGC
Black Start sites must first secure and stabilize on site generation that has tripped.
Communicate condition of Black Start/Next Start units to local QSE.
Communicate condition of fuel, water, and station service.
Implement Black Start Plan at the direction of TO/ERCOT.

## Slide 39
Concepts - Black Start Units
Timing is critical.
The coordination problem of re-energizing the grid is complicated.
Hydro, Combustion Turbines and Thermal Plants are likely Black Start units.
Generators have min. and max. load limits and max. ramp rates (MW/minute).
The balance of load and generation is very difficult when both are changing rapidly.

## Slide 40
Concepts - Generators
Plant operators will be controlling system frequency during initial stages of restoration.
AVRs should be placed in service as soon as practical to improve machine stability.
AGCs should be placed in automatic position to ensure instantaneous governor response to changes in load.

## Slide 41
Concepts - Transmission System
The transmission system itself presents a dynamic reactive load.
Transmission lines are highly capacitive when not loaded and voltages can easily become excessive.

## Slide 42
Concepts - Transmission System
Generators and reactors are used to hold voltages down.
Unfortunately, generators are less stable when they are absorbing reactive power.

## Slide 43
Concepts – Cold Load Pick-up
Initial load magnitude will be greater after energization.
Initial inrush currents can be ten or more times than the normal load current magnitude.

## Slide 44
Concepts – Energizing Lines
Carry at least 50% reserve with only a single generating unit on-line.
Keep at least 20% reserve once a second generating unit comes on-line.
Avoid closing a weak source into a fault possibly resulting in the loss of a unit.
Voltage regulators could be placed at lower than nominal set points prior to energizing lines to avoid over voltage due to line charging capacitance.

## Slide 45
Concepts – Synchronizing Point
When synchronizing two islands you must ensure the voltages are matched.
Synchronizing variables:
  Voltage magnitude difference.
  Voltage phase angle.
  Frequency difference.
Synch-check relay determines if the voltage, frequency and phase are matched.

## Slide 46
Concepts – Synchronizing Point
Synchroscopes are used to match the frequency and voltage phase angle.

## Slide 47
Summary
15 Black Start Islands.
ERCOT and TO Black Start Plans.
  Principles
  Strategies
  Priorities
  Responsibilities
Review system and equipment concepts.

## Slide 48
References
1. ERCOT Protocols
2. ERCOT Operating Guides
3. TO Local Black Start Plans
4. NERC Operating Guides.

## Slide 49
Questions
?
?