## Slide 1: Formulas & Factors in understanding Power Systems
Robin Boehnemann
ERCOT
Market Operations Support

## Slide 2: MATH

## Slide 3: Objectives
Discuss mathematical concepts related to
  Hertz
  Frequency Response Characteristic (bias)
  Time error
  Ramp rates
  Stated line values
  Active, reactive, and complex power
  Shift factors

## Slide 4: Frequency
How do we control this bulk power system?
  Maintaining scheduled frequency
Normal scheduled frequency is 60 Hz
  Hertz (Hz) is defined as the unit for frequency equal to one cycle per second
  60 Hz = 60 cycles per second

## Slide 5: Hertz
1 cycle = 1 sine wave
60 Hz = 60 sine waves per second
60 Hz = 1 sine wave every 1/60th of a second

## Slide 6: Maintaining control
Maintaining scheduled frequency is a basic responsibility of a system operator
However, maintaining a constant scheduled frequency is impossible due to the continuous change of the Load
Load is never constant, therefore, there will be an imbalance between generation and Load

## Slide 7: Maintaining control
Maintaining control within acceptable bandwidth is necessary to prevent
  Equipment damage
  Islanding/separation

## Slide 8: Frequency Response Characteristic (Frequency Bias)
Part of NERC ACE equation
Part of ERCOT ACE equation
Given in MW/0.1 Hz
Relates the MW response of the system to a change in frequency
Current ERCOT Bias = 489.00 MW/0.1 Hz

## Slide 9: Frequency Response Characteristic (Frequency Bias)
For a contingency resulting in a frequency decrease, approximately 489 MW will need to be deployed to raise frequency by 0.1 Hz
The real-time frequency bias value will vary following a frequency disturbance because it depends on the system conditions at the time of the disturbance
  Generating Resources currently on-line
  magnitude of the Load
  transmission lines in service
  as well as other many other factors

## Slide 10: Frequency Response Characteristic (Frequency Bias)
Example:
Scheduled frequency = 60.00 Hz
Loss of generation causes frequency to drop to 59.67 Hz
Using 489 MW/ 0.1 Hz
60.00 Hz – 59.67 Hz = 0.33 Hz decrease in frequency
Notes: For simplicity, governor response not considered.

## Slide 11: Time error
The imbalance between generation and Load leads to time error
ERCOT schedules time correction and notifies Market Participants
Math to remember:
  +0.02 Hz to gain 1.2 seconds per hour
  -0.02 Hz to lose 1.2 seconds per hour
Notes: Keeping in mind that with the constant changing of load, operator can only estimate how long a time correction will be in effect base on the current time error. The new scheduled frequency will be just as hard to maintain as the normal 60 Hz.

## Slide 12: Ramp Rates
Ramp rates are given in MW/min
Provided to ERCOT in BES bids and Resource Plans
ERCOT has 10 minute ramping period
Mismatch ramp rates result in inability to maintain scheduled frequency
  Time Error

## Slide 13: BES Ramp Rates
Example 1:
QSE A submits UBES bid in South Zone:
0–550 MW Ramp rate = 20 MW/min.
1330: QSE A deployed 200 MW UBES in South
Considering ramp rate and MW bid ONLY:
At 1345 QSE A could deploy another 200 MW for total of 400 MW or recalled to 0 MW
1345: QSE A deployment = 350 MW UBES in South
Notes: Example assumptions:
NO price consideration
NO violations
No congestion
Will not cross 0 in ramp rate recall (due to time weighted ramp rates for UBES and DBES ramp rates)

## Slide 14: BES Ramp Rates
Example 2:
QSE X submits UBES bid in North Zone:
0–300 MW Ramp rate = 10 MW/min.
0145: QSE X deployed 250 MW UBES in North
Considering ramp rate and MW bid ONLY:
At 0200 QSE X could deploy another 50 MW for total of 300 MW or recalled 100 MW to 150 MW
0200: QSE X deployment = 150 MW UBES in North
Notes: Example assumptions:
NO price consideration
NO violations
No congestion
Will not cross 0 in ramp rate recall (due to time weighted ramp rates for UBES and DBES ramp rates)

## Slide 15: Mismatched Ramp Rates
QSE A sells 200 MW to QSE B
QSE A must raise output by 200 MW
QSE B must lower output by 200 MW
Rates of adjustment should be the same
If QSE A ramp rate higher, frequency will be higher than scheduled frequency
If QSE B ramp rate higher, frequency will be lower than scheduled frequency

## Slide 16: Line values
If voltage is alternating how do we derive the values by which we call lines?
  69kV, 345kV, etc.
Need effective value of AC
  The DC equivalent of AC
Notes: When current flows through resistance, electric energy is converted to heat.
Need to determine effective value of AC line.
Find relation between AC and DC values so relative efficiency of energy conversion can be determined.

## Slide 17: Line values
Max/peak value of AC is called amplitude. Sine wave has both positive and negative peaks, but magnitude is the same.

## Slide 18: Line values
The amplitude is used to calculate the effective value of AC, called the root mean square (RMS).
RMS = amplitude ÷ = (amplitude)(~0.707)
Notes: All 3 phase systems are fairly well-balanced. Therefore can analyze one phase equivalent because once one phase is know, the others are identical in magnitude, separated by 120º.
RMS value is single or phase-phase in 3 phase system. Phase to ground = RMS X √3.
Again, this RMS value is the effective value of AC, the DC equivalent.
Most voltmeters and ammeters are calibrated in RMS values.
How was this determined?
Math, of course!

## Slide 19: Line Values
IDC = 1 amp
IAC MAX = 1 amp
=
+50º
+25º
DC circuit
AC circuit
IAC = IAC MAX ÷
IAC = (IAC MAX)(~0.707)
Divide both sides by R
Take sq root of both sides
Substitute
= power used to heat resistor for both AC and DC
Notes: When current flows through resistance, electric energy is converted to heat.
Need to determine effective value of AC line.
Find relation between AC and DC values so relative efficiency of energy conversion can be determined.
Passed current through equivalent resistors for same amount of time. Compared the two temperature increases, which effectively gives the power loss ratio between the two.
RMS voltage cause same heating effect as equivalent DC voltage. It effectively produces same amount of work.
When alternating current or voltage is specified it is always RMS value that is meant, unless stated otherwise.

## Slide 20: Line values
RMS = 345kV
Amplitude =
RMS ÷ 0.707
Amplitude =
345kV ÷ 0.707
Amplitude = 487.9kV
Amplitude = 487.9kV

## Slide 21: Line values
RMS = 69kV
Amplitude =
RMS ÷ 0.707
Amplitude =
69kV ÷ 0.707
Amplitude = 97.60kV
Amplitude = 97.60kV

## Slide 22: Active, Reactive, & Complex Power
P = Active Power (True Power)
  power dissipated by Load, measured in watts (W, MW)
Q = Reactive Power
  provided and maintained for explicit purpose of insuring continuous, steady voltage on transmission networks, produced for maintenance of system and not produced for end-use consumption, measured in volt-amps-reactive (VAR, MVAR)
S = Complex Power (Apparent Power)
  both dissipated and absorbed/returned power, measured in volt-amps (VA, MVA)
Notes: Only giving brief definition. This presentation only covers the math portion. There is a presentation on Wednesday that will cover the theory.

## Slide 23: Active, Reactive, & Complex Power
(theta) = Phase angle
  taken at a single point in the system – it is the difference in phase between the current and the voltage waves and can vary from one point in a power system to another
= Power factor
  =
(delta) = Power angle
  Difference between the phase angles at two points
Notes: Only giving brief definition. This presentation only covers the math portion. There is a presentation on Wednesday that will cover the theory.

## Slide 24: Active, Reactive, & Complex Power
P = Active Power (MW)
Q = Reactive Power (MVAR)
S = Complex Power (MVA)
Notes: Relationship between complex, active, and reactive power.
Remember Pythagorean’s Theory (adding as vectors) =
(Complex power)2 = (Active power)2 + (Reactive power)2

## Slide 25: Active, Reactive, & Complex Power
P = Active Power (MW)
Q = Reactive Power (MVAR)
S = Complex Power (MVA)
S = 500 MVA
P = 400 MW
Q = ? MVAR
Notes: Relationship between complex, active, and reactive power.
Remember Pythagorean’s Theory (adding as vectors) =
(Complex power)2 = (Active power)2 + (Reactive power)2

## Slide 26: Power Factor
θ
P = Active Power (MW)
Q = Reactive Power (MVAR)
S = Complex Power (MVA)
Notes: Goal is to have high pf, therefore having the highest possible level of MW (MW = $$$).
Operating with low pf actually creates “penalty” on power source. Might be unable to provide sufficient active power to consumers if needed to produce large amount of MVARS (reactive power) to provide voltage support for highly inductive load. In general most consumers’ loads tend to be inductive.
Generators have leading power factor when absorbing VARS, lagging when providing VARS.
Unity pf = 1 = max active power => active power = complex power. Only possible in purely resistive circuit => current and voltage in phase.
Unity pf not possible in bulk power systems; practical transmission lines contain resistance, inductance (series inductance through length of line), and capacitance (btwn conductors and btwn conductors and ground; and distributed throughout length of line). VARS will flow whenever inductance and capacitance are present: Inductance absorbs VARS and capacitance supplies VARS. When inductance/capacitance added, current and voltage become out of phase => pf<>1.

## Slide 27: Power Factor
θ
P = Active Power (MW)
Q = Reactive Power (MVAR)
S = Complex Power (MVA)
S = 500 MVA
P = 400 MW
Q = 300 MVAR

## Slide 28: Phase Angle and Power Angle
Phase angle = (theta)
  Single point – phase difference between voltage and current
Power angle = (delta)
  Between two points – the difference in phase angles
Notes: Power angle throughout system:
Always keep in mind that voltage phase angle difference exists across each element of power system and varies according to:
impedance of element
amount of power transfer through element
In actual practice, under normal operating conditions, δ never approaches 90º. Max maybe 40º across entire system.

## Slide 29: Active Power Equation
Remember: P is active power (MW) and under current ERCOT Protocols, Market Participants are paid only for active power (not reactive power); therefore it is easy to understand the Market Participants’ objective of wanting to maximize active power.
HOWEVER, a power system contains inductance and reactance, and therefore, will have reactive power.
In order maintain stability in the power system both active and reactive power must be produced.
Notes: Rule of thumb: Active power normally flows from points where the bus voltage is more leading to points where bus voltage is more lagging.
P=Active Power
VS = Sending end voltage
VR = Receiving end voltage
X=series reactance
δ = POWER angle – between two points in the system – it is the voltage angle between two locations in the power system

## Slide 30: Max Active Power
PMAX is the maximum active power a system is electrically capable of transmitting regardless of stability concerns
To determine PMAX sin( ) = 1 ( =90º)
(1)
Notes: P=Active Power
VS = Sending end voltage
VR = Receiving end voltage
X=series reactance
δ=power angle
To determine PMAX δ must = 90°, therefore sin(90°) = 1
However, in normal system conditions, δ is less than 20°, sin(20°) = 0.34 and decreases as angle decreases.
Power angle throughout system:
Always keep in mind that voltage phase angle difference exists across each element of power system and varies according to:
impedance of element
amount of power transfer through element
In actual practice, under normal operating conditions, δ never approaches 90º. Max maybe 40º across entire system.

## Slide 31: Max Active Power
Max Active Power is NOT an obtainable value in a real power system
Power angle ( ) will NOT = 90º in a real system, under normal conditions
Should max active power transfer be reached any further increase will cause instability
Notes: Power angle throughout system:
Always keep in mind that voltage phase angle difference exists across each element of power system and varies according to:
impedance of element
amount of power transfer through element
In actual practice, under normal operating conditions, δ never approaches 90º. Max maybe 40º across entire system.
If it were possible, operating at δ = 90º, means operating at steady state stability limit => NOT ACCEPTABLE operating point because ANY system disturbance, no matter how minor, could cause loss of synchronism => islanding, separation

## Slide 32: Active Power Equation
Example:
Notes: Rule of thumb: Active power normally flows from points where the bus voltage is more leading to points where bus voltage is more lagging.
P=Active Power
VS = Sending end voltage
VR = Receiving end voltage
X=series reactance
δ = POWER angle – between two points in the system – it is the voltage angle between two locations in the power system

## Slide 33: Active Power Equation
Notes: Rule of thumb: Active power normally flows from points where the bus voltage is more leading to points where bus voltage is more lagging.
P=Active Power
VS = Sending end voltage
VR = Receiving end voltage
X=series reactance
δ = POWER angle – between two points in the system – it is the voltage angle between two locations in the power system

## Slide 34: Reactive Power Equation
Reactive power, like active power, depends on the value of .
However, reactive power takes the cosine (active power takes the sine), so as approaches 0, cosine ( ) approaches 1.
Notes: VS = sending voltage
VR = receiving voltage
X = impedance
δ = power angle
XC = capacitive reactance – total for the line
(VS2)/(XC) represents line charging. (Higher the line voltage, the greater the line charging. Line charging increases at light loads.)
For now, we will ignore the line charging.
The equation then becomes…

## Slide 35: Reactive Power Equation
X
(VS2)/(XC) represents line charging.
The higher the line voltage, the greater the line charging.
For now, we will ignore the line charging.
The equation then becomes…
Notes: VS = sending voltage
VR = receiving voltage
X = impedance
δ = power angle
XC = capacitive reactance – total for the line
(VS2)/(XC) represents line charging. (Higher the line voltage, the greater the line charging. Line charging increases at light loads.)
For now, we will ignore the line charging.
The equation then becomes…

## Slide 36: Reactive Power Equation
(1)
Notes: The reactive power transferred between two points is now determined by the voltage magnitudes at the two points, the impedance, and the cosine of the power angle between the two points.
In normal system conditions, the power angle between two connected buses is small. If δ (delta) is small (<20°), the cosine δ term will be very close to one. If we assume that the power angle stays small then the reactive power transfer equation can be simplified even further.
FYI:
IF δ = 10°, cos (10°) = 0.9848 sin (10°) = 0.1736
IF δ = 20°, cos (20°) = 0.9397 sin (20°) = 0.3420
IF δ = 40°, cos (40°) = 0.7660 sin (40°) = 0.6428
Cosine δ becomes ~1 (and therefore, can be left out of the equation).

## Slide 37: Reactive Power Equation
Which, after factoring, becomes this:
Notes: Cosine δ becomes ~1 (and therefore, can be left out of the equation).
The critical part of this equation is (Vs – VR). The voltage difference between the source and the load is the driving force behind MVAR flow. The higher the voltage difference (voltage drop), the higher the MVAR flow.
Adding VAR resources to the power system, increases the voltage drop between two elements, therefore increasing the reactive power. Voltage is highly dependent on MVAR flow. Low voltage on system => need more reactive power (high loads). High voltage on system => need to absorb VARS (light loads => line supplying VARS)
Reactive power does normally flow from the high to the low voltage bus.
When power angles exceed approximately 20°, the rule of thumb that reactive power flows from high to low voltage no longer applies. Reactive power CAN flow from the low to high voltage bus if the power angle between the buses is large.

## Slide 38: Active and Reactive Equations
Phase angle = (theta)
  Single point – phase difference between voltage and current
Power angle = (delta)
  Between two points – the difference in phase angles
Notes: Ideally, want as much active power (P) to flow as possible, however, in reality, there must be both active and reactive power in a power system.
Both active and reactive power depend on the value of the power angle. Under normal conditions, power angle is relatively small: 40 or below.

## Slide 39: Active, Reactive, & Complex Power
P = Active Power (MW)
Q = Reactive Power (MVAR)
S = Complex Power (MVA)
Notes: Relationship between complex, active, and reactive power.
Remember Pythagorean’s Theory (adding as vectors) =
(Complex power)2 = (Active power)2 + (Reactive power)2

## Slide 40: Shift Factors
Measure of the effect of power injection on transmission element(s)
Factors impacting shift factors:
  Line length
  Number of paths (outages)
  Line capacity
Two calculation examples
  Assumptions:
    Part of a larger system
    Drawing NOT to scale
Notes: Have software that will automatically determine shift factors or can figure it out manually

## Slide 41: Shift Factors
Example 1:
X

## Slide 42: Shift Factors
Example 1:
X
Gen 1: min=225MW max=400 current=250MW
Gen 2a: min=300MW max=800 current=600MW
Gen 2b: min=300MW max=800 current=600MW
Line Initial Post cont Rating
138-5 200MVA 0MVA
345-1 460MVA 600MVA 550MVA
Gen1 up 100MW = 3MVA relief Shift factor = -0.03 = -3%
Gen2a down 100MW = 20MVA relief Shift factor = 0.20 = 20%
Gen2b down 100MW = 20MVA relief Shift factor = 0.20 = 20%
Move Gen2a and Gen2b a total of 250MW down to relief the 50MVA overload.
Check: Gen2a and Gen2b have ability to move down 600MW total.

## Slide 43: Shift Factors
Example 2:
X

## Slide 44: Shift Factors
Example 2:
Gen 1: min=225MW max=400 current=250MW
Gen 2a: min=300MW max=800 current=600MW
Gen 2b: min=300MW max=800 current=600MW
Line Initial Post cont Rating
138-2 125MVA 0MVA
138-1 125MVA 200MVA 150MVA
Gen1 down 25MW = 15MVA relief Shift factor = 0.60 = 60%
Gen2a up 100MW = 10MVA relief Shift factor = -0.10 = -10%
Gen2b up 100MW = 10MVA relief Shift factor = -0.10 = -10%
Can only move Gen 1 down 25MW to min of 225MW.
X
Move Gen2a and Gen2b total of 350MW up to relieve the additional 35MVA.
Check: Gen2a and Gen2b have ability to move up 400MW total.

## Slide 45: Recap
Hertz
Frequency Bias
Time error
Ramp rates
Stated line values
Active, reactive, and complex power
Shift factors

## Slide 46: Sources and credits
ERCOT Fundamentals
Power System Operation, Third Edition
Fundamental Knowledge, ISO – New England
Basic Electricity, Revised Edition, Complete Course
www.energyvortex.com
Jim Bowles for music editing
Chad Thompson for help with examples and reviewing