## Slide 1: Further Voltage/Reactive Concepts

## Slide 2: Further Voltage/Reactive Concepts
Where to Turn on Capacitors
Voltage Collapse
Voltage Stability Analysis

## Slide 3: Where to Turn On Capacitors
Turn Them on Close to the Load (Largest Effect)
Demonstration Follows

## Slide 10: Effect of Capacitors
Capacitors Have the Greatest Effect Closest to the Load.

## Slide 11: What is a Voltage Collapse?
Informal definition: A blackout caused by a power system going past its nose point.
Notes: Now we have to understand Nosepoint

## Slide 12: DC
+10V
Rt=10
Rl
Notes: Voltage collapse often thought of as an AC phenomenon.
Can happen in a DC system
Simple example
Ideal 10V power source
10 Ohm “Transmission Line”
Variable resistance load

## Slide 13
Rl | Rtotal | I | Vl | Pl
Infinite |  |  |  | 
90 |  |  |  | 
40 |  |  |  | 
30 |  |  |  | 
15 |  |  |  | 
10 |  |  |  | 
8 |  |  |  | 
5 |  |  |  | 
1 |  |  |  | 

## Slide 14
Rl | Rtotal | I | Vl | Pl
Infinite | Infinite | 0 | 10 | 0
90 | 100 | 0.1 | 9 | 0.9
40 | 50 | 0.2 | 8 | 1.6
30 | 40 | 0.25 | 7.5 | 1.875
15 | 25 | 0.4 | 6 | 2.4
10 | 20 | 0.5 | 5 | 2.5
8 | 18 | 0.555 | 4.44 | 2.47
5 | 15 | 0.667 | 3.33 | 2.22
1 | 11 | 0.909 | 0.909 | 0.826

## Slide 15: Power vs Load Impedance

## Slide 16: Voltage vs. Power Transfer
Nose Point

## Slide 17: DC Example (Base case)
+10V
Rt=50
Rt=50
Rt=50
Rt=50
Rt=50
Rtotal=10
Pload = 2.22W
Rload = 20

## Slide 18: DC Example (Contingency)
+10V
Rt=50
Rt=50
Rt=50
Rt=50
Rtotal=12.5
Rload = 20

## Slide 19: DC Example Contingency

## Slide 22: AC Case is Similar
Nose point higher than 0.5
  Vectors
Reactive Power plays a Large Role
  Capacitors
  Reactive Capability of Units
  Reactive Consumption of Transmission Lines

## Slide 23: AC Example (Basecase)
Generation
Area
Load
Area
500 kV, 250km, 0.32 /km Reactive
80  per line
5 lines

## Slide 24: AC Example (Contingency)
Generation
Area
Load
Area
500 kV, 250km, 0.32 /km Reactive
80  per line
4 lines

## Slide 25: Voltage vs. Load for simple example

## Slide 26: Capacitors can help
Better if at load center
  Difficult/impossible to transmit VArs
Extend nose point
  Higher loads possible w/o voltage collapse
Makes system more “brittle”
  Moves nose point to higher voltages.
  Could collapse at 1 pu!!!
Following slide shows the addition of 6000MVAr capacitor to load

## Slide 27
Curve with Cap
Banks Switching on
All Cap Banks on at
All Times

## Slide 28: Support from Generators is Better
Real Power reduces flow over lines and reduces Reactive consumption
Reactive Power (VArs) boosts voltage in surrounding area
  Reactive power from generators not a function of voltage
Following slide shows comparison of 6000 MVArs from the generator and 6000 MVArs from a Cap Bank

## Slide 29
Curve with Cap
Banks Switching on
Generators with AVRs
at 1 pu.

## Slide 30: Maintaining Safety Margin (OG 5.1.4)
Voltage stability margin shall be sufficient to maintain post-transient voltage stability within a defined importing (Load) area under the following study conditions:
  Peak Load conditions, with import to the area increased by five percent (5%) of the forecasted area Load, and NERC Category A or B operating conditions (see NERC Table I in ERCOT Planning Criteria); and
  Peak Load conditions, with import to the area increased by two and one half percent (2.5%) of the forecasted area Load, and NERC Category C operating conditions.

## Slide 31: Safety Margin
VC
2.5%
5%

## Slide 32: Under Voltage Load Shedding
Drops load if voltage goes too low (Voltage Collapse)
Safety Net (Try not to use it)

## Slide 33: VSAT (Voltage Stability Analysis Tool)

## Slide 34: What Does VSAT Do?
Increases Power
Generation
Increases Load
Increasing Transfer

## Slide 35: What Does VSAT Do?
VSAT stresses a system until it breaks
VSAT can stress a system in 4 ways
  Decrease load in one area and increase generation in another (Gen-Load transfer)
  Decrease generation in one area and increase it in another (Gen-Gen transfer)
  Decrease load in one area and increase it in another (Load-Load transfer)
  Implements contingencies (Used in all 3 types of transfer)
“Break” is defined as voltage collapse