ERCOT Meter Working Group Meeting

Agenda

Meeting Date: May 11, 2006

Location: ERCOT Met Center

Austin, TX

Conference Room 168

If needed:

Call in Number: (512) 225 – 7282 pswd 1166 (8 ports)

9:30 – 9:35: 	Reading of ERCOT Anti trust rules.

Dotty DiSanto read anti trust rules.

9:35 – 9:40: 	Opening Business from Chairman – Dotty DiSanto

9:40 – 10:00:	Review of MV-90 Xi update – How’s the New MV90 Tims are working - 			Pat Vinton

    - The Q1000 and Jemstar do not contain all event codes required by SMOG.

      - Only one (1) Jemstar currently installed and is a Backup meter.

      - DME will work with vendor to include events in TIM – Pat Vinton will contact DME.

    - ION and Transdata Mark V contain all codes and meet current SMOG requirements.

    - AEN and CPS will follow up with Q1000 vendor to include events codes in TIM.

    - Should a deadline be imposed for vendor to include events?

      - AEN has discussed with ITRON the possibility of using a different meter type.

    - CPS raised issue of possibly removing Power Up code as a requirement.  The event can be obtained from meter and supplied to MDAS for editing purposes.

      - Depending on follow up with ITRON, this may be submitted as a SMOGRR to the MWG for review.

    - DST discussed for setting meter on “standard” time when removing DST flag.

10:00 – 10:30:	Review of survey of CCVT’s and FOCT’s field test /or change outs – 			Tony Davis

- Held discussion concerning the test results of the CCVTs. Preliminary results indicate that the CCVTs manufactured since 1999 are so far stable. The CCVT manufactured under the older technology are indicating instability.

- The preliminary Testing of OCT shows that the original equipment has shown signs of inaccuracies due to manufacturing defects and/or installation problems. Based on these findings, TDSP are using various monitoring methods for these sites and are evaluating if the 5-year testing frequency is adequate.

- Additional rows will be added to the spreadsheet to capture the subsequent tests.

10:30 – 11:30	Open discussion on 3rd party field testing CT methodology –				 Martin Lozano

11:30 – 13:00:	Lunch (1½ hour for lunch. NO Lunch will be provided)

13:00 – 14:45: Continue discussion

- The MWG support the use of this method as ratio verification pending the outcome of the following questions:

  - Can OCT support the burden introduced by this test method?

  - What is the confidence of the accuracy over a small sample range?

14:45 – 15:15: Nodal Market and EPS Metering Update – ERCOT

ERCOT discusses requirement for nodal market and possible need for meter points being in the network model by the electrical bus.

15:15 – 15:30:	Meeting Wrap-up.

Once Austin Energy gets the answers for the open items on OCT testing, ERCOT will schedule a conference call for MWG approval.