## Updated Event Code Matrix
Meter vs. MV90 Event codes
*** UPDATED Listing for 05-11-06 MWG Meeting***
EVENT | ERCOT Definition | METER
|  | ION | Mark V | Q1000 | JEMSTAR
Hardware Errors | Various hardware malfunctions (i.e. Modem card/chip, measurement chip, CPU, etc..) Fatal or not. | Various | Various | Various | Various
Firmware Errors | Firmware has a checksum error, watchdog time out error, or other problem with the firmware. Fatal or not. | Various | Various | Various | Various
RAM and ROM Errors | Bad spots in memory identified via checksum or other means. | 40 | 6 | OA | NA
Pulse Overflow Errors | The maximum size value for the number of pulses per interval in Load Profile has been exceeded. Does not apply to meters that store/report data in Engineering Units. | DC | 2C | NA | NA
Low Battery Condition | Low battery has been sensed during initial power up, daily self checks, after power outages, or any other means to check for a low battery condition. | CA | 1 | NA | NA
AC Power Up | When the Meter Electronics are power up either via Aux Pwr or connected to System Power | OE | OE | NA | OE
AC Power Down | When the Meter Electronics loses power either by Aux Pwr or connected to System Power | OD | OD | OD | OD
Configuration Changed | Meter has been reprogrammed, or any meter programming where a settlement metering parameter is changed. | 12 | 12 | 12 | NA
Clock Set/Change | The Meter real time clock has been set/changed by external sources | 15, 16 | 6B | 6B or 85 | 15, 16
Test Mode Activation | Meter going into and out of Test Mode | 51,52 | 51, 52 | 51, 52 | 51, 52
Inactive Potential | System Phase Voltage has been lost on any phase. | A0, A1, A2 | A0, A1, A2 | DB | NA
|  | NA | = No Event Information Retrieved by MV90xi TIM
Note on D10: pvinton: Event added in MV90xi
Note on E8: 062404: Marks interval load profile status of "V", but not logged in event log.
Note on E9: 062404: In meter diagnostics, but not logged in event log
Note on E15: PRS 062404: "DB" code for any phase
Note on F4: pvinton: As of 10-29-04, there is one (1) JEMSTAR Meter in service.

## ION
MV-90xi | [6 empty] | MV-90 5.0 and Older
Conversion of IONTM Events to MV-90 Events - MV90xi | [6 empty] | Conversion of IONTM events to MV-90 events - MV-90 Version 5.0 and Older
Cause Value | Effect Value | Effect Handle | Effect Ion | Event Priority | MV-90 Event Code | MV-90 Event | EFFECT VALUE | EFFECT HANDLE | MV-90-EVENT | MV-90 EVENT CODE
| Power down |  |  |  | 0D | Power outage, short int | Power down |  | Power outage, short int | 0D
| Power up |  |  |  | 0E | Power outage, short int | Power up |  | Power outage, short int | 0E
| Time about to be changed |  |  |  | 15 | Time reset occurred | Time about to be changed |  | Time reset occurred | 15
| Time changed |  |  |  | 16 | Time reset occurred | Time changed |  | Time reset occurred | 16
Internal Error | 9011 |  |  |  | 0C | Watchdog timeout | 9011 |  | Watchdog timeout | 0C
| Battery low |  |  |  | CA | Battery fail | Battery low |  | Battery fail | CA
| Master reset complete |  |  |  | D4 | Reset occurred | Master reset complete |  | Reset occurred | D4
Internal Error | 54608 |  |  |  | 40 | Load Profile Corrupt | 54608 |  | Program malfunction detected | 3
Internal Error | 64608 |  |  |  | 40 | Load Profile Corrupt | 700 |  | Modem failure | 98
Internal Error | 600 |  |  |  | D4 | Metering Equipment Reset | Meter password change |  | Password changed | 13
Internal Error | 700 |  |  |  | 98 | Modem failure | Pulsed |  | Billing reset | 45
| Meter password change |  |  |  | 13 | Password changed | On | 61DDh | Meter over Kw demand | 2C
Wrote control | Pulsed |  |  |  | 45 | Billing reset | On | 61E1h | Meter over voltage unbalance | D5
| On | 61DDh |  | 128 | 2C | Meter over Kw demand | On | 61DEh | Meter over threshold phase a | DC
Wrote control | 'ON' / 'ENABLE' | 609Bh |  |  |  |  | On | 61DFh | Meter over threshold phase b | DC
(not checked) | TEST MODE ENBLE |  |  | 51 | Start of test mode |  | On | 61E0h | Meter over threshold phase c | DC
Wrote control | 'OFF' / | [5 empty] | On | 6063 | Potential voltage loss on (phase not listed) | EB
'DISABLE' | 609Bh (not checked) | TEST MODE ENBLE |  | 52 | End Of Test Mode |  | On | 6064 | Potential voltage loss on (phase not listed) | A0
| On | 61E1h |  | 128 | D5 | Meter over voltage unbalance | On | 6065 | Potential voltage loss on (phase not listed) | A1
| On | 61E2h |  | 128 | 5M | Meter over current unbalance | On | 6066 | Potential voltage loss on (phase not listed) | A2
| On | 61DEh |  | 128 | DC | Meter over threshold phase a | On | 6063 | Voltage sag | E6
| On | 61DFh |  | 128 | DC | Meter over threshold phase b | On |  | Voltage imbalance | D5
| On | 61E0h |  | 128 | DC | Meter over threshold phase c | Disturbance |  | Power quality event start | E2
| On | 6063 |  | 128 | EB | Potential voltage loss on (phase not listed) | Normal |  | Power quality event end | E3
| On | 6064 |  | 128 | A0 | Potential voltage loss on (phase not listed) | Partial factory init |  | Configuration changed | 12
| On | 6065 |  | 128 | A1 | Potential voltage loss on (phase not listed) | Hardware security |  | Password changed | 13
| On | 6066 |  | 128 | A2 | Potential voltage loss on (phase not listed) | Hardware security enabled |  | Password changed | 13
| On | 6063 |  | 128 | E6 | Voltage sag | Changed setup |  | Configuration changed | 12
| On |  |  | 128 | D5 | Voltage imbalance | DST started |  | Fall daylight savings time change | 18
Sag/swell 1 | Disturbance |  |  |  | E2 | Power quality event start | DST on |  | Fall daylight savings time change | 18
Sag/swell 1 | Normal |  |  |  | E3 | Power quality event end | Time sync |  | Recorder clock set new time | 16
| Partial factory init |  |  |  | 12 | Configuration changed | Time change |  | Recorder clock set new time | 16
| Hardware security |  |  |  | 13 | Password changed |  |  | Output control relay toggle | 44
| Hardware security enabled |  |  |  | 13 | Password changed | Password security en |  | Changed password
| Changed setup |  |  |  | 12 | Configuration changed | Telnet locked out |  | Attempted access with invalid password
| DST started |  |  |  | 18 | Fall daylight savings time change | Value changed |  | Operating parameter changed
| DST on |  |  |  | 18 | Fall daylight savings time change |  |  | Unknown - text event
| Time sync |  |  |  | 16 | Recorder clock set new time | Test Mode Activated |  | Test Mode Activated | Added to TIM by ITRON/Power Measurement
Time change | Time change |  |  |  | 16 | Recorder clock set new time
|  |  |  | 20 | 44 | Output control relay toggle
Changed setup | Telnet locked out |  |  | 1E |  | Attempted access with invalid password
Changed setup | Value changed |  |  | 11 |  | Operating parameter changed
|  |  |  | FF |  | Unknown - text event

## Mark V
MV-90xi |  |  |  | MV-90 5.0 and Older
MARK V EVENT CODE MAP - MV90xi |  |  |  | MARK V EVENT CODE MAP
Transdata EMS 50/ MARK V Firmware Version MV90xi 1.0 |  |  |  | Transdata EMS 50/ MARK V Firmware Version 4.0 or later only
TRANSDATA MARK V EVENT |  | MV90 EVENT | MV90 Event Code | TRANSDATA MARK V EVENT | MV90 EVENT | MV90 Event Code
MV90 Event Message | Code | Qualifier | Note/Manufacturer’s description of event | Voltage Sag- Phase A | Voltage Sag | E6
Voltage Sag | E6 | A,B,C | Voltage Sag Phase A,B,C | Voltage Sag- Phase B | Voltage Sag | E6
Voltage Swell | E7 | A,B,C | Voltage Swell Phase A,B,C | Voltage Sag- Phase C | Voltage Sag | E6
Potential A Inactive | A0 |  | Voltage Outage Phase A | Voltage Swell - Phase A | Voltage Swell | E7
Potential B Inactive | A1 |  | Voltage Outage Phase B | Voltage Swell - Phase B | Voltage Swell | E7
Potential C Inactive | A2 |  | Voltage Outage Phase C | Voltage Swell - phase C | Voltage Swell | E7
Breaker Operation | E8 | A,B,C | Breaker Operation Phase A, B, C | Voltage Outage - Phase A | Potential A Inactive | A0
Low Voltage Limit | E9 | A,B,C | Volt. Under Limit Phase A, B, C | Voltage Outage - Phase B | Potential C Inactive | A2
Phase Angle Limit | EA | A,B,C | Angle Outside Limit Ph A, B, C | Voltage Outage - Phase C | Potential B Inactive | A1
Low Current Limit | EB | A,B,C | Cur. Below Limit Phase A, B, C | Breaker Operation - Phase A | Breaker Operation | E8
Power Factor Limit | EC | A,B,C | PF Outside Limit Phase A, B, C | Breaker Operation - Phase B | Breaker Operation | E8
Status Input Opening | 32 |  | Ext. Input 1,2 Open (High) | Breaker Operation - Phase C | Breaker Operation | E8
Status Input Closure | 31 |  | Ext. Input 1,2 Closed (Low) | Volt. Under Limit - Phase A | Low Voltage Limit | E9
Relay Opened Relay # | 36 |  | Control Output 1,2,3,4,5 Open | Volt. Under Limit - Phase B | Low Voltage Limit | E9
Relay Closed Relay # | 84 |  | Control Output 1,2,3,4,5 Closed | Volt. Under Limit - Phase C | Low Voltage Limit | E9
Battery Failure | 1 |  | Battery Time Over Limit | Angle Outside Limit - Ph A | Phase Angle Limit | EA
EEPROM Failure | 9D |  | EPROM Diagnostics Error | Angle Outside Limit - Ph B | Phase Angle Limit | EA
RAM Error Detected | 6 |  | RAM Diagnostics Error | Angle Outside Limit - Ph C | Phase Angle Limit | EA
Watchdog Timer Error | 0C |  | Register Watchdog Tripped, A/D Watchdog Activated | Cur Below Limit - Phase A | Low Current Limit | EB
Communication Session Interrupted | 43 |  | Communications Error | Cur Below Limit - Phase B | Low Current Limit | EB
Call-in Failure | 20 |  | Dial Out Unsuccessful | Cur Below Limit - Phase C | Low Current Limit | EB
AC Power Down | 0D |  | Meter Power Turned Off | PF Outside Limit - Phase A | Power Factor Limit | EC
Billing Reset | 45 |  | Maximum Demand Reset | PF Outside Limit - Phase B | Power Factor Limit | EC
Data Log Uploaded | 8C |  | Recorder Data Retrieved | PF Outside Limit - Phase C | Power Factor Limit | EC
Configuration Changed | 12 |  | Register Programmed | Ex input 1 Open (hi) | Status Input Opening - # | 32
Time or Date Changed | 6B |  | Time Changed | Ex Input 1 Closed (lo) | Status Input Closure - # | 31
Fall DST Time Change | 18 |  | Time Changed (if sent on DST time instead of) Day Light Savings Time | EX input 2 Open(hi) | Status Input Opening - # | 32
Spring DST Time Change | 19 |  | Time Changed (if sent on DST time instead of) Day Light Savings Time | Ex input 2 Closed (lo) | Status Input Closure - # | 31
Pre-Set Register Values | 5C |  | Register Reading Changed | Control Output 1 Open | Relay Opened - Relay # | 36
Calibration Change | ED |  | A/D Programmed or Re-Cal | Control Output 1 Closed | Relay Closed - Relay # | 84
Start of Test Mode | 51 |  | Test Mode Initiated | Control Output 2 Open | Relay Opened - Relay # | 36
End of Test Mode | 52 |  | Test Mode Exited | Control Output 2 Closed | Relay Closed - Relay # | 84
Recorder Time Sync | EE |  | Recorder Time Sync | Control Output 3 Open | Relay Opened - Relay # | 36
Season Change | EF |  | Time of Use Season Change | Control Output 3 Closed | Relay Closed - Relay # | 84
RAM Buffer Overflow/Initialization | 0A |  | Register Rollover, Demand Register Overflow, Recorder Overflow | Control Output 4 Open | Relay Opened - Relay # | 36
Meter Over Threshold Channel # | 2C |  | Demand Over Limit – Start | Control Output 4 Closed | Relay Closed - Relay # | 84
Meter Return Within Limits Ch. # | B9 |  | Demand Over Limit – End | Control Output 5 Open | Relay Opened - Relay # | 36
Customer 1 Alarm | 75 |  | Harmonic Alarm – Start, Harmonic Alarm – End | Control Output 5 Closed | Relay Closed - Relay # | 84
Event Log Uploaded | 8D |  | Event Log Data Retrieved | Battery Time Over Limit | Battery Failure | 1
Metering Equipment Reset | D4 |  | All Meter Data Reset | EPROM Diagnostic Error | EPROM Failure | 9D
Phase Restoration | DF | A, B, C | Phase Restoration | RAM Diagnostic Error | RAM Error Detected | 6
AC Power Up | 0E |  | AC Power Up | Register Watchdog Tripped | Watchdog Timer Error | 0C
Unrecognized Recorder Event Code | 74 |  | (If the TIM gets a Day Light Savings Time event code whose time is not equal to the TIM’s DST time change, or any code not listed above) | A/D Watchdog Activated | Watchdog Timer Error | 0C
|  |  |  | Communications Error | Communications Session Interrupted | 43
|  |  |  | Dial Out Unsuccessful | Call-in Failure | 20
|  |  |  | Meter Power Turned off | AC Power Down | 0D
|  |  |  | Maximum Demand Reset | Billing Reset | 45
|  |  |  | Recorder Data Retrieved | Data Log Uploaded | 8C
|  |  |  | Register programmed | Configuration Changed | 12
|  |  |  | Time Changed | Time or Date Changed | 6B
|  |  |  | Register reading changed | Pre-Set Register Values | 5C
|  |  |  | A/D Programmed /recalibrated | Calibration Change | ED
|  |  |  | Test Mode Initiated | Start of Test Mode | 51
|  |  |  | Test Mode Exited | End of Test Mode | 52
|  |  |  | Daylight Savings Time | Unrecognized recorder Event Code/ Spring Daylight Savings Time changed/ Fall daylight Savings Time Changed | 74/19/18
|  |  |  | Recorder Time Sync | Recorder time Sync. | EE
|  |  |  | TOU Season Change | Season Change | EF
|  |  |  | Register Rollover | RAM Buffer Overflow/Initialization | 0A
|  |  |  | Demand register overflow | RAM Buffer Overflow/Initialization | 0A
|  |  |  | Recorder Overflow | RAM Buffer Overflow/Initialization | 0A
|  |  |  | Demand over limit - start | Meter Over Threshold – Channel # | 2C
|  |  |  | Demand Over Limit End | Meter Return Within Limits – Channel # | B9
|  |  |  | Harmonic Alarm - start | Customer Alarm 1 | 75
|  |  |  | Harmonic Alarm - END | Customer Alarm 1 | 75
|  |  |  | Event Log Data Retrieved | Event Log Uploaded | 8D
|  |  |  | All Meter Data Reset | Metering Equipment Reset | D4
|  |  |  | Any Other Event | Unrecognized Recorder Event Code | 74

## Q1000
MV-90xi |  |  |  | MV-90 5.0 and Older
Q1000 Event Code Map - MV90xi |  |  |  | Q1000 Event Code Map
Manufacturers Description | MV90 Event Code | MFG Event Code | MV90 Message | Manufacturers Description | MV90 Message | MV90 Event Code
DEMAND_RESET | ‘11’ | ‘004’ | Operating Parameter changed | MASS_MEM1_EOI | RAM Buffer Overflow/Initialization | ‘0A’
LOSS_OF_PHASE | ‘D6’ | ‘005’ | Phase Failure | MASS_MEM2_EOI | RAM Buffer Overflow/Initialization | ‘0A’
LOSS_OF_PHASEA | ‘DB’ | ‘006’ | Phase Drop-out(Phase, short/Long) | DEMAND_RESET | Operating Parameter changed | ‘11’
LOSS_OF_PHASEB | ‘DB’ | ‘007’ | Phase Drop-out(Phase, short/Long) | LOSS_OF_PHASE | Phase Failure | ‘D6’
LOSS_OF_PHASEC | ‘DB’ | ‘008’ | Phase Drop-out(Phase, short/Long) | LOSS_OF_PHASEA | Phase Drop-out(Phase, short/Long) | ‘DB’
REGISTER_FREEZE | ‘47’ | ‘009’ | Freeze Meter Readings | LOSS_OF_PHASEB | Phase Drop-out(Phase, short/Long) | ‘DB’
CLOCK_ERROR | ‘17’ | ‘010’ | Recorder Clock Malfunction Detected | LOSS_OF_PHASEC | Phase Drop-out(Phase, short/Long) | ‘DB’
ENTER_TEST_MODE | ‘51’ | ‘011’ | Start of Test Mode | REGISTER_FREEZE | Freeze Meter Readings | ‘47’
LEAVE_TEST_MODE | ‘52’ | ‘012’ | End of Test Mode | CLCOK_ERROR | Recorder Clock Malfunction Detected | ‘17’
POWER_OUTAGE | ‘0D’ | ‘013’ | AC Power Down | ENTER_TEST_MODE | Start of Test Mode | ‘51’
CALL_ON_SCHEDULE | ‘95’ | ‘014’ | Scheduled Call-in | LEAVE_TEST_MODE | End of Test Mode | ‘52’
METER_REPROGRAM | ‘12’ | ‘015’ | Configuration Changed | POWER_OUTAGE | AC Power Down | ‘0D’
INTERROGATION | ‘1A’ | ‘016’ | Unit Accessed | CALL_ON_SCHEDULE | Scheduled Call-in | ‘95’
CLOCK_ADJUSTMENT | ‘6B’ | ‘017’ | Time or Date Changed | METER_REPROGRAM | Configuration Changed | ‘12’
OPTICAL_ACTIVE | ‘1C’ | ‘018’ | Unit Accessed by Reader | CLOCK_ADJUSTMENT | Time or Date Changed | ‘6B’
COMM1_ACTIVE | ‘1B’ | ‘019’ | Unit Accessed Remotely | ALARM1_ON | Customer 1 Alarm | ‘75’
COMM2_ACTIVE | ‘1B’ | ‘020’ | Unit Accessed Remotely | ALARM2_ON | Customer 2 Alarm | ‘76’
ALARM1_ON | ‘75’ | ‘021’ | Customer 1 Alarm | ALARM3_ON | Alarm Activated | ‘89’
ALARM2_ON | ‘76’ | ‘022’ | Customer 2 Alarm | ALARM4_ON | Alarm Activated | ‘89’
ALARM3_ON – ALARM24_ON | ‘89’ | ‘023’ – ‘44’ | Alarm Activated | ALARM5_ON | Alarm Activated | ‘89’
ALARM1_OFF – ALARM24_OFF | ‘C8’ | ’45’- ‘68’ | Customer 1 Alarm Off | ALARM6_ON | Alarm Activated | ‘89’
EXTERNAL_INP0_ON | ‘6E’ | ‘069’ | Status Input Opening | ALARM7_ON | Alarm Activated | ‘89’
EXTERNAL_INP1_ON | ‘6E’ | ‘070’ | Status Input Opening | ALARM8_ON | Alarm Activated | ‘89’
EXTERNAL_INP2_ON | ‘6E’ | ‘071’ | Status Input Opening | ALARM9_ON | Alarm Activated | ‘89’
EXTERNAL_INP3_ON | ‘6E’ | ‘072’ | Status Input Opening | ALARM10_ON | Alarm Activated | ‘89’
EXTERNAL_INP4_ON – EXTERNAL_INP7_ON | ‘6E’ | ‘073’ – ‘076’ | Status Input Opening | ALARM11_ON | Alarm Activated | ‘89’
EXTERNAL_INP0_OFF – EXTERNAL_INP7_OFF | ‘6D’ | ‘077’ – ‘84’ | Status Input Closing | ALARM12_ON | Alarm Activated | ‘89’
EXTERNAL_EOI | ‘6E’ | ‘085’ | Status Input Opening | ALARM13_ON | Alarm Activated | ‘89’
BEFORE_DST_ENTRY | ‘19’ | ‘086’ | Spring DST Change | ALARM14_ON | Alarm Activated | ‘89’
AFTER_DST_ENTRY | ‘19’ | ‘087’ | Spring DST Change | ALARM15_ON | Alarm Activated | ‘89’
BEFORE_DST_EXIT | ‘18’ | ‘088’ | Fall DST Change | ALARM16_ON | Alarm Activated | ‘89’
AFTER_DST_EXIT | ‘18’ | ‘089’ | Fall DST Change | ALARM17_ON | Alarm Activated | ‘89’
INVALID_PASSWORD | ‘1E’ | ‘090’ | Attempted Access With Invalid Password | ALARM18_ON | Alarm Activated | ‘89’
AUTO_TIME_ADJUST | ‘85’ | ‘103’ | Auto Timeset Performed | ALARM19_ON | Alarm Activated | ‘89’
EXTERNAL_INP9_ON – EXTERNAL_INP16_ON | ‘6E’ | ‘164’- ‘171’ | Status Input Opening | ALARM20_ON | Alarm Activated | ‘89’
EXTERNAL_INP9_OFF – EXTERNAL_INP16_OFF | ‘6D’ | ‘172’ – ‘179’ | Status Input Closing | ALARM21_ON | Alarm Activated | ‘89’
RATE_A_ON – RATE_Z_OFF | ‘6V’ | ‘209’ – ‘592’ | Rate Change | ALARM22_ON | Alarm Activated | ‘89’
SEASON_CHANGE | ‘EF’ | ‘680’ | Season Change | ALARM23_ON | Alarm Activated | ‘89’
| ‘74’ | EvtID | Unrecognized Recorder Event Code | ALARM24_ON | Alarm Activated | ‘89’
|  |  |  | EXTERNAL_INP0_ON | Status Input Opening | ‘6E’
|  |  |  | EXTERNAL_INP1_ON | Status Input Opening | ‘6E’
|  |  |  | EXTERNAL_INP2_ON | Status Input Opening | ‘6E’
|  |  |  | EXTERNAL_INP3_ON | Status Input Opening | ‘6E’
|  |  |  | EXTERNAL_EOI | Status Input Opening | ‘6E’
|  |  |  | BEFORE_DST_ENTRY | Spring DST Change | ‘19’
|  |  |  | AFTER_DST_ENTRY | Spring DST Change | ‘19’
|  |  |  | BEFORE_DST_EXIT | Fall DST Change | ‘18’
|  |  |  | AFTER_DST_EXIT | Fall DST Change | ‘18’
|  |  |  | INVALID_PASSWORD | Attempted Access With Invalid Password | ‘1E’
|  |  |  | AUTO_TIME_ADJUST | Auto Timeset Performed | ‘85’
[5 empty] | Unrecognized Recorder Event Code | ‘74’

## JEMSTAR
MV-90xi |  |  | MV-90 5.0 and Older
JEMSTAR Event Code Map - MV90xi |  |  | JEMSTAR Event Code Map
Note/Manufacturer’s Description | MV90 EventCode |  | Note/Manufacturer’s Description | MV90 Event Message | MV90 EventCode
AC Power Down | 0D | Power outage | Power outage | AC Power Down | 0D
AC Power Up | 0E | Power outage | Power outage | AC Power Up | 0E
Recorder Clock Set – previous time | 15 | Time set | Time set | Recorder Clock Set – previous time | 15
Recorder Clock Set – new time | 16 | Time set | Time set | Recorder Clock Set – new time | 16
Start of Test Mode | 51 | Test mode | Test mode | Start of Test Mode | 51
End of Test Mode | 52 | Test mode | Test mode | End of Test Mode | 52
DST Change – Previous time | 4A | Daylight Saving time Change | Daylight Saving Time Change | DST Change – Previous Time | 4A
DST Change – New time | 4B | Daylight Saving time Change | Daylight Saving Time Change | DST Change – New Time | 4B
Billing Reset | 45 | Billing Period Reset | Billing Period Reset | Billing Reset | 45
Freeze Meter Readings | 47 | Register Freeze | Register Freeze | Freeze Meter Readings | 47
Pre-Set Register Values | 5C | Register Preset | Register Preset | Pre-Set Register Values | 5C