## Slide 1: Frequency Control Task Force
Presentation to the
ERCOT Technical Advisory Committee
June 1, 2006

## Slide 2: Presentation Overview
Frequency Control Issue Background
Schedule Control Error (SCE) as a component of the frequency issue
Work of the Frequency Control Task Force
  PRRs 661 and 662

## Slide 3: Frequency Issue Background
The ERCOT system has experienced primary frequency control problems since the beginning of Single Control Area operations in 2001
ERCOT’s frequency performance is monitored by NERC Control Performance Standard 1 (CPS1)

## Slide 4: ERCOT CPS1 Average

## Slide 5: Frequency Issue Background
Main tools for maintaining primary frequency control are governor response and Regulation Service (RGS)
  PDCWG has observed poor governor response
  Online units with governors are required to place governors in service at specified droop
  ERCOT does not procure governor response, generators are not paid to provide it, and there is no govenor response performance measure

## Slide 6: Frequency Issue Background
  FCTF continues to work on creation of a Governor Response Service and corresponding performance measure
  Patton and others have postulated ERCOT procures excessive amounts of RGS
  Generator Schedule Control Error (SCE) assumed to impact overall primary system frequency control and the quantity of RGS procured and deployed

## Slide 7: Schedule Control Error
SCE-based solutions to frequency control and RGS procurement and deployment
  PRRs 356 and 358
  PRR 525
PRR 525 responses
  PRR 586
  PRRs 605, 607, and 608
  PRRs 649, 656, 661, and 662

## Slide 8: Schedule Control Error
Key Features of PRR 525
  Created new methodology for calculating QSE SCE
  Applied new SCE performance measure to all resource QSEs (not just RGS providers) in all intervals (not just when RGS provided)
  Did not address penalties for non-compliance, leaving Protocols 6.10.12 as sole enforcement language (the “death penalty”)

## Slide 9: Schedule Control Error
Protocols Sec. 6.10.12
  6.10.12 Non-Compliance Actions of ERCOT
  ERCOT may revoke any or all Ancillary Service qualification of any QSE providing an Ancillary Service(s) for continued under-performance.
  Failure to deliver energy resulting from a valid Dispatch Instruction is cause for ERCOT, at ERCOT’s option, to withhold payment for any Ancillary Services purchased and not delivered.
  ERCOT will make information relative to each QSE’s performance as well as ERCOT’s performance, available to the marketplace on a monthly basis, subject to the provisions of Section 1.3.1, Restrictions on Protected Information.

## Slide 10: Schedule Control Error
PRR 525 implementation
  Adopted by ERCOT Board in April 2005
  System changes required to “unbox” PRR 525 complete in October 2005
  Board resolution in December 2005 to implement PRR 525 on January 1, 2006 with 6-month death penalty moratorium
  Absent Board action, stakeholders assume death penalty is reinstated July 1, 2006

## Slide 11: QSE SCE performance (CPS2 scores using PRR 525 methodology)

## Slide 12: Frequency Control Task Force
Formed by WMS in July 2005
  Met 18 times to date with participation from all market segments, incl. ERCOT and PUCT
  Reports to WMS, ROS, and PRS
  Focus on proper alignment of commercial incentives with market goals, performance measures, and compliance penalties
Produced PRRs 661 and 662 as a “package solution” to SCE performance measures, commercial incentives, and compliance penalties

## Slide 13: Frequency Control Task Force
Issues examined by FCTF
  Contribution of SCE to poor frequency control
  Contribution of SCE to regulation procurement and deployment
  Contribution of load swings and load forecast error to regulation deployment
  Market obligations / incentives to provide primary frequency response

## Slide 14: Frequency Control Task Force
Issues examined by FCTF (cont.)
  Market incentives / penalties for SCE performance
  Uncontrollable Renewable Resource forecast error
  Accuracy of ERCOT regulation signals and their impact on the QSE SCE calculation
  Evaluation of PRR 525 implementation

## Slide 15: Frequency Control Task Force
Set of options presented to ROS and WMS in April 2006
  ROS recommended retaining the existing performance measure (PRR 525)
  WMS agreed with ROS recommendation and narowed FCTF options to incentive/penalty structures built upon existing CPS2 metric

## Slide 16: Frequency Control Task Force
Key Features of PRR 661
  Maintains existing SCE Performance Measure
    10-minute measure applied to all resource QSEs in all intervals
    Requirement to pass 90% of all intervals in each month maintained
  Applies financial penalties to non-performers
  Creates financial incentives for compliance
  Provides physical penalties for very poor performance, without death penalty shock
  Provides adjustment mechanism to scale financial penalty factor based on experience

## Slide 17: PRR 661 Backcast Analysis
ID | AINT | Cost to get to 90% | MINT | PINT | Failing Interval Count | Comment
AO | 32.5 | $12,463.46 | 4375 | 3905 | 470 | Round up to 33
AQ | 313.9 | $12,868.75 | 1141 | 713 | 428 | Round up to 314
B | 239.2 | $29,403.65 | 4028 | 3386 | 642 | Round up to 240
H | 219.2 | $29,440.61 | 3578 | 3001 | 577 | Round up to 220
L | 791.3 | $81,454.30 | 4387 | 3157 | 1230 | Round up to 792
R | 79.1 | $23,422.18 | 4439 | 3916 | 523 | Round up to 80
AL | 2971.9 |  | 4311 | 908 | 3403 | Wind-Only QSE
AG | 2743 |  | 4240 | 1073 | 3167 | Wind-Only QSE
AN | 2532.2 |  | 4138 | 1192 | 2946 | Wind-Only QSE
AM | 2391.2 |  | 4008 | 1216 | 2792 | Wind-Only QSE
 |  | $189,052.95 |  |  |  | 
Notes: Produced by ERCOT Compliance based on final March 2006 CPS2 scores.

## Slide 18: Frequency Control Task Force
Key Features of PRR 662
  Clarifies/tightens unit trip exemption
  Addresses unit testing
  Addresses Uncontrollable Renewables
  Clarifies unit and portfolio capability violations
  Deletes RRS deployment exemption

## Slide 19
Questions?