## Slide 1: 2006 Report on the Capacity, Demand, & Resources for the ERCOT Region
Technical Advisory Committee
June 1, 2006
Kenneth A. Donohoo. P.E.
Manager, Transmission Services
System Planning
Operations

## Slide 2: Elements of the CDR Report
Load Forecasts
LAARs
Existing Resources
Wind Generation
Mothballed Units
RMR Units
Private Networks
New Resource
GATF Review Assumptions
In order to adequately prepare the CDR, ERCOT planners have compiled the best information available with regards to forecasted load demands and available resources.
Load Forecasts
Peak Demand
-LARRs
Resource Forecast
Existing
-Retired/Mothballed
+Private
+New
Available Resources
-Firm Load
Reserves
CDR
Firm Load
Available Resources
The CDR is based on a single “snapshot” in time. Changes will, and do, occur on a continuous basis and may not be reflected in the current CDR.

## Slide 3: GENERATION INTERCONNECTION ACTIVITY
Currently tracking 99 active generation interconnection or change requests
North South West Total
Capacity for Grid, MW 14,550 9,730 10,779 35,059
Includes Wind, MW 480 2,930 9,237 12,647
Fuel Type Not Public Public Total
Coal 3,992 11,245 15,237
Gas 3,900 2,300 6,200
Other 975 0 975
Wind 10,002 2,645 12,647
Grand Total 18,869 16,590 35,059
THESE NUMBERS CHANGE
EVERYDAY AS NEW REQUESTS ARE
RECEIVED, PROJECTS GO IN-SERVICE
OR ARE NO LONGER ACTIVE
ERCOT ONLY
DOES NOT INCLUDE ALL OF TEXAS

## Slide 6: Capacity, Demand, & Reserves in the ERCOT Region for 2006-2011 (Summer Summary)
 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Load Forecast (MW): |  |  |  |  |  | 
Total Summer Peak Demand | 61,656 | 63,222 | 64,318 | 65,950 | 67,548 | 69,034
Less LAARs Serving as Responsive | (1,112) | (1,112) | (1,112) | (1,112) | (1,112) | (1,112)
Firm Load Forecast (MW): | 60,544 | 62,110 | 63,206 | 64,838 | 66,436 | 67,922
Resources (MW): |  |  |  |  |  | 
Installed Capacity | 58,831 | 58,831 | 58,831 | 58,831 | 58,831 | 58,831
Less Retiring Units | 0 | 0 | (393) | (451) | (451) | (451)
Capacity from Private Networks | 6,419 | 6,575 | 6,279 | 6,279 | 6,279 | 6,279
2.6% of Wind Generation | 62 | 62 | 62 | 62 | 62 | 62
RMR Under Contract | 267 | 170 | 170 | 170 | 0 | 0
50% of Asynchronous Ties | 428 | 553 | 553 | 553 | 553 | 553
Switchable Units | 2,645 | 2,810 | 2,810 | 2,810 | 2,810 | 2,810
Mothballed Units Available | 2,104 | 1,997 | 1,790 | 1,787 | 1,783 | 1,820
Planned Units (Wind w/ IA -- 2.6%) | 0 | 25 | 38 | 38 | 38 | 38
Planned Units (Fossil w/ IA) | 0 | 550 | 550 | 550 | 1,300 | 1,300
Total Resources (MW): | 70,756 | 71,573 | 70,690 | 70,628 | 71,205 | 71,242
OFFICIAL RESERVE MARGIN: | 16.9% | 15.2% | 11.8% | 8.9% | 7.2% | 4.9%

## Slide 7: Alternate Scenarios for 2006 CDR (Summer)
 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Firm Load Forecast (MW): | 60,544 | 62,110 | 63,206 | 64,838 | 66,436 | 67,922
Total Resources (MW): | 70,756 | 71,573 | 70,690 | 70,628 | 71,205 | 71,242
RESERVE MARGIN: | 16.9% | 15.2% | 11.8% | 8.9% | 7.2% | 4.9%
“High” Reserve Margin (all Mothballed Units Return) | 16.9% | 26.4% | 23.1% | 19.9% | 18.2% | 15.6%
“Low” Reserve Margin (no Mothballed Units Return) | 16.9% | 12.0% | 9.0% | 6.2% | 4.5% | 2.2%
Reserve Margin w/ Publicly Announced Thermal Units | 16.9% | 15.4% | 12.0% | 20.0% | 24.0% | 23.0%
Reserve Margin (%)

## Slide 8: Key Issues for 2006
In examining the 2006 CDR, ERCOT staff has identified several key issues for to aid in understanding this report.
Projected annual demand growth has been increased from 1.8% to 2.3% based on updated social-economic data for Texas.
ERCOT staff was unable to reconcile load demands which may be demand or price responsive, other than LAARs.
Private Use Networks data was implemented for the first time.
The GATF recommended no change in the methodology for dealing with Planned New Generation at this time.

## Slide 9: Next Steps
ERCOT staff will present the CDR Summary on June 1, 2006 and will have the final report available within a week.
ERCOT staff will continue to work with the GATF to review and refine the methodologies. (Next meeting of the GAFT is scheduled for July 14th).
ERCOT staff will continue to work with Market Participants to improve Private-Use Network reporting and to identify and assess the impact to the load forecast.
ERCOT will publish the next CDR by June 1, 2007.

## Slide 10
Questions?

## Slide 11
Background

## Slide 12: Current Publicly Announced Projects (As of May 25, 2006)
Site Name | Status | Air Permit | Fuel | In Service Date | MW into Grid
Colorado Bend | IA Signed | Issued | Gas | 2007 | 275
Quail Run | IA Signed | Issued | Gas | 2007 | 275
Sandow 5 | FIS Requested | Issued | Coal | 2009 | 585
Big Brown 3 | FIS Requested | Pending | Coal | 2009 | 800
Martin Lake 4 | FIS Requested | Pending | Coal | 2009 | 800
Monticello 4 | FIS Requested | Pending | Coal | 2009 | 800
Valley 4 | FIS Requested | Pending | Coal | 2009 | 800
Cobisa-Greenville | FIS Requested | Issued | Gas | 2009 | 1,750
Sandy Creek | FIS Requested | Issued | Coal | 2009 | 800
Tradinghouse 3 Tradinghouse 4 | FIS Requested | Pending | Coal | 2009 2010 | 800 800
Oak Grove SES | FIS Requested | Pending | Coal | 2009 2010 | 790 790
Lake Creek 4 | FIS Requested | Pending | Coal | 2010 | 800
Morgan Creek 7 | FIS Requested | Pending | Coal | 2010 | 800
JK Spruce 2 | Muni IA | Issued | Coal | 2010 | 750
Twin Oaks 3 | FIS Requested | Pending | Coal | 2011 | 630
Hugo Plant | FIS Requested | Pending | Coal | 2011 | 500
 |  |  |  | Totals: | 13,545
Notes: A Public Commitment Letter is needed from the owners of J.K. Spruce and Hugo. Part of the Interconnection Procedures – an official letter from the municipal utility or CoOp will serve as the public commitment.