## Verifiable Cost above LSL
General Input/Output Equation:
Heat Input (MMBtu/h) = a + bx + cx^2 + dx^3
x - Output MW, it is between Pmin and Pmax
a | -8.5
b | 17
c | -0.14
d | 0.0007
Pmin- Minimum output limit: |  |  | 150 | MW
Pmax- Maximum output limit: |  |  | 15 | MW
Generator Category: |  |  | GSNONR
Marginal Heat Rate = b + 2cx + 3dx^2
x - Output MW, it is between Pmin and Pmax
Output | Output | Input Heat | Heat Rate | Mariginal Heat Rate
(%) | (MW) | (MMBtu/h) | (MMBtu/MWh) | (MMBtu/MWh)
10 | 15 | 217.3625 | 14.4908 | 13.2725
15 | 22.5 | 311.0984 | 13.8266 | 11.7631
20 | 30 | 394.4 | 13.1467 | 10.49
22.2 | 33.3 | 428.2036 | 12.859 | 10.0047
25 | 37.5 | 469.0391 | 12.5077 | 9.4531
30 | 45 | 536.7875 | 11.9286 | 8.6525
35 | 52.5 | 599.4172 | 11.4175 | 8.0881
40 | 60 | 658.7 | 10.9783 | 7.76
45 | 67.5 | 716.4078 | 10.6134 | 7.6681
50 | 75 | 774.3125 | 10.3242 | 7.8125
55 | 82.5 | 834.1859 | 10.1113 | 8.1931
60 | 90 | 897.8 | 9.9756 | 8.81
65 | 97.5 | 966.9266 | 9.9172 | 9.6631
66.65 | 99.975 | 991.25 | 9.915 | 9.9965
70 | 105 | 1043.3375 | 9.9365 | 10.7525
75 | 112.5 | 1128.8047 | 10.0338 | 12.0781
78.87 | 118.305 | 1202.2986 | 10.1627 | 13.2664
80 | 120 | 1225.1 | 10.2092 | 13.64
85 | 127.5 | 1333.9953 | 10.4627 | 15.4381
90 | 135 | 1457.2625 | 10.7945 | 17.4725
95 | 142.5 | 1596.6734 | 11.2047 | 19.7431
100 | 150 | 1754 | 11.6933 | 22.25

## Mitigated Cap By Protocol
Verifiable variable O&M (MMBtu/MWh) : |  |  |  | 0.5 | Comparison Heat Rate (MMBtu/MWh): | 10.5
(Assume verifiable variable O&M has the unit as $/MWh. For simplicity, it is coverted to MMBtu/MWh here )
Output | Mariginal Heat Rate | MHR+VVOM | Mitigated Cap
(MW) | (MMBtu/MWh) | (MMBtu/MWh) | (MMBtu/MWh)
15 | 13.2725 | 13.7725 | 13.7725
22.5 | 11.7631 | 12.2631 | 12.2631
30 | 10.49 | 10.99 | 10.99
33.3 | 10.0047 | 10.5047 | 10.5047
37.5 | 9.4531 | 9.9531 | 10.5
45 | 8.6525 | 9.1525 | 10.5
52.5 | 8.0881 | 8.5881 | 10.5
60 | 7.76 | 8.26 | 10.5
67.5 | 7.6681 | 8.1681 | 10.5
75 | 7.8125 | 8.3125 | 10.5
82.5 | 8.1931 | 8.6931 | 10.5
90 | 8.81 | 9.31 | 10.5
97.5 | 9.6631 | 10.1631 | 10.5
99.975 | 9.9965 | 10.4965 | 10.5
105 | 10.7525 | 11.2525 | 11.2525
112.5 | 12.0781 | 12.5781 | 12.5781
118.305 | 13.2664 | 13.7664 | 13.7664
120 | 13.64 | 14.14 | 14.14
127.5 | 15.4381 | 15.9381 | 15.9381
135 | 17.4725 | 17.9725 | 17.9725
142.5 | 19.7431 | 20.2431 | 20.2431
150 | 22.25 | 22.75 | 22.75

## Issues for Mitigated Cap
| Question | Description | Solution
1 | How if the Marginal verifiable heatrate is not monotonically increasing? | Depend on how QSE model the cost for verification. In some cases, the mariginal verifiable heatRate is not monotonically increasing.
2 | How to get/calculate verifiable variable of OM? | Verifiable variable of OM ($/MWh) is assumed to be a constant. No clear definition in the protocol. | Need TPTF clarification.

## Rectifications
|  |  |  | Comparison Heat Rate (MMBtu/MWh): | 10.5
Rectification Method 1: |  | Max[Max(MarginalheatRate(x)), Comparison Heat Rate] |  | MariginalHeatRate(x) = b + 2cx + 3dx^2
Rectification Method 2: |  | Max[MarginalheatRate(min), MarginalheatRate(x), Comparison Heat Rate] |  | x - Output MW, it is between Pmin and Pmax
Pmin- Minimum output limit
Pmax- Maximum output limit
Output | Mitigated Cap by Protocol | Rectification (Method 1) | Rectification (Method 2)
(MW) | (MMBtu/MWh) | (MMBtu/MWh) | (MMBtu/MWh)
15 | 13.7725 | 22.75 | 13.7725
22.5 | 12.2631 | 22.75 | 13.7725
30 | 10.99 | 22.75 | 13.7725
33.3 | 10.5047 | 22.75 | 13.7725
37.5 | 10.5 | 22.75 | 13.7725
45 | 10.5 | 22.75 | 13.7725
52.5 | 10.5 | 22.75 | 13.7725
60 | 10.5 | 22.75 | 13.7725
67.5 | 10.5 | 22.75 | 13.7725
75 | 10.5 | 22.75 | 13.7725
82.5 | 10.5 | 22.75 | 13.7725
90 | 10.5 | 22.75 | 13.7725
97.5 | 10.5 | 22.75 | 13.7725
99.975 | 10.5 | 22.75 | 13.7725
105 | 11.2525 | 22.75 | 13.7725
112.5 | 12.5781 | 22.75 | 13.7725
118.305 | 13.7664 | 22.75 | 13.7725
120 | 14.14 | 22.75 | 14.14
127.5 | 15.9381 | 22.75 | 15.9381
135 | 17.9725 | 22.75 | 17.9725
142.5 | 20.2431 | 22.75 | 20.2431
150 | 22.75 | 22.75 | 22.75