| NPRR Number | XXX | NPRR Title | Zonal PRR Synchronization and ERCOT Staff Clarifications of Draft Section 6, Adjustment Period and Real-Time Operations |
| --- | --- | --- | --- |
| Nodal Protocol Section(s) Requiring Revision (include Section No. and Title) |  | Draft Section 6, Adjustment Period and Real-Time Operations |  |
| Revision Description |  | This NPRR incorporates: (1) Relevant language from the following PRRs that were the Board between April 2004 and February 2006: - PRR468, Frequency Response Requirements and Monitoring - PRR487, Black Start Resources - PRR496, Block Bidding and Deployment of LaaRs providing Responsive Reserve Service and Non-Spinning Reserve Service - PRR499, Eliminate Fuel Shortage Notice - PRR513, Verification of Operational Model after Recurring Local Congestion Event - PRR531, Load Clarification - PRR543, Schedules and Emergency Assistance Over CFE-ERCOT DC Ties - PRR561, Remove Nuclear and Hydroelectric Generators from Automatic Deployment Software - PRR611, Reporting of Operation Reserve Capability Under Severe Gas Curtailments - PRR612, Ancillary Service Procurement During the Adjustment Period (2) TPTF determinations regarding ERCOT Staff clarification questions as discussed by TPTF on 1/23/06 and documented in the ERCOT Clarification Matrix for Section 6. (3) Portions of Shams Siddiqi testimony in Docket No. 31540, Proceeding to Consider Protocols to Implement a Nodal Market in the Electric Reliability Council of Texas Pursuant to Subst. R. §25.501 (November 10, 2005). |  |
| Reason for Revision |  | To incorporate into the Draft Nodal Protocols provisions approved by the Board for the Zonal market and determined by the ERCOT stakeholders to be relevant to the Nodal market. To document stakeholder understanding of questions raised by ERCOT Staff during their review of the Draft Nodal Protocols. |  |
| Credit Implications (Yes or No, and summary of impact) |  | N/A |  |
| Timeline |  |  |  |
| Date Posted |  |  |  |
| Please access the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Trip Doggett on behalf of TPTF |
| E-mail Address | tdoggett@ercot.com |
| Company | ERCOT |
| Company Address | 2705 West lake Dr., Taylor, TX 76574 |
| Phone Number | (512) 248-6360 |
| Fax Number | (512) 248-3992 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive NPRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the NPRR.

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Inclusion of these revisions provides for a Nodal market design that more completely reflects the intentions of the ERCOT stakeholders. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

Proposed Nodal Protocol Language Revision

ERCOT Nodal Protocols

Section 6: Adjustment Period and Real-Time Operations

May 15, 2006

ERCOT Settlements Comments

PRR468, Frequency Response Requirements and Monitoring

PRR487, Black Start Resources

PRR496, Block Bidding and Deployment of LaaRs providing Responsive Reserve Service and Non-Spinning Reserve Service

PRR499, Eliminate Fuel Shortage Notice

PRR513, Verification of Operational Model after Recurring Local Congestion Event – does not appear to belong to Section 6.5.7.1.10.

PRR531, Load Clarification

PRR543, Schedules and Emergency Assistance Over CFE-ERCOT DC Ties

PRR561, Remove Nuclear and Hydroelectric Generators from Automatic Deployment Software

PRR611, Reporting of Operation Reserve Capability Under Severe Gas Curtailments

PRR612, Ancillary Service Procurement During the Adjustment Period

ERCOT Clarifications - MP

ERCOT Clarifications - ST

ERCOT Clarifications - BTW

ERCOT Clarifications - HX

ERCOT Clarifications - JMA

ERCOT Clarifications – J F

ERCOT Clarifications – J S H A

ERCOT Clarifications – AB

Additional ERCOT Clarifications – AB  {{These clarifications have not yet been discussed by TPTF}}

Additional ERCOT Clarifications - MM  {{These clarifications have not yet been discussed by TPTF.}}

Shams Siddiqi

Conform Style

Format List

6	Adjustment Period and Real-Time Operations	6-1

6.1	Introduction	6-1

6.2	Market Timeline Summary	6-1

6.3	Adjustment Period and Real-Time Operations Timeline	6-2

6.3.1 	Activities for the Adjustment Period	6-1

6.3.2	Activities for Real-Time Operations	6-2

6.3.3	Real-Time Timeline Deviations	6-3

6.3.4	ERCOT Notification of Validation Rules for Real-Time	6-4

6.4	Adjustment Period	6-4

6.4.1	Capacity Trade, Energy Trade, Self-Schedule, and Ancillary Service Trades	6-4

6.4.2	Output Schedules	6-4

6.4.2.1	Output Schedules for Resources Other than Dynamically Scheduled Resources	6-5

6.4.2.2	Output Schedules for Dynamically Scheduled Resources	6-5

6.4.2.3	Output Schedule Criteria	6-6

6.4.2.4	Output Schedule Validation	6-7

6.4.2.5	DSR Load	6-7

6.4.3	Energy Offer Curve	6-8

6.4.4	Incremental and Decremental Energy Offer Curves	6-8

6.4.5	Resource Status	6-8

6.4.6	QSE-Requested Decommitment of Resources	6-9

6.4.6.1	QSE Request to Decommit Resources in the Operating Period	6-9

6.4.6.2	QSE Request to Decommit Resources in the Adjustment Period	6-9

6.4.7	Notification of Forced Outage of a Resource	6-10

6.4.8	Ancillary Services Capacity During the Adjustment Period and in Real-Time	6-10

6.4.8.1	Evaluation and Maintenance of Ancillary Service Capacity Sufficiency	6-10

6.4.8.1.1	ERCOT Increases to the Ancillary Services Plan	6-11

6.4.8.1.2	Replacement of Undeliverable Ancillary Service Due to Transmission Constraints	6-11

6.4.8.1.3	Replacement of Ancillary Service Due to Failure to Provide	6-12

6.4.8.2	Supplemental Ancillary Services Market	6-13

6.4.8.2.1	Resubmitting Offers for Ancillary Services in the Adjustment Period	6-15

6.4.8.2.2	SASM Clearing Process	6-15

6.4.8.2.3	Communication of SASM Results	6-16

6.5	Real-Time Energy Operations	6-16

6.5.1	ERCOT Activities	6-16

6.5.1.1	ERCOT Control Area Authority	6-17

6.5.1.2	Centralized Dispatch	6-17

6.5.2	Operating Standards	6-18

6.5.3	Equipment Operating Ratings and Limits	6-18

6.5.4	Inadvertent Energy Account	6-18

6.5.5	QSE Activities	6-19

6.5.5.1	Changes in Resource Status	6-19

6.5.5.2	Operational Data Requirements	6-19

6.5.6	TSP and DSP Responsibilities	6-22

6.5.7	Energy Dispatch Methodology	6-22

6.5.7.1	Real-Time Sequence	6-22

6.5.7.1.1	SCADA Telemetry	6-23

6.5.7.1.2	Network Topology Builder	6-23

6.5.7.1.3	Bus Load Forecast	6-23

6.5.7.1.4	State Estimator	6-24

6.5.7.1.5	Topology Consistency Analyzer	6-24

6.5.7.1.6	Breakers/Switch Status Alarm Processor and Forced Outage Detection Processor	6-24

6.5.7.1.7	Real-Time Weather and Dynamic Rating Processor	6-24

6.5.7.1.8	Overload Alarm Processor	6-25

6.5.7.1.9	Contingency List and Contingency Screening	6-25

6.5.7.1.10	Network Security Analysis Processor and Security Violation Alarm	6-25

6.5.7.1.11	Transmission Constraint Management	6-26

6.5.7.1.12	Resource Limits	6-26

6.5.7.1.13	Data Inputs and Outputs for the Real-Time Sequence and SCED	6-27

6.5.7.2	Resource Limit Calculator	6-29

6.5.7.3	Security Constrained Economic Dispatch	6-33

6.5.7.4	Base Points	6-37

6.5.7.5	Ancillary Services Capacity Monitor	6-37

6.5.7.6 	Load Frequency Control	6-38

6.5.7.6.1	LFC Process Description	6-39

6.5.7.6.2	LFC Deployment	6-40

6.5.7.6.2.1	Deployment of Regulation Service	6-40

6.5.7.6.2.2	Deployment of Responsive Reserve Service	6-41

6.5.7.6.2.3	Non-Spinning Reserve Service Deployment	6-43

6.5.7.7	Voltage Support Service	6-44

6.5.7.8	Dispatch Procedures	6-45

6.5.7.9	Compliance with Dispatch Instructions	6-46

6.5.8	Verbal Dispatch Instructions	6-47

6.5.9	Emergency Operations	6-48

6.5.9.1	Emergency and Short Supply Operation	6-48

6.5.9.2	Failure of the SCED Process	6-49

6.5.9.3	Communication under Emergency Conditions	6-50

6.5.9.3.1	Operating Condition Notice	6-50

6.5.9.3.2	Advisory	6-51

6.5.9.3.3	Alert	6-52

6.5.9.3.4	Emergency Notice	6-53

6.5.9.4	Emergency Electric Curtailment Plan	6-54

6.5.9.4.1	EECP Steps	6-55

6.5.9.4.2	Restoration of Market Operations	6-57

6.5.9.5	Block Load Transfers between ERCOT and Non-ERCOT Control Areas	6-57

6.5.9.5.1	Registration of BLT Points	6-59

6.5.9.5.2	Scheduling and Operation of BLTs	6-59

6.5.9.6	Black Start	6-60

6.6	Settlement Calculations for the Real-Time Energy Operations	6-60

6.6.1	Real-Time Settlement Point Prices	6-60

6.6.1.1	Real-Time Settlement Point Price for a Resource Node	6-60

6.6.1.2	Real-Time Settlement Point Price for a Load Zone	6-61

6.6.1.3	Real-Time Settlement Point Price for a Hub	6-62

6.6.2	Load Ratio Share	6-62

6.6.2.1	ERCOT Total Adjusted Metered Load	6-62

6.6.2.2	QSE Load Ratio Share for a 15-Minute Settlement Interval	6-62

6.6.2.3	QSE Load Ratio Share for an Operating Hour	6-63

6.6.3	Real-Time Energy Charges and Payments	6-63

6.6.3.1	Real-Time Energy Imbalance Payment or Charge at a Resource Node	6-63

6.6.3.2	Real-Time Energy Imbalance Payment or Charge at a Load Zone	6-65

6.6.3.3	Real-Time Energy Imbalance Payment or Charge at a Hub	6-67

6.6.3.4	Real-Time Energy Payment for DC Tie Import	6-70

6.6.3.5	Real-Time Payment for a Block Load Transfer Point	6-71

6.6.3.6	Real-Time Energy Charge for DC Tie Export Represented by the QSE Under the Oklaunion Exemption	6-74

37	6-75

6.6.4	Real-Time Congestion Payment or Charge for Self-Schedules	6-76

6.6.5	Generation Resource Base-Point Deviation Charge	6-77

6.6.5.1	General Generation Resource Base-Point Deviation Charge	6-78

6.6.5.1.1	Base Point Deviation Charge for Over Generation	6-78

6.6.5.1.2	Base Point Deviation Charge for Under Generation	6-79

6.6.5.2	IRR Generation Resource Base-Point Deviation Charge	6-80

6.6.5.3	Generators Exempt from Deviation Charges	6-81

6.6.5.4	Base Point Deviation Payment	6-82

6.6.6	Reliability Must-Run Settlement	6-82

6.6.6.1	RMR Standby Payment	6-82

6.6.6.2	RMR Payment for Energy	6-85

6.6.6.3	RMR Adjustment Charge	6-87

6.6.6.4	RMR Charge for Unexcused Misconduct	6-89

6.6.6.5	RMR Service Charge	6-89

6.6.7	Voltage Support Settlement	6-92

6.6.7.1	Voltage Support Service Payments	6-92

6.6.7.2	Voltage Support Charge	6-94

6.6.8	Black Start Capacity	6-95

6.6.8.1	Black Start Capacity Payment	6-95

6.6.8.2	Black Start Capacity Charge	6-96

6.6.9	Emergency Operations Settlement	6-97

6.6.9.1	Payment for Emergency Power Increase directed by ERCOT	6-97

6.6.9.2	Charge for Emergency Power Increases	6-99

6.6.10	Real-Time Revenue Neutrality Allocation	6-100

6.7	Real-Time Settlement Calculations for the Ancillary Services	6-104

6.7.1	Payments for Ancillary Service Capacity Sold in a Supplemental Ancillary Service Market	6-104

6.7.2	Charges for Ancillary Service Capacity Replaced Due to Failure to Provide	6-106

6.7.3	Adjustments to Cost Allocations for Ancillary Services Procurement	6-107

# Adjustment Period and Real-Time Operations

6.1	Introduction

(1)	This Section addresses the following components: the Adjustment Period and Real-Time Operations, including Emergency Operations.

(2)	The Adjustment Period provides each QSE the opportunity to adjust its trades, Self-Schedules, and Resource commitments as more accurate information becomes available under Section 6.4, Adjustment Period.  During the Adjustment Period, ERCOT continues to evaluate system sufficiency and security by use of Hour-Ahead Reliability Unit Commitment processes, as described in Section 5, Transmission Security Analysis and Reliability Unit Commitment.  Under certain conditions during the Adjustment Period, ERCOT may also open one or more Supplemental Ancillary Service Markets (SASMs), as described in Section 6.4.8.2, Supplemental Ancillary Services Market.

(3)	During Real-Time operations, ERCOT dispatches Resources under normal system conditions and behavior based on economics and reliability to match system Load with On-Line generation while observing Resource and transmission constraints. The Security Constrained Economic Dispatch (SCED) process produces Base Points for Resources. ERCOT uses the Base Points from the SCED process and uses the deployment of Regulation Up (Reg-Up), Regulation Down (Reg-Down), Responsive Reserve, and Non-Spinning Reserve (Non-Spin) to control frequency and solve potential reliability issues.

(4)	Under Emergency Conditions, as described in Section 6.5.9, Emergency Operations, ERCOT may implement manual procedures and must keep the Market Participants informed of the status of the system.

(5)	Real-Time energy settlements use Real-Time Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs for a 15-minute Settlement Interval, using the LMPs from all of the executions of SCED in the Settlement Interval.  In contrast, the DAM energy settlements will use DAM Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs for a one-hour Settlement Interval.

6.2	Market Timeline Summary

The figure below is a high-level summary of the overall market timeline:

6.3	Adjustment Period and Real-Time Operations Timeline

(1)	The figure below highlights the major activities that occur in the Adjustment Period and Real-Time operations:

(2)	Activities for the Adjustment Period begin at 1800 in the Day-Ahead and end one full hour before the start of the Operating Hour.  The figure above is intended to be only a general guide and not controlling language, and any conflict between this figure and another section of the Protocols is controlled by the other section.

(3)	All Real-Time LMPs, SASM MCPCs, and Real-Time Settlement Point Prices are final at 1600 of the next Business Day after the Operating Day.  After Real-Time LMPs, SASM MCPCs, and Real-Time Settlement Point Prices are final, they cannot be changed unless the Board finds that the Real-Time LMPs, SASM MCPCs, or Real-Time Settlement Point Prices are significantly affected by a software or data error.

6.3.1 	Activities for the Adjustment Period

(1)	The following table summarizes the timeline for the Adjustment Period and the activities of QSEs and ERCOT.  The table is intended to be only a general guide and not controlling language, and any conflict between this table and another section of the Protocols is controlled by the other section:

| Adjustment Period | QSE Activities | ERCOT Activities |
| --- | --- | --- |
| Time = From 1800 in the Day-Ahead up to one hour before the start of the Operating Hour | Submit and update Energy Trades, Capacity Trades, Self-Schedules, and Ancillary Service Trades Submit and update Output Schedules Submit and update Incremental and Decremental Energy Offer Curves for Dynamically Scheduled Resources (DSRs) Submit and update Energy Offer Curves Update Current Operating Plan (COP) Request Resource decommitments Submit Three-Part Supply Offers for Off-Line Generation Resources Submit offers for any Supplemental Ancillary Service Markets Communicate Resource Forced Outages | Post shift schedules on the MIS Secure Area. Validate Energy Trades, Capacity Trades, Self-Schedules, and Ancillary Service Trades and identify invalid or mismatched trades. Validate Output Schedules Validate Incremental and Decremental Energy Offer Curves Validate Energy Offer Curves Validate Current Operating Plan (COP) Review and approve or reject Resource decommitments Validate Three-Part Supply Offers Publish Notice of Need to Procure Additional Ancillary Service capacity if required Validate Ancillary Service Offers At the end of the Adjustment Period snap-shot the net capacity credits for HRUC Settlement Update Short-Term Wind Power Forecast (WGRPP) Execute the Hour-Ahead Sequence Notify the QSE via the MIS Certified Area that an Energy Offer Curve or Output Schedule has not yet been submitted for a Resource as a reminder that one of the two must be submitted by the end of the Adjustment Period |

6.3.2	Activities for Real-Time Operations

(1)	Activities for Real-Time operations begin at the end of the Adjustment Period and conclude at the close of the Operating Hour.

(2)	The following table summarizes the timeline for the Operating Period and the activities of QSEs and ERCOT during Real-Time operations where “T” represents any instant within the Operating Hour.  The table is intended to be only a general guide and not controlling language, and any conflict between this table and another section of the Protocols is controlled by the other section:

| Operating Period | QSE Activities | ERCOT Activities |
| --- | --- | --- |
| During the first hour of the Operating Period |  | Execute the Hour-Ahead Sequence, including HRUC, beginning with the second hour of the Operating Period Review and communicate HRUC commitments |
| Before the start of each SCED run | Update Output Schedules for Dynamically Scheduled Resources (DSRs) | Validate Output Schedules for Dynamically Scheduled Resources (DSRs) Execute Real-Time Sequence |
| SCED run |  | Execute SCED |
| During the Operating Hour | Acknowledge receipt of Dispatch Instructions Comply with Dispatch Instruction Review Resource Status to assure current state of the Resources is properly telemetered Update Current Operating Plan with actual Resource Status and limits and Ancillary Service Schedules Communicate Resource Forced Outages to ERCOT | Communicate all Base Points, Dispatch Instructions and LMPs for energy and Ancillary Services using ICCP, SCADA, or Verbal Dispatch Instructions Monitor Resource Status and identify discrepancies between Current Operating Plan and telemetered Resource Status Restart Real-Time Sequence on major change of Resource or Transmission Element Status Monitor ERCOT total system capacity providing Ancillary Services; Validate COP information Monitor ERCOT control performance; Distribute by ICCP, and post to the MIS Public Area, the LMPs created by each SCED process for each Resource Node , and the Settlement Point Price at each Hub and Load Zone immediately on deployment of Base Points from SCED with the time stamp the prices are effective Post SCED Shadow Prices via the MIS Public Area Post on the MIS Public Area active binding transmission constraints by Transmission Element name (contingency /overloaded element pairs) via the MIS Public Area Post the Settlement Point Prices for each Settlement Point immediately following the end of each Settlement Interval Post parameters as required by Section 6.4.8, Ancillary Services Capacity During the Adjustment Period and in Real-Time, to the MIS Secure Area |

(3)	At the beginning of each hour, ERCOT shall post on the MIS Secure Area the following information:

(a)	Changes in ERCOT System conditions that could affect the security and dynamic transmission limits of the ERCOT System, including:

(i)	changes or expected changes,  in the status of Transmission Facilities for the remaining hours of the current Operating Day and all hours of the next Operating Day, supplementing those that are already in the Outage Scheduler; and

(ii)	any conditions such as adverse weather conditions as determined from the ERCOT-designated weather service;

(b)	Updated system-wide Load forecasts;

(c)	The quantities of RMR Services deployed by ERCOT for each previous hour of the current Operating Day;

(d)	Total ERCOT System Demand, from Real-Time operations, integrated over each Settlement Interval; and

(e)	Updated Electrical Bus Load distribution factors and other information necessary to forecast Electrical Bus Loads for each hour of the current Operating Day and all hours of the next Operating Day.

6.3.3	Real-Time Timeline Deviations

ERCOT may temporarily deviate from the Real-Time deadlines but only to the extent necessary to ensure the secure operation of the ERCOT System.  Temporary measures may include varying the timing requirements as specified below or omitting one or more procedures in the Real-Time Sequence.  In such an event, ERCOT shall immediately declare an Emergency Condition and notify all QSEs of the following:

(a)	Details of the affected timing requirements and procedures;

(b)	Details of any interim requirements;

(c)	An estimate of the period for which the interim requirements apply; and

(d)	Reasons for the temporary variation.

6.3.4	ERCOT Notification of Validation Rules for Real-Time

ERCOT shall provide each QSE with the information necessary to pre-validate its data for Real-Time operations including publishing validation rules for offers, bids, and trades and posting any software documentation and code that is not Protected Information to the MIS Secure Area within five Business Days after receipt by ERCOT.

6.4	Adjustment Period

6.4.1	Capacity Trade, Energy Trade, Self-Schedule, and Ancillary Service Trades

(1)	A detailed explanation of Capacity Trade criteria and validations performed by ERCOT is provided in Section 4.4.1, Capacity Trades. A QSE may submit and update Capacity Trades during the Adjustment Period.

(2)	A detailed explanation of Energy Trade criteria and validations performed by ERCOT is provided in Section 4.4.2, Energy Trades.  A QSE may submit and update Energy Trades during the Adjustment Period and through 1430 on the day following the Operating Day for Settlement.

(3)	A detailed explanation of Self-Schedule criteria and validations performed by ERCOT is provided in Section 4.4.3, Self-Schedules.  A QSE may submit and update Self-Schedules during the Adjustment Period.

(4)	A detailed explanation of Ancillary Service Trade criteria and validations performed by ERCOT is provided in Section 4.4.7.3, Ancillary Service Trades. A QSE may submit and update Ancillary Service Trades during the Adjustment Period.

6.4.2	Output Schedules

(1)	A QSE that represents a Resource, other than an RMR Unit, must submit and maintain either an Energy Offer Curve or an Output Schedule for the Resource for all times when the Resource is On-Line.

(2)	For an On-Line RMR Unit, ERCOT, in its sole discretion, shall submit either an Output Schedule or an Energy Offer Curve, considering contractual constraints on the Resource and any other adverse effects on, or implications arising from, the RMR Agreement, that may occur as the result of the Dispatch of the RMR Unit.

(3)	The entry of an Energy Offer Curve for a Resource automatically nullifies the Output Schedule for that Resource and prohibits entry of future Output Schedules for that Resource for the time during which the Energy Offer Curve is in effect.

(4)	For a Resource for which an Energy Offer Curve has not been submitted, the SCED process uses the Output Schedule submitted for that Resource as desired Dispatch levels for the Resource.

6.4.2.1	Output Schedules for Resources Other than Dynamically Scheduled Resources

(1)	An Output Schedule for a non-DSR Resource may be submitted and updated only during the Adjustment Period.  An Output Schedule for a non-DSR Resource may be submitted and updated for each five-minute interval for each Operating Hour.

(2)	For a Resource that is not a DSR and that is On-Line, the following provisions apply:

(a)	The Output Schedule for a Qualifying Facility (QF) not submitting an Energy Offer Curve is considered to be equal to the telemetered output of the QF at the time that the SCED runs;

(b)	The Output Schedule for Intermittent Renewable Resources not submitting Energy Offer Curves is considered to be equal to the telemetered output of the Resource at the time that the SCED runs; and

(c)	ERCOT shall create proxy Energy Offer Curves for the Resource under Section 6.5.7.3, Security Constrained Economic Dispatch, paragraph (3)(a).

6.4.2.2	Output Schedules for Dynamically Scheduled Resources

(1)	A QSE representing a DSR may update the Output Schedule for a dispatch interval at any time before the SCED process for that interval.

(2)	For a DSR that is On-Line, the following provisions apply:

(a)	For an On-Line DSR for which its QSE has not submitted an Incremental and Decremental Energy Offer Curve, ERCOT shall use the Output Schedule available at the SCED snapshot for the execution of the SCED and shall assume that the scheduled MW amount in the Output Schedule is the Base Point for the DSR for that SCED interval. ERCOT shall create proxy Energy Offer Curves for the DSR under Section 6.5.7.3, Security Constrained Economic Dispatch, paragraph (3)(a).

(b)	If the QSE representing a DSR submits an Incremental and Decremental Energy Offer Curve under Section 6.4.4, Incremental and Decremental Energy Offer Curves, then ERCOT shall use the Incremental and Decremental Energy Offer Curve to create proxy Energy Offer Curves for the DSR under Section 6.5.7.3, Security Constrained Economic Dispatch, paragraph (3)(b).

(c)	For a DSR that is dispatched to a Base Point other than its Output Schedule for that SCED interval, the Base-Point Deviation Charge under Section 6.6.5, Generation Resource Base-Point Deviation Charge, applies:

(i)	beginning after four consecutive, complete 15-minute Settlement Intervals have occurred after the DSR is dispatched to a Base Point other than its Output Schedule; and

(ii)	ending when the DSR is no longer dispatched to a Base Point other than its Output Schedule.

(d)	After the DSR is no longer dispatched to a Base Point other than its Output Schedule, the 15 MW or 15% limit, whichever is greater, under paragraph (3) of Section 6.4.2.3, Output Schedule Criteria, does not apply to the DSR until four consecutive, complete 15-minute Settlement Intervals have occurred after the DSR is no longer dispatched to a Base Point other than its Output Schedule.

6.4.2.3	Output Schedule Criteria

(1)	An Output Schedule submitted by a QSE for a Resource that is not an RMR Unit and by ERCOT for an RMR Unit must include the following:

(a)	The name of the Entity submitting the Output Schedule for the Resource;

(b)	The name of the Resource;

(c)	The desired MW output level for each five-minute interval for the Resource for all of the remaining five-minute intervals in the Operating Day for which an Energy Offer Curve has not been submitted.

(2)	ERCOT must reject an Output Schedule for a Resource if an Energy Offer Curve corresponding to any period in the Output Schedule exists;

(3)	For a QSE representing one or more Dynamically Scheduled Resources, the sum of all Output Schedules (excluding Ancillary Services Energy deployments, energy deployed through Dispatch Instructions, and Energy Trades) for the QSE must be within 15% or 15 MW (whichever is greater) of the aggregate telemetered DSR Load;

(4)	The MW difference between Output Schedules for any two consecutive five-minute intervals must be less than 10 times the SCED Up Ramp Rate for schedules showing an increase from the prior period and the SCED Down Ramp Rate for schedules showing a decrease from the prior period.

(5)	The Output Schedule for each interval in the Operating Period must be less than the Resource’s HSL and must be greater than the Resource’s LSL for the corresponding hour.

6.4.2.4	Output Schedule Validation

(1)	A validated Output Schedule is a schedule that ERCOT has determined meets the criteria listed in Section 6.4.2.3, Output Schedule Criteria.

(2)	ERCOT shall notify the QSE submitting an Output Schedule by the Messaging System if the schedule was rejected or was considered invalid for any reason.  The QSE may then resubmit the schedule within the appropriate market timeline.

(3)	ERCOT shall continuously validate Output Schedules and continuously display on the MIS Certified Area information that allows any QSE to view its valid Output Schedule.

(4)	If a valid Output Schedule does not exist for a Resource that has a status of On-Line Dynamically Scheduled Resource at the time of SCED execution, then ERCOT shall notify the QSE and set the Output Schedule equal to the telemetered output of the Resource until a revised Output Schedule is validated.

(5)	If a valid Energy Offer Curve or an Output Schedule does not exist for a non-Dynamically Scheduled Resource that has a status of On-Line at the end of the Adjustment Period, then ERCOT shall notify the QSE and set the Output Schedule equal to the then current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period.

6.4.2.5	DSR Load

(1)	A QSE may designate a Resource in the Current Operating Plan and through the telemetered Resource Status as a participant in the QSE’s control of DSR Load under the requirements in Section 16.2.3.2, Process to Gain Approval to Follow DSR Load.

(2)	Each QSE may not have more than one DSR Load.

(3)	The following principles for DSR Load apply:

(a)	All power signals for DSR Load must be sent to ERCOT in Real-Time by telemetry; and

(b)	If a DSR Load signal is lost for any reason for a period greater than one 15-minute Settlement Interval, then ERCOT shall notify the QSE and suspend validation of Dynamically Scheduled Resource Output Schedules.  If the DSR Load signal fails for more than 10 consecutive hours, ERCOT shall suspend the QSE’s ability to use Dynamically Scheduled Resources until the signal is reliably restored (as determined by ERCOT).  If the signal failure is identified to be an ERCOT communication problem, ERCOT may not suspend the QSE’s ability to use Dynamically Scheduled Resources.

6.4.3	Energy Offer Curve

(1)	A detailed description of Energy Offer Curve and validations performed by ERCOT is in Section 4.4.9, Energy Offers and Bids.

(2)	For an On-Line RMR Unit, ERCOT, in its sole discretion, shall submit either an Output Schedule or an Energy Offer Curve considering contractual constraints on the Resource and any other adverse effects on, or implications arising from, the RMR Agreement, that may occur as the result of the Dispatch of the RMR Unit.  If ERCOT chooses to submit an Energy Offer Curve instead of an Output Schedule, the Energy Offer Curve must be based on the RMR Agreement input/output curve and the fuel budget for the RMR Unit.

(3)	If a valid Energy Offer Curve or an Output Schedule does not exist for a Resource that has a status of On-Line at the end of the Adjustment Period, then ERCOT shall notify the QSE and create an Output Schedule equal to the then-current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period.

6.4.4	Incremental and Decremental Energy Offer Curves

A QSE for a DSR may submit an “Incremental Energy Offer Curve” and a “Decremental Energy Offer Curve” in addition to the Output Schedule for the DSR.  At every MW value of the curves, the price of the Incremental Energy Offer Curve must be greater than the Decremental Energy Offer Curve. Incremental and Decremental Energy Offer Curves are subject to the same requirements for the same criteria and validations performed by ERCOT as provided in Section 4.4.9, Energy Offers and Bids.

6.4.5	Resource Status

(1)	ERCOT shall use the telemetered Resource Status for all applications requiring status of Resources during the Operating Hour, including SCED, Load Frequency Control (LFC), and Network Security Analysis processes. QSEs shall provide ERCOT with accurate telemetry of the current capability of each Resource including the Resource Status, Ramp Rates, HSL, and LSL and a text reason for any Resource where a Ramp Rate is deviating from a standard Ramp Rate curve for the Resource, or the HSL is less than, or LSL is greater than, the normal high and low limits set in Section 3.7.1, Resource Parameter Criteria.

(2)	ERCOT shall perform the following validations during the Operating Period:

(a)	Each QSE shall provide the Real-Time operating status of each Resource to ERCOT by telemetry using the status codes in the Current Operating Plan for Real-Time as described in Section 3.9, Current Operating Plan (COP); and

(b)	Five minutes before the end of each hour, ERCOT shall identify inconsistencies between the telemetered Resource Status and the Resource Status stated in the COP for that Resource in the next hour.  On detecting an inconsistency, ERCOT shall provide a notice of inconsistent Resource Status to the QSE using the Messaging System.

6.4.6	QSE-Requested Decommitment of Resources

(1)	A Resource must remain committed during any RUC-Committed Interval unless the Resource has a Forced Outage.

(2)	In the Operating Period, a QSE may request to decommit a Resource for any interval that is not a RUC-Committed Interval by verbally requesting ERCOT to consider its request.

(3)	In the Adjustment Period, a QSE may request to decommit a Resource for any interval that is not a RUC-Committed Interval by indicating a change in unit status in the QSE’s COP.

(4)	A Resource cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. If a Resource that is decommitted for a DAM-Committed Interval, that one-hour DAM-Committed Interval is excluded from the calculation of any Day-Ahead Make-Whole Payment for that Resource.

6.4.6.1	QSE Request to Decommit Resources in the Operating Period

(1)	For a request made during the Operating Period to decommit a Resource, ERCOT may perform a study using Real-Time conditions to determine if ERCOT will remain n-1 secure with that Resource Off-Line.  ERCOT may grant the request if analysis indicates the Resource Outage contingency results in no additional active constraints for SCED.  ERCOT may only approve requests that do not have a reliability impact.

(2)	If more units are requesting decommitment than can be accommodated, ERCOT shall review the requests in order of receipt.

6.4.6.2	QSE Request to Decommit Resources in the Adjustment Period

(1)	To decommit an otherwise available Resource for hours other than the Operating Period, the QSE must update the COP indicating the change in Resource Status for each hour in the COP for the remaining hours in the Adjustment Period. On detection of a change from On-Line to Off-Line Available state in future hours for a Resource, ERCOT shall review all requests for decommitment using the next scheduled HRUC.  The Resource must be shown as available for HRUC commitment.  The next HRUC commitment must consider the Resource’s Minimum-Energy Offer excluding the Resource’s Startup Offer from the Three-Part Supply Offer.

(2)	If HRUC continues to require the Resource to be committed, ERCOT shall notify the QSE, using the process described in Section 5.5.3, Communication of RUC Commitments and Decommitments, that the decommitment has been denied, and the affected intervals become RUC-Committed Intervals instead of QSE-Committed Intervals for RUC Settlement purposes. The QSE must update its COP to denote the RUC-Committed Intervals.

6.4.7	Notification of Forced Outage of a Resource

In the event of a Forced Outage of a Resource, the telemetered status of the Resource automatically notifies ERCOT of the event.  In the event of a Forced Outage, an impending Forced Outage, or de-rating of a Resource, the QSE shall inform ERCOT of the following:

(a)	Time of expected change in Resource Status or rating;

(b)	Text message describing the nature of the Forced Outage or de-rating updated as new information becomes available; and

(c)	The expected minimum and maximum duration of the Forced Outage or de-rating.

6.4.8	Ancillary Services Capacity During the Adjustment Period and in Real-Time

6.4.8.1	Evaluation and Maintenance of Ancillary Service Capacity Sufficiency

(1)	ERCOT shall evaluate Ancillary Service requirements and capacity sufficiency using the Ancillary Services Capacity Monitor, described in Section 6.5.7.5, Ancillary Services Capacity Monitor, throughout the Adjustment Period and Operating Period and may procure Ancillary Services in the Adjustment Period for:

(a) 	increased need of Ancillary Services capacity above that specified in the Day-Ahead;

(b) 	replacement of Ancillary Services capacity that is undeliverable due to transmission constraints; or

(c) 	replacement of Ancillary Services capacity due to failure to provide.

(2)	A QSE may change the specific Resources supplying Ancillary Services under Section 3.9, Current Operating Plan (COP) using the QSE’s Ancillary Service Schedule in the COP only if, in ERCOT’s determination, that change does not adversely affect the deliverability of the service(s) being allocated to an alternate Resource and if that change does not adversely affect the deliverability of other services previously procured by ERCOT.  A QSE may not change the quantity provided of each type Ancillary Services awarded through the ERCOT procurement process or the aggregate amount of Self-Arranged Ancillary Services (by Ancillary Service type) from the DAM. On detection of a change in COP for Resources providing Ancillary Services, ERCOT shall review the impact on deliverability and communicate to the QSE if the change is not approved.  The QSE must update its COP to reflect the ERCOT decision. If ERCOT does not act on the request by the beginning of the Operating Hour in which the change will take effect, the request is deemed approved.

6.4.8.1.1	ERCOT Increases to the Ancillary Services Plan

(1)	If ERCOT determines in the Adjustment Period, in its sole discretion, that more Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead Ancillary Services Plan, it shall notify each QSE of its increased Ancillary Service Supply Obligation.

(2)	ERCOT may procure more Ancillary Services through a Supplemental Ancillary Services Market, as described below in Section 6.4.8.2, Supplemental Ancillary Services Market (SASM) if the Self-Arranged Ancillary Service quantities are insufficient to meet the total Ancillary Service Supply Obligation.

(3)	When a SASM has been executed in response to ERCOT increasing the Ancillary Services Plan, each QSE that purchases Ancillary Service capacity shall be charged its share of the net cost incurred for that service, in accordance with Section 6.7.3, Adjustments to Cost Allocations for Ancillary Services Procurement.

6.4.8.1.2	Replacement of Undeliverable Ancillary Service Due to Transmission Constraints

(1)	The HRUC process must honor the HASL and LASL for each Resource for each hour of the RUC Study Period unless by doing so a transmission constraint exists where energy from the Resource is needed to resolve the constraint that cannot be resolved by any other means or the energy output from the Resource must be decreased such that the Resource is unable to provide the Ancillary Service capacity allocated to that Resource in the COP.  In those cases, ERCOT shall provide the following information to each affected QSE with two hours’ advance notice of:

(a)	The amount by which the QSE must reduce the Ancillary Services currently allocated to each affected Resource; and

(b)	The start and stop times of the reduction.

(2)	Within the two-hour advance notice period, each affected QSE may do one or more of the following:

(a)	Substitute capacity from other Resources represented by that QSE to meet its Ancillary Services Supply Responsibility;

(b)	Substitute capacity from other QSEs using Ancillary Service Trades; or

(c)	Inform ERCOT that all or part of the Ancillary Services capacity needs to be replaced.

(3)	If a QSE elects to substitute capacity, ERCOT shall determine the feasibility of the substitution.  If the substitution is deemed infeasible by ERCOT or the QSE informs ERCOT that the Ancillary Services capacity needs to be replaced, then ERCOT shall procure, if in its sole discretion it finds that the service is still needed, the Ancillary Services capacity required under Section 6.4.8.2, Supplemental Ancillary Services Market.

(4) 	If ERCOT procures additional Ancillary Services for the amount of substituted capacity that is deemed infeasible or the amount of Ancillary Services capacity that each affected QSE does not replace, then all QSEs that bought the specific Ancillary Service in the DAM are charged for their share of the net cost incurred for the Ancillary Service procured by ERCOT as part of the multiple procurement processes (DAM and SASMs) , in accordance with Section 6.7.3, Adjustments to Cost Allocations for Ancillary Services Procurement.

(5)	If the QSE’s Ancillary Service capacity that is undeliverable because of a transmission constraint identified by ERCOT, as set forth in (1) above, was not awarded in the DAM or any SASM (i.e., the capacity is part of  Self-Arranged Ancillary Services for the hours of the RUC Study Period), then the QSE is charged for the insufficient Ancillary Service capacity the same price paid for the Ancillary Service as purchasers in the DAM paid for that time period, as determined under paragraph (4) above.

(6)	If the QSE’s Ancillary Service capacity that is undeliverable because of a transmission constraint identified by ERCOT, as set forth in (1) above, was awarded in the DAM or any SASM, then the QSE is not compensated for the quantity of the Ancillary Service capacity that is undeliverable.

6.4.8.1.3	Replacement of Ancillary Service Due to Failure to Provide

(1)	ERCOT may procure Ancillary Services to replace those of a QSE that has failed on its Ancillary Services Supply Responsibility through a Supplemental Ancillary Services Market, as described below in Section 6.4.8.2, Supplemental Ancillary Services Market.  A QSE is considered to have failed on its Ancillary Services Supply Responsibility when ERCOT determines, in its sole discretion, that some or all of the QSE’s Resource-specific Ancillary Service capacity will not be available in Real-Time. This Section does not apply to a failure to provide caused by events described in Section 6.4.8.1.2, Replacement of Undeliverable Ancillary Service Due to Transmission Constraints.

(2)	Within a time frame acceptable to ERCOT, each affected QSE may either substitute capacity to meet its Ancillary Services Supply Responsibility or inform ERCOT that the Ancillary Services capacity needs to be replaced.  If a QSE elects to substitute capacity, ERCOT shall determine the feasibility of the substitution.  If the substitution is deemed infeasible by ERCOT or the QSE informs ERCOT that the Ancillary Services capacity needs to be replaced, then ERCOT shall procure, if in its sole discretion it finds that the service is still needed, the Ancillary Services capacity required under Section 6.4.8.2, Supplemental Ancillary Services Market.

(3)	ERCOT shall charge each QSE that has failed according to paragraph (1) on its Ancillary Service Supply Responsibility for a particular Ancillary Service for a specific hour.  The hourly charge of the failure is either (a) or (b):

(a)	If a SASM is executed for that hour, then the charge equals the MW amount of the failed Ancillary Services Supply Responsibility multiplied by the greater of the:

(i)	The MCPC for the Ancillary Service in the DAM for that hour ; or

(ii)	The maximum MCPC set from any SASM for the same operating hour.

(b)	If no SASM is executed for failure to supply for that hour, then the cost equals the MW amount of the failed Ancillary Services Supply Responsibility multiplied by the MCPC for the Ancillary Service in the DAM for that hour.

(4)	If the Ancillary Service capacity of the affected QSE was awarded in the DAM or any SASM, then the QSE is still compensated for the quantity of the Ancillary Service capacity.

(5)	If the Ancillary Service capacity of the affected QSE was not awarded in the DAM or any SASM (i.e., Self-Arranged Ancillary Service), then the QSE continues to receive credit toward its Ancillary Service Supply Responsibility.

6.4.8.2	Supplemental Ancillary Services Market

(1)	During the Adjustment Period, ERCOT may procure additional Reg-Up, Reg-Down, Responsive Reserve, and Non-Spinning Services for the reasons, and in the amounts, specified in Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency, using a Supplemental Ancillary Services Market (SASM).

(2)	{{TPTF begin rejection}} The SASM process for acquiring more Ancillary Service capacity must use the following timeline with time “X” being the time that ERCOT sends notice to all QSEs of the SASM.  Time X may be any time not less than three hours before the start of the Operating Hour for which the additional Ancillary Services capacity is required.

| SASM Process | QSE Activities: | ERCOT Activities: |
| --- | --- | --- |
| Time = X (Not later than Operating Hour start minus 180 minutes) |  | Notify all QSEs by voice communication of intent to procure additional Ancillary Services. This verbal communication will include the total amount of additional Ancillary Service capacity required |
| Time = X plus 60 minutes (Not later than Operating Hour start minus 120 minutes) | May submit additional quantity of Self-Arranged Ancillary Services limited to the additional Ancillary Services Obligation of the QSE. QSEs may resubmit Ancillary Service Offers under Section 6.4.8.2.1, Resubmitting Offers for Ancillary Service in the Adjustment Period. | - Allocate additional AS responsibility to LSEs and aggregate to the QSE level. |
| Time = X plus 90 minutes (Not later than Operating Hour start minus 90 minutes) | Submit updated COP and updated Ancillary Service Schedule. | Execute SASM. |
| Time = X plus 100 minutes (Not later than Operating Hour minus 80 minutes) |  | Notify QSEs with awards of results Post the quantities and MCPCs of Ancillary Services bought in the SASM. |
| Time = X plus 120minutes (Not later than Operator Hour minus 60) | Submit updated COP and updated Ancillary Service Schedule to include awards. | Validate COPs and Ancillary Service Schedules. |

(3)	Each QSE that is awarded capacity in a SASM is paid the SASM MCPC for the quantity it is awarded.

(4)	ERCOT shall allocate additional Ancillary Service Obligations to QSEs using the same percentages as the original Day-Ahead allocation of Ancillary Service Obligations.

6.4.8.2.1	Resubmitting Offers for Ancillary Services in the Adjustment Period

(1)	During the Adjustment Period, a QSE may resubmit an offer for an Ancillary Service that it submitted for a Resource, but was not struck in a previous market. The resubmitted offer for that Resource must meet the following criteria to be considered a valid offer in any subsequent market:

(a)	The resubmitted offer quantity (in MW) must be offered at a price equal to or less than the lowest price of the previous offer for capacity of the portion that was not resubmitted;

(b)	For any amount of the offer that is greater in quantity than the QSE’s offer that was not selected in a previous market, the incremental amount of the offer may be submitted at any price subject to applicable offer caps and offer floors; and

(c)	QSEs may change or delete any offers submitted or resubmitted during the Adjustment Period subject to the restrictions in paragraphs (a) and (b) above. {{TPTF end rejection}}

6.4.8.2.2	SASM Clearing Process

(1)	SASM procurement requirements are:

(a)	ERCOT shall procure the additional quantity required of each Ancillary Service, less the quantity self-arranged, if applicable. ERCOT may not buy more of one Ancillary Service in place of the quantity of a different service.

(b)	ERCOT shall select Ancillary Service Offers submitted by QSEs, such that:

(i)	For each Ancillary Service being procured, other than Reg-Down, ERCOT shall select offers that minimize the overall offer-based  cost of these Ancillary Services.  For each of these Ancillary Services, if selection of the Resource offer exceeds ERCOT’s required Ancillary Service quantity, then ERCOT shall select a portion of the Resource offer to meet the Ancillary Service quantity required. For Load Resources offering a block of capacity, ERCOT shall ignore the offer unless the entire block can be accepted.

(ii)	For Reg-Down, ERCOT shall procure required quantities by selecting capacity in ascending order starting from the lowest-priced offer.  ERCOT shall continue this selection process until the required quantity of Reg-Down is obtained.  If selection of the Resource offer exceeds ERCOT’s required Ancillary Service quantity, then ERCOT shall select a portion of the Resource offer to meet the Ancillary Service quantity required.  For Load Resources offering a block of capacity, ERCOT shall ignore the offer unless the entire block can be accepted.

(c)	If a QSE has submitted offers of the same Resource capacity for more than one Ancillary Service (sometimes called linked offers), ERCOT may not select any one part of that Resource capacity to provide more than one Ancillary Service in the same Operating Hour. ERCOT may, however, select part of that Resource capacity to provide one Ancillary Service and another part of that capacity to provide a different Ancillary Service in the same Operating Hour.

(d)	The SASM MCPC for each hour for each service is the Shadow Price for the corresponding Ancillary Service constraint for the hour as determined by the SASM algorithm.

6.4.8.2.3	Communication of SASM Results

(1)	As soon as practicable, but no later than the time specified in Section 6.4.8.2, Supplemental Ancillary Services Market, ERCOT shall notify each QSE of its awarded Ancillary Service Offer quantities in each SASM, specifying Resource, Ancillary Service type, SASM MCPC, and first and last hours of the awarded offer.

(2)	As soon as practicable, but no later than the time specified in Section 6.4.8.2, Supplemental Ancillary Services Market, ERCOT shall post on the MIS Public Area the hourly:

(a)	SASM MCPC for each type of Ancillary Service for each hour;

(b)	Total Ancillary Service procured in MW by Ancillary Service type for each hour; and

(c)	Aggregated Ancillary Service Offer Curve for each Ancillary Service for each hour.

(3)	ERCOT shall monitor SASM MCPCs for errors and shall “flag” for further review questionable prices before posting and make notations in the posting if there are conditions that cause the prices to be questionable.

6.5	Real-Time Energy Operations

6.5.1	ERCOT Activities

ERCOT activities during Real-Time operations are summarized in the table located in Section 6.3.2, Activities for Real-Time operations.  That table is intended to be only a general guide and not controlling language, and any conflict between the table and another section of the Protocols is controlled by the other section.

6.5.1.1	ERCOT Control Area Authority

ERCOT, as Control Area Operator (CAO), is authorized to perform the following actions for the limited purpose of securely operating the ERCOT Transmission Grid under the standards specified in NERC Standards, the Operating Guides and these Protocols, including:

(a)	Direct the physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment;

(b)	Dispatch Resources that have committed to provide Ancillary Services;

(c)	Direct changes in the operation of voltage control equipment;

(d)	Direct the implementation of RMR Service, RAPs, SPSs, and transmission switching to prevent the violation of ERCOT Transmission Grid security limits; and

(e)	Perform additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT Transmission Grid to a secure state in the event of an ERCOT Transmission Grid Emergency Condition.

6.5.1.2	Centralized Dispatch

(1)	ERCOT shall centrally Dispatch Resources and Transmission Facilities under these Protocols, including deploying energy by establishing Base Points, and Emergency Base Points, and by deploying Regulation Service, Responsive Reserve Service, and Non-Spinning Reserve Service to ensure operational security.

(2)	ERCOT shall verify that either an Energy Offer Curve providing prices for the Resource between its HSL and LSL or an Output Schedule has been submitted for each On-Line Resource an hour before the end of the Adjustment Period for the upcoming Operating Hour.  ERCOT shall notify QSEs that have not submitted an Output Schedule or Energy Offer Curve through the MIS Certified Area.

(3)	ERCOT is the regional security coordinator for the ERCOT Region and is responsible for all regional security coordination as defined in the NERC Operating Manual and applicable ERCOT operating manuals or Operating Guides.

(4)	ERCOT may only issue Dispatch Instructions for the Real-Time -operation of Transmission Facilities to a TSP, for the Real-Time operation of distribution facilities to a DSP, or for a Resource to the QSE that represents it.

(5)	ERCOT shall post shift schedules on the MIS Secure Area.

6.5.2	Operating Standards

ERCOT and each TSP shall operate the ERCOT Transmission Grid under these Protocols, and, to the extent they are not inconsistent with these Protocols, Good Utility Practice and NERC standards and policies.  These Protocols control to the extent of any inconsistency between the Protocols and any of the following documents:

(a)	The Operating Guides;

(b)	The NERC standards and policies and the ERCOT procedures manual, supplied by NERC and ERCOT, respectively, as references for ERCOT Operators to use during normal and emergency operations of the ERCOT Transmission Grid;

(c)	Specific operating procedures and RAPs submitted to ERCOT by individual Transmission Facilities owners or operators to address operating problems on their respective grids that could affect operation of the ERCOT Transmission Grid; and

(d)	Guidelines established by the ERCOT Board, which may be more stringent than those established by NERC for the secure operation of the ERCOT Transmission Grid.

6.5.3	Equipment Operating Ratings and Limits

(1)	ERCOT shall consider all equipment operating limits when issuing Dispatch Instructions.  Except as stated in Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TSP, a DSP, or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

(2)	Each TSP shall notify ERCOT of any limitations on the TSP’s system that may affect ERCOT Dispatch Instructions.  ERCOT shall continuously maintain a posting on the MIS Secure Area of any TSP limitations that may affect Dispatch Instructions.  Examples of such limitations may include: temporary changes to transmission or transformer ratings, temporary changes to range of automatic tap position capabilities on auto-transformers, fixing or blocking tap changer, changes to no-load tap positions or other limitations affecting the delivery of energy across the ERCOT Transmission Grid.  Any conflicts that cannot be satisfactorily resolved may be brought to ERCOT by any of the affected Entities for investigation and resolution.

6.5.4	Inadvertent Energy Account

ERCOT shall track any differences between the net of deemed meter readings at each BtB Tie and the actual metered value at that BtB Tie in an “Inadvertent Energy Account” between ERCOT and each interconnected non-ERCOT Control Area.  ERCOT shall coordinate operation of each BtB Tie with the BtB Tie Operator such that the Inadvertent Energy Account is maintained as close to zero as possible.  Corrections of inadvertent energy between ERCOT and the other NERC-interconnected non-ERCOT Control Areas must comply with the NERC scheduling protocols and the ERCOT Operating Guides. ERCOT shall establish procedures to correct Inadvertent Energy Accounts with non-ERCOT Control Areas that are not subject to NERC scheduling protocols.

6.5.5	QSE Activities

QSE activities during Real-Time operations are summarized in the table located in Section 6.3.2, Activities for Real-Time Operations. That table is intended to be only a general guide and not controlling language, and any conflict between the table and another section of the Protocols is controlled by the other section.

6.5.5.1	Changes in Resource Status

(1)	Each QSE shall notify ERCOT of a change in Resource Status via telemetry and through changes in the COP as soon as practicable following the change.

(2)	Each QSE shall promptly inform ERCOT when the operating mode of its Generation Resource’s Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) is changed while the Resource is On-Line.  The QSE shall also provide the Resource’s AVR or PSS status logs to ERCOT upon request.

(3)	Each QSE shall immediately report to ERCOT and the TSP any inability of the QSE’s Generation Resource required to meet its reactive capability requirements in these Protocols.

6.5.5.2	Operational Data Requirements

(1)	ERCOT shall use Operating Period data to monitor and control the reliability of the ERCOT Transmission Grid and shall use it in network analysis software to predict the short-term reliability of the ERCOT Transmission Grid.  Each TSP, at its own expense, may obtain that Operating Period data from ERCOT or directly from QSEs.

(2)	A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Generation Resource.  ERCOT shall make that data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to requesting TSPs and DSPs operating within ERCOT. Such data must be provided to the requesting TSP or DSP at the requesting TSP’s or DSP’s expense, including:

(a)	Net real power (in MW);

(b)	Net Reactive Power (in Mvar);

(c)	Power to standby transformers serving Plant auxiliary Load;

(d)	Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid;

(e)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(f)	Generation Resource breaker and switch status;

(g)	High Sustained Limit;

(h)	High Emergency Limit, under Section 6.5.9.2, Failure of the SCED Process;

(i)	Low Emergency Limit, under Section 6.5.9.2, Failure of the SCED Process;

(j)	Low Sustained Limit;

(k)	Ancillary Service Schedule for each quantity of Reg-Up, Reg-Down, Responsive Reserve and Non-Spin; and

(l)	Reg-Up, Reg-Down and Responsive Reserve Services participation factors that represent how a QSE is deploying the Ancillary Service energy on a percentage basis to specific qualified Resource.

(3)	For each wind-powered Generation Resource the QSE shall set the HSL to the output capability of the facility based upon all available units and the current measured wind speed (HSL must be equal to or greater than the latest telemetered net real power of the wind-powered Generation Resource).

(4)	A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP or DSP expense. The Net real power consumption, LPC and MPC shall be telemetered to ERCOT using a negative (-) sign convention:

(a)	Net real power consumption (in MW);

(b)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(c)	Load Resource breaker status;

(d)	Low Power Consumption (LPC);

(e)	Maximum Power Consumption (MPC)

(f)	Ancillary Service Schedule for each quantity of Reg-Up, Reg-Down, Responsive Reserve and Non-Spin; and

(g)	If the Load Resource is used as a Responsive Reserve Resource, the status of the high-set under-frequency relay.

(5)	A QSE with Resources used in SCED shall provide communications equipment to receive ERCOT-telemetered control deployments.

(6)	A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-Down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE.

(7)	Real-Time data for reliability purposes must be accurate to within three percent.  This telemetry may be provided from relaying accuracy instrumentation transformers.

(8)	Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT.

(a)	Each configuration for a power block of combined-cycle Resources is considered as a single Resource unless multiple generators are connected to the ERCOT Transmission Grid at different voltage levels.

(b)	Each QSE shall use continuous telemetry to report changes to Combined-Cycle Configurations.  Changes must be reported by changing the Resource Status in Real-Time and in COP for that Resource representing the desired Combined-Cycle Configuration.  Each QSE shall provide ERCOT with the elements comprising each Combined-Cycle Configurations for a Resource through the Registration system, through Real-Time telemetry, and by appropriate entries in the COP.

(c)	Each QSE shall provide individual telemetered generator output (MW and Mvar) and Resource Status that indicates the Combined-Cycle Configuration to be used in SCED and RUC.

(9)	A QSE representing combined-cycle Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits and price points.  Power augmentation methods must be made available to ERCOT as part of one or more of the configurations.  Price points for the range of the curve represented by the power augmentation method must reflect the price of the added capability.  Such power augmentation methods may include:

(a)	Combustion turbine inlet air cooling (CTIAC) methods;

(b)	Duct firing;

(c)	Other ways of temporarily increasing the output of combined-cycle Resources; and

(d)	For QFs, an LSL that represents the minimum energy available, in MW, from the Resource for economic dispatch based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.

6.5.6	TSP and DSP Responsibilities

(1)	Each TSP shall notify ERCOT of any changes in status of Transmission Elements as provided in these Protocols and clarified in the ERCOT procedures.

(2)	Each TSP shall as soon as practicable report to ERCOT any short-term inability to meet minimum TSP reactive requirements.

(3)	Each DSP shall as soon as practicable report to ERCOT any short-term inability to meet minimum DSP reactive requirements.

6.5.7	Energy Dispatch Methodology

This Section outlines the programmatic and manual processes employed by ERCOT to simultaneously achieve power balance (minimizing the use of Regulation Service) and manage congestion while operating within the constraints of the system at economically optimized cost.  The Real-Time Sequence describes the key system components and inputs that are required to support the SCED process, which produces the LMPs and Base Points while meeting transmission system constraints.  Section 6.5.7.3, Security Constrained Economic Dispatch, provides further details regarding additional components and inputs and ex-ante mitigation.

6.5.7.1	Real-Time Sequence

(1)	The Real-Time Sequence consists of multiple interdependent processes that are driven by telemetry data and the network topology.  This section describes the core aspects of the Real-Time Sequence.

(2)	The figure below highlights the key computational modules and processes that are used during the Real-Time Sequence:

6.5.7.1.1	SCADA Telemetry

Supervisory Control and Data Acquisition (SCADA) telemetry provides the actual Real-Time status and output of Resources and the status of observable Transmission Elements of the Network Operations Model.

6.5.7.1.2	Network Topology Builder

The Network Topology Builder creates the Updated Network Model based on the observed topology of the ERCOT Transmission Grid.  The Updated Network Model is then used as the basis for the State Estimator solution.

6.5.7.1.3	Bus Load Forecast

Once the Updated Network Model is created, the transmission Electrical Buses in the model will have a Bus Load Forecast applied.  The forecasted Load must be denoted with a low State Estimator measurement confidence factor.  The State Estimator must use the forecasted Load coupled with the remaining telemetry of line flows and voltages to estimate the actual Load on each Electrical Bus.

6.5.7.1.4	State Estimator

The State Estimator must use the Bus Load Forecast and the remaining telemetry information of line flows and voltages to estimate all the transmission parameters needed to provide, on convergence, a mathematically consistent data set of constrained inputs to the Network Security Analysis (NSA) and the Topology Consistency Analyzer.

6.5.7.1.5	Topology Consistency Analyzer

The Topology Consistency Analyzer identifies possibly erroneous breaker and switch status. The Topology Consistency Analyzer must notify ERCOT of inconsistencies detected and must indicate the correct breaker and switch status(es) when the preponderance of redundant information from the telemetered database indicates true errors in status.  For example, such processing would detect flow on lines, flow on devices or network load, shown as disconnected from the transmission system and would indicate to ERCOT that there was a continuity error associated with the flow measurement or status indication.  ERCOT may override SCADA telemetry as required to correct erroneous breaker and switch status before that information is processed by the Network Security Analysis for the next SCED interval.  ERCOT shall notify the TSP or QSE, who shall correct the status indications as soon as practicable.  The Topology Consistency Analyzer maintains a summary of all incorrect status indicators and provides that information to all TSPs and other Market Participants through the MIS Secure Area.

6.5.7.1.6	Breakers/Switch Status Alarm Processor and Forced Outage Detection Processor

The Real-Time Sequence includes processes that detect and provide alarms to the ERCOT operator when the status of breakers and switches, Resources, transmission lines and transformers, and Load disconnected from the Updated Network Model changes. Also, the ERCOT operator must be able to determine if an Outage of Transmission Facilities had been scheduled in the Outage Scheduler or is a Forced Outage.

6.5.7.1.7	Real-Time Weather and Dynamic Rating Processor

(1)	The Dynamic Rating Processor provides Dynamic Ratings using the processes described in Section 3.10.8, Dynamic Ratings, for all transmission lines and transformer elements with Dynamic Ratings designated by the TSPs.  ERCOT shall obtain Real-Time weather data, where available, from multiple locations and provide it to the Dynamic Rating Processor.  Weather conditions must include ambient temperature and may include wind speed when available. ERCOT shall post summaries of dynamically adjusted Transmission Element limits on the MIS Secure Area in a form that allows Market Participants to directly upload Real-Time data into the Common Information Model.

(2)	On a monthly basis, ERCOT shall provide a summary report for each dynamically rated Transmission Element specifying the average change in Normal Rating in MVA that is gained on the element through use of a Dynamic Rating rather than the Normal Rating.  ERCOT shall post this report to the MIS Secure Area.

6.5.7.1.8	Overload Alarm Processor

Once transmission line and transformer Dynamic Ratings are retrieved, ERCOT shall compare the actual flow and state estimated flow calculation of MVA to the effective Transmission Element limit and, if an out-of-limit condition exists, ERCOT shall produce an overload notification.

6.5.7.1.9	Contingency List and Contingency Screening

For the Real-Time Sequence, ERCOT may select relevant contingencies from a standard contingency list previously developed by ERCOT under Section 5.5.1, Security Sequence, that are likely to be active in Real-Time.  ERCOT may use the information provided by the Hour-Ahead or Day-Ahead Network Security Analysis to assist in determining which contingencies are candidates for activation.

6.5.7.1.10	Network Security Analysis Processor and Security Violation Alarm

(1)	Using the input provided by the State Estimator, ERCOT shall use the Network Security Analysis (NSA) processor to perform analysis of all contingencies remaining in the active list.  For each contingency, ERCOT shall use the NSA processor to monitor the elements for limit violations.  ERCOT shall use the NSA processor to verify Electrical Bus voltage limits to be within a percentage tolerance as outlined in the ERCOT Operating Guides. Contingency security violations for transmission lines and transformers occur if:

(a)	The predicted post-contingency MVA exceeds 100% of the Emergency Rating after adjustments for Real-Time weather conditions applicable to the contingency are incorporated; and

(b)	A Remedial Action Plan (RAP) or Special Protection System (SPS) is not defined allowing relief within the time allowed by the security criteria.

(2)	When the NSA processor notifies ERCOT of a security violation, ERCOT shall immediately initiate the process described in Section 6.5.7.1.11, Transmission Constraint Management.

(3)	If the SCED does not resolve an insecure state, ERCOT shall attempt to relieve the insecure state by:

(a)	Confirming that pre-determined relevant Remedial Action Plans (RAPS) are properly modeled in the system;

(b)	Re-dispatching generation through the mechanism of over-riding HDLs and LDLs to provide more capacity to SCED;

(c)	After declaring an Alert, as appropriate, manual Dispatch of generation;

(d)	Removing non-cascading contingency overload/constraints from the SCED process; and

(e)	If all other mechanisms have failed, ERCOT may authorize the use of a Mitigation Action Plan (MAP) previously reviewed by the appropriate TSP or DSP.  A MAP is a set of pre-defined actions taken beyond normal RAPs under emergency circumstances to relieve transmission security violations.

(3)	NSA must be capable of analyzing contingencies, including the effects of automatically deployed SPSs and RAPs.  The NSA must fully integrate into the evaluation and deployment of these SPSs and RAPs and notify the ERCOT operator of the application of these SPSs and RAPs to the solution.

(4)	The Real-Time NSA may employ the use of appropriate ranking and other screening techniques to further reduce computation time by executing one or two iterations of the contingency study to gauge its impact and discard further study if the estimated result is inconsequential.

6.5.7.1.11	Transmission Constraint Management

(1)	ERCOT may not allow any contingency anticipated to be active in SCED, identified by NSA, until it has verified that the contingency is accurate and appropriate given the current operating state of the ERCOT Transmission Grid.  ERCOT shall continuously post to the MIS Secure Area any active contingencies in SCED and any contingencies that it has determined to be inaccurate or inappropriate and thus excluded from SCED under Section 5.5.1, Security Sequence.  The ERCOT System Operator will flag for further review by ERCOT any contingencies deemed inaccurate or inappropriate.

(2)	ERCOT shall establish a maximum Shadow Price for each constraint as part of the definition of contingencies.  The cost calculated by SCED to resolve an additional MW of congestion on the constraint is limited to the maximum Shadow Price for the constraint.  ERCOT shall develop a policy for setting maximum Shadow Prices for approval through the PRR process.

6.5.7.1.12	Resource Limits

(1)	The following Generation Resource limits are calculated by ERCOT and used as inputs by the SCED process:

(a)	High Ancillary Service Limit (HASL);

(b)	Low Ancillary Service Limit (LASL);

(c)	Normal Ramp Rate by using the curve submitted by the QSE and the Resource’s MW telemetry;

(d)	Emergency Ramp Rate by using the curve submitted by the QSE and the Resource’s MW telemetry;

(e)	SCED Up Ramp Rate (SURAMP), which represents the ability of a Generation Resource to increase generation output in SCED.

(f)	SCED Down Ramp Rate (SDRAMP), which represents the ability of a Generation Resource to decrease generation output in SCED.

(g)	High Dispatch Limit (HDL), which represents a dynamically calculated MW upper limit on a Resource that describes the maximum capability of the Resource SCED dispatch for the next five minutes (the Resource’s Real-Time generation plus the product of the Normal Ramp Rate at that Real-Time output level multiplied by five), restricted by HASL;

(h)	Low Dispatch Limit (LDL), which represents a dynamically calculated MW lower limit on a Resource that describes the minimum capability of the Resource SCED dispatch for the next five minutes (the Resource’s Real-Time generation minus the product of the Normal Ramp Rate at that Real-Time output level multiplied by five), restricted by LASL.

(2)	The following Load Resource limits are calculated by ERCOT and used in other calculations and as information for ERCOT operators:

(a)	High Ancillary Service Limit (HASL); and

(b)	Low Ancillary Service Limit (LASL).

(3)	For a more detailed explanation of all the Resource limits calculated by ERCOT, please reference Section 6.5.7.2, Resource Limit Calculator.

6.5.7.1.13	Data Inputs and Outputs for the Real-Time Sequence and SCED

(1)	Inputs: The following information must be provided as inputs to the Real-Time Sequence and SCED.  ERCOT may require additional information as required, including:

(a)	Real-Time data from TSPs including status indication for each point if that data element is stale for more than 20 seconds;

(i)	Transmission Electrical Bus voltages;

(ii)	MW and Mvar pairs and calculated MVA for all lines and transformers and reactors;

(iii)	Actual breaker and switch status for all modeled devices;

(iv)	Telemetered breaker and switch status changes that occurred since the prior telemetry scan for all modeled devices; and {{TPTF revisit-ERCOT action item}}

(v)	Tap position for auto-transformers.

(b)	State Estimator results (MW and Mvar pairs and calculated MVA )for all modeled Transmission Elements;

(c)	Logic equations to determine the in- or out-of-service state of a transmission line or transformer;

(d)	Transmission Element ratings from TSPs;

(i)	Data from the Common Information Model:

(A)	Transmission lines – Normal and Emergency Ratings (MVA); and

(B)	Transformers and Auto-transformers – Normal and Emergency Ratings (MVA) and tap position limits.

(ii)	Data from QSEs:

(A)	Generator Step-up transformers tap position;

(B)	Resource High Sustained Limit (from telemetry); and

(C)	Resource Low Sustained Limit (from telemetry).

(e)	Real-Time weather, from WGRs, and where available from TSPs or other sources.  ERCOT may elect to obtain other sources of weather data and may utilize such information to calculate the dynamic limit of any Transmission Element.

(2)	ERCOT shall validate the inputs of the Resource Limit Calculator as follows:

(a)	The calculated SCED Up Ramp Rate and SCED Down Ramp Rate are each greater than or equal to zero; and

(b)	Other provision specified under Section 3.18, Resource Limits in Providing Ancillary Service.

(3)	Outputs for ERCOT operator information and possible action include:

(a)	Operator notification of any change in status of any breaker or switch;

(b)	Lists of all breakers and switches not in their normal position;

(c)	Result of logic equation calculation of the in and out status of transmission lines and transformers;

(d)	Operator notification of all Transmission Element overloads detected from telemetered or State-Estimated data;

(e)	Operator notification of all Transmission Element security violations; and

(f)	Operator summary displays

(i)	Transmission system status changes;

(ii)	Overloads;

(iii) 	System security violations; and

(iv)	Base Points.

(4)	Every hour, ERCOT shall post on the MIS Secure Area the following information:

(a)	Status of all breakers and switches used in the Network Security Analysis except breakers and switches connecting Resources to the ERCOT Transmission Grid;

(b)	Transmission flows and voltages from the State Estimator;

(c)	Individual transmission Load on Electrical Buses, sum of the Load on each Electrical Bus in each Load Zone, and total Load on Electrical Buses in the ERCOT System, the sum of ERCOT generation, and flow on the BtB Ties, all from the State Estimator;

(d)	Transformer flows, voltages and tap position from the State Estimator;

(e)	All voltage schedules;

(f)  	All binding transmission constraints and the contingency or overloaded element pairs that caused such constraint;

(g)	All Shadow Prices on binding transmission constraints; and

(h)	The 15-minute average of Loads on the Electrical Buses from State Estimator results.

6.5.7.2	Resource Limit Calculator

(1)	ERCOT shall calculate the HASL, LASL, SCED Up Ramp Rate (SURAMP), SCED Down Ramp Rate (SDRAMP), HDL and LDL within 4 seconds after a change of the Resource-specific attributes provided as part of the QSE’s SCADA telemetry under Section 6.5.5.2, Operational Data Requirements.  The formulas described below define which Resource-specific attributes must be used to calculate each Resource limit.  The Resource limits are used as inputs into both the SCED process and the Ancillary Service Capacity Monitor as described in Section 6.5.7.6, Load Frequency Control.  These Resource limits help ensure that the deployments produced by the SCED and LFC processes will respect the commitment of a Resource to provide Ancillary Services as well as individual Resource physical limitations.

(2)	The figure below illustrates how the Resource Limit Calculator determines the Resource limits for both Generation and Load Resources:

{{modifications to diagram below: “HSL = LPC” changed to “HSL = -LPC”; “LSL = MPC” changed to “LSL = -MPC”; and “Ancillary services provided: Reg Up, Responsive” changed to “Ancillary services provided: Reg Up, Responsive, NSRS- change to Non-Spin”}}

(3)	High Ancillary Service Limit (HASL) is calculated as follows:

HASL	=	Max (LASL, (HSLTELEM – (RRSTELEM + RUSTELEM + NSRSTELEM)))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit |
| HSLTELEM | High Sustained Limit provided via telemetry – per Section 6.5.5.2 Operational Data Requirements |
| LASL | Low Ancillary Service Limit |
| RRSTELEM | Responsive Reserve designation provided by telemetry |
| RUSTELEM | Reg-Up designation provided by telemetry |
| NSRSTELEM | Non-Spin designation provided via telemetry; ERCOT shall set the NSRSTELEM to adjust for deployed Non-Spin on On-Line Generation Resources |

(4)	Low Ancillary Service Limit (LASL) is calculated as follows:

LASL	= 	LSLTELEM + RDSTELEM

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit |
| LSLTELEM | Low Sustained Limit provided via telemetry |
| RDSTELEM | Reg-Down designation provided by telemetry |

(5)	For each Generation Resource, the SURAMP is calculated as follows:

SURAMP	= 	MIN ([NORMRAMP– (RUSTELEM / 5)], [EMRRAMP – (RRSTELEM / 10)])

| Variable | Description |
| --- | --- |
| SURAMP | SCED up ramp rate |
| NORMRAMP | Normal Ramp Rate |
| EMRRAMP | Emergency Ramp Rate |
| RRSTELEM | Responsive Reserve designation provided by telemetry |
| RUSTELEM | Reg-Up designation provided by telemetry |

(6)	For each Generation Resource, the SDRAMP is calculated as follows:

SDRAMP	= 	NORMRAMP – (RDSTELEM / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED down ramp rate |
| NORMRAMP | Normal Ramp Rate |
| RDSTELEM | Reg-Down designation by Resource provided via telemetry |

(7)	For Generation Resources, HDL is calculated as follows:

HDL	= 	Min (POWERTELEM + (SURAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit |
| POWERTELEM | Gross or net real power provided via telemetry |
| SURAMP | SCED Up Ramp Rate – |
| HASL | High Ancillary Service Limit – definition provided in Section 2, Definitions and Acronyms. |

(8)	For Generation Resources, LDL is calculated as follows:

LDL	= 	Max (POWERTELEM - (SDRAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit |
| POWERTELEM | Gross or net real power provided via telemetry |
| SDRAMP | SCED Down Ramp Rate – |
| LASL | Low Ancillary Service Limit – definition provided in Section 2, Definitions and Acronyms. |

6.5.7.3	Security Constrained Economic Dispatch

(1)	The Security Constrained Economic Dispatch (SCED) process is designed to simultaneously manage energy balance and congestion through Resource Base Points and calculation of LMPs every five minutes.  The SCED process uses a two-step methodology that applies mitigation prospectively to resolve Non-Competitive Constraints for the current Operating Hour.  The SCED process evaluates Energy Offer Curves and Output Schedules to produce a least cost dispatch of On-Line Generation Resources to the total current generation output level, subject to transmission constraints.  The SCED process uses the Resource Status provided by SCADA Telemetry under Section 6.5.5.2, Operational Data Requirements, and validated by the Real-Time Sequence, instead of the Resource Status provided by the Current Operating Plan.

(2)	The SCED solution must monitor cumulative deployment of Regulation Services and ensure that Regulation Services deployment is minimized over time.

(3)	For use as SCED inputs, ERCOT shall use the available capacity of all committed Generation Resources by creating proxy Energy Offer Curves for certain Resources as follows:

(a)	Non-wind-powered Generation and Dynamically Scheduled Resources without Energy Offer Curves.

ERCOT shall create a monotonically increasing proxy Energy Offer Curve as described below for:

(i)	Each non-wind-powered Generation Resource for which its QSE has submitted an Output Schedule instead of an Energy Offer Curve; and

(ii)	Each Dynamically Scheduled Resource that has not submitted Incremental and Decremental Energy Offer Curves.

| MW | Price (per MWh) |
| --- | --- |
| HSL | $1,000.00 |
| Output Schedule MW plus 1 MW | $999.99 |
| Output Schedule MW | -$249.99 |
| LSL | -$250.00 |

(b)	Dynamically Scheduled Resources with Energy Offer Curves

For each Dynamically Scheduled Resource that has submitted Incremental and Decremental Energy Offer Curves, ERCOT shall create a monotonically increasing proxy Energy Offer Curve. That curve must consist of the Incremental Energy Offer Curve that reflects the available capacity above the Resource’s Output Schedule to its HSL and the Decremental Energy Offer Curve that reflects the available capacity below the Resource’s Output Schedule to the LSL. The curve must be created as described below:

| MW | Price (per MWh) |
| --- | --- |
| Output Schedule MW plus 1 MW to HSL | Incremental Energy Offer Curve |
| LSL to Output Schedule MW | Decremental Energy Offer Curve |

(c)	Non-wind-powered Generation Resources without full-range Energy Offer Curves

For each non-wind-powered Generation Resource for which its QSE has submitted an Energy Offer Curve that does not cover the full range of the Resource’s available capacity, ERCOT shall create a proxy Energy Offer Curve that extends the submitted Energy Offer Curve to use the entire available capacity of the Resource using the system-wide offer cap above the highest point on the Energy Offer Curve to the Resource’s HSL and the offer floor from the lowest point on the Energy Offer Curve to its LSL, using these points:

| MW | Price (per MWh) |
| --- | --- |
| HSL (if more than highest MW in Energy Offer Curve) | $1,000.00 |
| 1 MW above highest MW in Energy Offer Curve (if less than HSL) | $999.99 |
| Energy Offer Curve | Energy Offer Curve |
| 1 MW below lowest MW in Energy Offer Curve (if more than LSL) | -$249.99 |
| LSL (if less than lowest MW in Energy Offer Curve) | -$250.00 |

(d)	Wind-powered Generation Resource

(i)	For each wind-powered Resource that has not submitted an Energy Offer Curve ERCOT shall create a monotonically increasing proxy Energy Offer Curve as described below:

| MW | Price (per MWh) |
| --- | --- |
| HSL | $1,000.00 |
| HSL minus 1 MW | -$249.99 |
| LSL | -$250.00 |

(ii)	For each wind-powered Resource for which its QSE has submitted an Energy Offer Curve, ERCOT shall create a monotonically increasing proxy Energy Offer Curve as described below:

| MW | Price (per MWh) |
| --- | --- |
| HSL (if more than highest MW in Energy Offer Curve) | $1,000.00 |
| 1 MW above highest MW in Energy Offer Curve (if less than HSL) | $999.99 |
| Energy Offer Curve | Energy Offer Curve |
| 1 MW below lowest MW in Energy Offer Curve (if more than LSL) | -$249.99 |
| LSL (if less than lowest MW in Energy Offer Curve) | -$250.00 |

(4)	The creation of a proxy Energy Offer Curve by ERCOT under this section  does not constitute the submission of an offer by a QSE for purposes of paragraph (2) of Section 1.3.3, Expiration of Confidentiality.

(5)	The two-step SCED methodology referenced in paragraph (1) above is:

(a)	The first step is to execute the SCED process to determine Reference LMPs.  In this step ERCOT executes SCED using the full Network Operations Model while only observing limits of Competitive Constraints.  Energy Offer Curves for all On-Line Generation Resources, whether submitted by QSEs or created by ERCOT under this section  are used in the SCED to determine “Reference LMPs.”

(b)	The second step is to execute the SCED process to produce Base Points, Shadow Prices, and LMPs, subject to security constraints (including Competitive and Non-Competitive Constraints) and other Resource constraints. The second step must:

(i)	Use Energy Offer Curves for all On-Line Generation Resources, whether submitted by QSEs or created by ERCOT.  Each Energy Offer Curve must be capped at the greater of the Reference LMP (from Step 1) at the Resource Node or the appropriate Mitigated Offer Cap  and bounded at the lesser of the Reference LMP (from Step 1) at the Resource Node or the appropriate Mitigated Offer Floor; and

(ii)	Observe all Competitive and Non-Competitive Constraints.

(c)	ERCOT shall archive information and provide monthly summaries of security violations and any binding transmission constraints identified in Step 2 of the SCED process.  The summary must describe the Limiting Element (or identified operator-entered constraint with operator’s comments describing the reason and the Resource-specific impacts for any manual overrides).  ERCOT shall provide the summary to Market Participants on the MIS Secure Area and to the WEMM.

(6)	ERCOT shall create a linear Energy Offer Curve for a pseudo-Resource with an HSL of 100 MW, LSL of 0 MW, Normal Ramp Rate of 100 MW per minute and no Ancillary Service Schedule.  The linear Energy Offer Curve must consist of the following points:

| MW | Price (per MWh) |
| --- | --- |
| 0 MW | Greater of $300.00 or 30% of the system-wide offer cap |
| 100 MW | Greater of $1,000.00 or 100% of the system-wide offer cap |

(a)	The Energy Offer Curve for the pseudo-Resource is not mitigated in Step 2 of the SCED.

(b)	The pseudo-Resource is modeled in SCED as an aggregation of capacity from those Generation Resources providing Responsive Reserve Service in proportion to the amount of Responsive Reserve Service responsibility of each of those Generation Resources.

(c)	If SCED procures energy from the pseudo-Resource, then the energy procured from the pseudo-Resource is used as the basis for increasing Resource Base Points for those Generation Resources providing Responsive Reserve Service weighted by the amount of Responsive Reserve Service responsibility of each of those Generation Resources. Such deployments may exceed the Resource’s HDL and HASL.

(d)	The Base Point Dispatch Instruction must contain a status indication providing notice to the QSE of the Resource’s dispatch above its HASL, if applicable.

(e)	ERCOT shall notify all Market Participants on the MIS Secure Area of any Dispatch of the pseudo-Resource.

6.5.7.4	Base Points

ERCOT shall issue a Base Point for each On-Line Generation Resource on completion of each SCED execution.  The Base Point set by SCED must observe a Generation Resource’s HDL and LDL.  Base Points are automatically superseded on receipt of a new Base Point from ERCOT regardless of the status of any current ramping activity of a Resource. ERCOT shall provide each Base Point using Dispatch Instructions issued over SCADA or Inter-Control Center Protocol (ICCP) data link to the QSE representing each Resource that include the following information:

(a)	Resource identifier that is the subject of the Dispatch Instruction;

(b)	MW output;

(c)	Status indicator providing notice of Responsive Reserve Deployment requesting dispatch above the Resource’s HASL;

(d)	Time of the Dispatch Instruction; and

(e)	Other information relevant to that Dispatch Instruction.

6.5.7.5	Ancillary Services Capacity Monitor

(1)	ERCOT shall calculate the following every 10 seconds and provide Real-Time summaries to ERCOT operators and all Market Participants using the MIS Secure Area and ICCP, giving updates of calculations every 10 seconds, which show the Real-Time total system amount of:

(a)	Responsive Reserve Capacity from Generation Resources;

(b)	Responsive Reserve Capacity from Load Resources;

(c)	Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves;

(d)	Non-Spinning Reserve available from undeployed Load Resources;

(e)	Non-Spinning Reserve available from Off-Line Generation Resources;

(f)	Non-Spinning Reserve available from Resources with Output Schedules;

(g)	Undeployed Reg-Up and undeployed Reg-Down;

(h)	Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED;

(i)	Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED;

(j)	Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED; and

(k)	Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED.

(2)	Each QSE shall operate Resources providing Ancillary Service capacity to meet its obligations. If a QSE experiences temporary conditions where its total obligation for providing Ancillary Service can not be met on the QSE's Resources, then the QSE may add additional capability from other Resources that it represents.  It adds that capability by changing the Resource Status and updating the Ancillary Service Schedules of the affected Resources and notifying ERCOT under Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.  If the QSE is unable to meet its total obligations to provide committed Ancillary Services capacity, the QSE shall notify ERCOT immediately of the expected duration of the QSE’s inability to meet its obligations.  ERCOT shall determine whether replacement Ancillary Services will be procured on behalf of the affected QSE according to Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.

6.5.7.6 	Load Frequency Control

The function of Load Frequency Control (LFC) is to maintain system frequency without a cost optimization function.  ERCOT shall execute LFC every four seconds to reduce system frequency deviations from scheduled frequency by providing a control signal to each QSE that represents Resources providing Regulation Service and Responsive Reserve Service.

6.5.7.6.1	LFC Process Description

(1)	The LFC system corrects system frequency based on the Area Control Error (ACE) algorithm and Good Utility Practice.

(2)	The ACE algorithm subtracts the actual frequency in Hz from the scheduled system frequency (normally 60Hz), and multiplies the result by the frequency bias constant of MW/0.1 Hz.  The ACE algorithm then takes that product and subtracts the difference between the Real-Time output and the Base Point for all Dynamically Scheduled Resources.  This calculation produces an ACE value, which is a MW-equivalent correction needed to control the actual system frequency to the scheduled system frequency value.  ERCOT shall develop a methodology, subject to TAC approval, to determine the optimal frequency bias for given system conditions.

(3)	The LFC module receives inputs from Real-Time telemetry that includes Resource output and actual system frequency.  The LFC uses actual Resource information calculated from SCADA to determine available Resource capacity providing Regulation and Responsive Reserve Services.

(4)	Based on the ACE MW correction, the LFC issues a set of control signals every four seconds to each QSE providing Regulation and, if required, each QSE providing Responsive Reserve.  Control must be proportional to the QSE’s share of each of the services that it is providing, respecting the QSE’s Resources’ capability to provide regulation control in each four-second interval. Control signals are provided to the QSE using the ICCP data link or SCADA.

(5)	Each QSE shall allocate its Regulation energy deployment among its Resources to meet a deployment signal, and shall provide ERCOT with the participation factor of each Resource via telemetry in accordance with Section 6.5.7.6.2.1, Deployment of Regulation Service, and Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.  Each QSE’s allocation of Regulation Service to its Resources must be consistent with the telemetry provided under Section 6.5.5.2, Operational Data Requirements.

(6)	If all Reg-Up capacity has been deployed, ERCOT shall use the LFC system to deploy Responsive Reserve on Generation Resources.  Such Responsive Reserve deployments by ERCOT must be deployed as specified in Section 6.5.7.6.2.2, Deployment of Responsive Reserve Service.

(7)	ERCOT shall settle energy that results from LFC deployment at the Settlement Point Price for the point of injection. When a QSE deploys Responsive Reserve Service, the QSE shall deploy units consistent with the performance criteria for Responsive Reserve Service in Sections 8.1.2.3.2, Responsive Reserve Service Capacity Monitoring Criteria and 8.1.2.4.2, Responsive Reserve Service Energy Deployment Criteria.

(8)	The inputs for Load Frequency Control include:

(a)	Actual system frequency;

(b)	Scheduled system frequency;

(c)	Capacity available for Regulation by QSE;

(d)	Telemetered high and low regulation availability status indications for each Resource available for Regulation deployments for ERCOT information;

(e)	Resource limits calculated by ERCOT as described Section 6.5.7.2, Resource Limit Calculator;

(f)	Generation Resource Regulation participation factor;

(g)	Capacity available for Responsive Reserve by QSE;

(h)	Generation Resource Responsive Reserve participation factor;

(i)	ERCOT System frequency bias;

(j)	Dynamically Scheduled Resource Base Points; and

(k)	Telemetered Resource output.

(9)	If system frequency deviation is greater than an established threshold, ERCOT may issue Dispatch Instructions to those Resources not providing Reg-Up or Reg-Down that have Base Points directionally opposite ACE, to temporarily suspend ramping to their Base Point until frequency deviation returns to zero.

6.5.7.6.2	LFC Deployment

ERCOT may deploy Regulation, Responsive Reserve, and Non-Spin only as prescribed by their respective specific functions to maintain frequency and system security.  ERCOT may not substitute one Ancillary Service for another.

6.5.7.6.2.1	Deployment of Regulation Service

(1)	ERCOT shall deploy Reg-Up and Reg-Down necessary to maintain ERCOT System frequency to meet NERC Control Area and other Control Area performance criteria as specified in these Protocols and the Operating Guides.

(2)	Reg-Up is a deployment or recall of a deployment referenced to the Resource’s Base Point in response to a change (up or down) in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

(3)	Reg-Down is a deployment or recall of a deployment referenced to the Resource’s Base Point in response to a change (up or down) in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

(4)	These requirements also apply to the deployment or recall of a deployment of Reg-Up and Reg-Down:

(a)	Deployment or recall of a deployment must be accomplished through use of an automatic signal from ERCOT to each QSE provider of Reg-Up and Reg-Down.

(b)	ERCOT shall minimize Reg-Up and Reg-Down energy as much as practicable in each SCED cycle.

(c)	ERCOT shall settle energy provided by Reg-Up and Reg-Down at the Resource’s Settlement Point Price.

(d)	ERCOT shall integrate the control signal sent to providers of Reg-Up and shall calculate the amount of energy deployed by Reg-Up in each Settlement Interval.

(e)	ERCOT shall integrate the control signal sent to providers of Reg-Down and shall calculate the amount of energy deployed by Reg-Down in each Settlement Interval.

(f)	ERCOT shall calculate for each LFC cycle the amount of regulation that each Resource is expected to provide at that instant in time.  The expected amount must be averaged over each SCED interval.  The actual generation from telemetry must also be averaged over each SCED interval.

(5)	Every day, ERCOT shall post to the MIS Secure Area the total amount of deployed Reg-Up and Reg-Down energy in each Settlement Interval of the previous day.

(6)	For each Resource providing Reg-Up or Reg-Down, the implied ramp rate in MW per minute is the total amount of Regulation Service awarded divided by five.

(7)	Each QSE providing Reg-Up or Reg-Down and ERCOT shall meet the deployment performance requirements specified in Section 8, Performance Monitoring and Compliance.

(8)	ERCOT shall issue Reg-Up and Reg-Down deployment Dispatch Instructions over SCADA or ICCP.  Those Dispatch Instructions must contain the change in MW output requested of the QSE assuming all Resources are at their last Base Point issued by SCED.

6.5.7.6.2.2	Deployment of Responsive Reserve Service

(1)	Responsive Reserve is intended to:

(a)	Help restore the frequency within the first few seconds of a significant frequency deviation of the interconnected transmission system;

(b)	Provide energy during the implementation of an Emergency Electric Curtailment Plan (EECP); and

(c)	Provide backup Reg-Up.

(2)	ERCOT shall deploy energy from Responsive Reserve Service (RRS) to meet NERC Control Area performance standards and other Control Area performance criteria as specified in these Protocols and the Operating Guides, by one or more of the following:

(a)	Automatic generator governor  action as a result of a significant frequency deviation;

(b)	Through use of an automatic Dispatch Instruction signal to deploy Responsive Reserve Energy from Generation Resources;

(c)	By Dispatch Instructions for deployment of Responsive Reserve Energy from a Load Resource by an electronic Messaging System; and

(d)	Automatic action of high-set under-frequency relays as a result of a significant frequency deviation.

(3)	ERCOT shall deploy Responsive Reserve to respond to a frequency deviation when the power requirement to restore frequency to normal (ACE) in 10 minutes exceeds the Reg-Up ramping capability.  Deployment of Responsive Reserve on Load Resources must be as described in Section 6.5.9.4, Emergency Electric Curtailment Plan.

(4)	ERCOT may deploy Responsive Reserve in response to NERC Disturbance Control Assistance requirements as specified in the Operating Guides if no additional energy is available to be dispatched from SCED as determined by the Ancillary Services Capacity Monitor.

(5)	Energy from Responsive Reserve Resources may also be deployed by ERCOT under Section 6.5.9, Emergency Operations.

(6)	ERCOT shall allocate the deployment of Responsive Reserve proportionally among QSEs that provide Responsive Reserve using Resources that are not on high-set under frequency relays.  If ERCOT has deployed 500 MW of Responsive Reserve, and additional Responsive Reserve is needed, ERCOT shall declare that an EECP is in effect and shall follow provisions in Section 6.5.9, Emergency Operations.

(7)	ERCOT shall use the SCED and Non-Spin as soon as practicable to minimize the prolonged use of Responsive Reserve Energy.

(8)	Once Responsive Reserve is deployed, the QSE’s obligation to deliver energy remains in effect until specifically instructed by ERCOT to stop providing energy from Responsive Reserve.  However, except in an Emergency Condition, the QSE’s obligation to deliver Responsive Reserve may not exceed the period for which the service was committed.

(9)	Following the deployment or recall of a deployment by Dispatch Instruction of Responsive Reserve, ERCOT shall adjust the HASL and LASL based on the QSE’s telemetered Responsive Reserve participation factors to account for such deployment.

(10)	QSEs providing Responsive Reserve and ERCOT shall meet the deployment performance requirements specified in Section 8, Performance Monitoring and Compliance.

(11)	ERCOT shall issue Responsive Reserve deployment Dispatch Instructions over SCADA or ICCP for Generation Resources and XML for Load Resources.  Those Dispatch Instructions must contain the MW output requested.

(12) 	To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource.

(13)	The amount of RRS that a QSE can self-arrange using a Load Resource is limited to the percentage amount of total RRS that the Load Resource can provide as specified by ERCOT.  However, a QSE may offer additional Load Resources into the ERCOT RRS Ancillary Service market.

6.5.7.6.2.3	Non-Spinning Reserve Service Deployment

(1)	ERCOT shall deploy Non-Spinning Reserve Service using SCED for On-Line Generation Resources with Energy Offer Curves and by Operator Dispatch Instruction for Resources with Output Schedules, Off-Line Generation Resources and Load Resources.  ERCOT shall develop a procedure approved by TAC to deploy Resources providing Non-Spinning Reserve Service.  ERCOT operators shall implement the deployment procedure when a specified threshold(s) in MW of capability available to SCED to increase generation is reached. ERCOT Operators may implement the deployment procedure to recover deployed Responsive Reserve or when other Emergency Conditions exist.

(2)	Once Generation Resources providing Non-Spin are deployed and On-Line, ERCOT shall use SCED to determine the amount of energy to be dispatched from those Resources.

(3)	Off-Line Generation Resources providing Non-Spin (OFFNS Resource Status) are required to provide an Energy Offer Curve for use by SCED.

(4)	On receipt of a Dispatch Instruction, Off-Line Generation Resources and Load Resource providing Non-Spin must, at a minimum, provide the requested deployment energy within 30 minutes of the Dispatch Instruction.

(5)	Once the On-Line Non-Spin Resource has been deployed for energy, ERCOT will automatically calculate new HASL constraints for SCED assuming the Resource’s Non-Spin Ancillary Service Schedule is reduced to the amount of the energy deployment.  On deployment of Off-Line Non-Spin Resources, the QSE will indicate the Non-Spin Ancillary Service Schedule is reduced by the amount of the deployment.

(6)	For Dynamically Scheduled Resources (DSRs) providing Non-Spin, on deployment of Non-Spin, the DSR’s QSE shall adjust its Resource Output Schedule to reflect the amount of deployment.  For non-DSRs with Output Schedules providing Non-Spin, on deployment of Non-Spin, ERCOT shall adjust the Resource Output Schedule for the remainder of the Operating Period to reflect the amount of deployment.  ERCOT shall notify the QSEs representing the non-DSR of the adjustment through the MIS Certified Area.

(7)	For On-Line Generation Resources with Energy Offer Curves, Base Points include Non-Spin energy as well as any other energy dispatched as a result of SCED.

(8)	Each QSE providing Non-Spin from a Resource shall inform ERCOT of the Non-Spin Resource availability using the Resource Status indications for the Operating Hour using telemetry and shall use the Current Operating Plan to inform ERCOT of Non-Spin Resource Status for hours in the Adjustment Period through the end of the Operating Day.

(9)	ERCOT may deploy Non-Spin at any time in a Settlement Interval.

(10)	ERCOT’s Non-Spin Dispatch Instructions for deployment of Resources with Output Schedules, Off-Line Generation Resources and Load Resources must include:

(a)	The Resource name;

(b)	A MW level of capacity deployment for Off-Line Generation Resources, a MW level of energy for Resources with Output Schedules, and interrupted amount for Load Resources; and

(c)	The anticipated duration of deployment.

(11)	ERCOT shall, as part of its TAC-approved Non-Spin deployment procedure, provide for the recall of Non-Spin energy including descriptions of changes to Output Schedules and release of energy obligations from On-Line Resources with Output Schedules and from On-Line Resources that were previously Off-Line Resources providing Non-Spin capacity.

(12)	Non-Spin procured from a Load Resource block offer must be deployed as a block.

6.5.7.7	Voltage Support Service

(1)	ERCOT shall coordinate with TSPs the creation and maintenance of Voltage Profiles as described in Section 3.15, Voltage Support.

(2)	ERCOT, or TSPs designated by ERCOT, shall instruct QSEs having Generation Resources required to provide VSS, to make adjustments for voltage support within the Unit Reactive Limit (URL) provided by the QSE to ERCOT.  A Generation Resource providing VSS may not be requested to reduce MW output so as to provide additional reactive (Mvar), nor may they be requested to operate on a voltage schedule outside the URL specified by the QSE without a Dispatch Instruction requesting Resource-specific Dispatch.

(3)	ERCOT and TSPs shall develop operating procedures specifying Voltage Profiles of transmission-controlled reactive resources to minimize the dependence on generation-supplied reactive resources.  For Generation Resources required to provide VSS, step-up transformer tap settings must be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(4)	Each TSP, under ERCOT’s direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS dynamic reactive sources in a local area are deployed in approximate proportion to their respective installed reactive capability requirements.

(5)	Each Generation Resource required to provide VSS shall maintain the transmission voltage at the point of interconnection to the ERCOT Transmission Grid as directed by ERCOT within the operating Reactive Power capability of the Resource.

(6)	Whenever a Generation Resource is On-Line and available for energy deployment, it is required to provide VSS up to its URL.  The URL must be available for utilization at the Resource’s continuous rated active power output, and Reactive Power up to the Resource’s operating capability must be available for utilization at lower active power output levels.  In no event may the Reactive Power available be less than the required installed reactive capability multiplied by the ratio of the lower active power output to the Resource’s continuously rated active power output, and any Reactive Power available for utilization must be fully deployed to support system voltage upon request by ERCOT, or a TSP.

(7)	Each QSE providing Voltage Support Service shall meet the deployment performance requirements specified in Section 8, Performance Monitoring and Compliance.

6.5.7.8	Dispatch Procedures

(1)	ERCOT shall issue all Resource Dispatch Instructions to the QSE that represents the affected Resource.  ERCOT may not issue Dispatch Instructions to the QSE for Resources with a Resource Status of ONTEST (which indicates that it is undergoing testing), except:

(a)	For Dispatch Instructions that are a part of the testing; or

(b)	During conditions when the Resource is the only alternative for solving a transmission constraint; or

(c)	During Force Majeure Events that threaten the reliability of the ERCOT System.

(2)	Each QSE shall immediately forward any valid Dispatch Instruction to the appropriate Resource or group of Resources or identify a reason for non-compliance with the Dispatch Instruction to ERCOT in accordance with Section 6.5.7.9, Compliance with Dispatch Instructions.

(3)	If ERCOT believes that a Resource has inadequately responded to a Dispatch Instruction, ERCOT shall notify the QSE representing the Resource as soon as practicable.

(4)	The recipient of a Verbal Dispatch Instruction shall confirm the Dispatch Instruction by providing the receiving operator’s identification and by repeating the Verbal Dispatch Instruction to ERCOT orally.

(5)	The recipient of an electronic Dispatch Instruction shall acknowledge receipt of the Dispatch Instruction to ERCOT electronically, within one minute.  The electronic acknowledgement must include the receiving operator’s identification.

(6)	The recipient of any Dispatch Instruction shall immediately request clarification of the Dispatch Instruction if the recipient fails to understand its responsibility under the Dispatch Instruction.

(7)	ERCOT shall record all voice conversations that occur in the communication of Dispatch Instructions.

(8)	ERCOT shall record and file all electronic Dispatch Instructions and acknowledgements as soon as practicable after the issuance of the Dispatch Instruction.

(9)	By mutual agreement of the TSP and ERCOT, Dispatch Instructions to the TSP may be provided to the TSP’s Designated Agent.  In that case, issuance of the Dispatch Instruction to the Designated Agent is considered issuance to the TSP, and the TSP must comply with the Dispatch Instruction exactly as if it had been issued directly to the TSP, whether or not the Designated Agent accurately conveys the Dispatch Instruction to the TSP.

6.5.7.9	Compliance with Dispatch Instructions

(1)	Except as otherwise specified in this Section, each TSP and each QSE shall comply fully and promptly with a Dispatch Instruction issued to it, unless in the sole and reasonable judgment of the TSP or QSE, such compliance would create an undue threat to safety, undue risk of bodily harm or undue damage to equipment, or the Dispatch Instruction is otherwise not in compliance with these Protocols.

(2)	If the recipient of a Dispatch Instruction does not comply because in the sole and reasonable judgment of the TSP or QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment, then the TSP or QSE must immediately notify ERCOT and provide the reason for non-compliance.

(3)	If the recipient of a Dispatch Instruction recognizes that the Dispatch Instruction conflicts with other valid instructions or is invalid, the recipient shall immediately notify ERCOT of the conflict and request resolution.  ERCOT shall resolve the conflict by issuing another Dispatch Instruction.

(4)	ERCOT’s final Dispatch Instruction to a QSE in effect applies for all Protocol-related processes. If the QSE does not comply after receiving the final Dispatch Instruction, the QSE remains liable for failure to meet its obligations under the Protocols and remains liable for any charges resulting from such failure.

(5)	ERCOT’s final Dispatch Instruction to a TSP in effect applies for all Protocol-related processes.  If the TSP does not comply after receiving the final Dispatch Instruction, the TSP remains liable for such failure under these Protocols under the TSP’s Agreement with ERCOT.

(6)	In all cases in which compliance with a Dispatch Instruction is disputed, both ERCOT and the QSE or TSP shall document their communications, agreements, disagreements, and reasons for their actions, to enable resolution of the dispute through the ADR process in Section 20, Alternative Dispute Resolution Procedure.

(7)	An IRR must comply with Dispatch Instructions requiring it to reduce output 2 MW or more below the Resource’s latest HSL.

6.5.8	Verbal Dispatch Instructions

A Verbal Dispatch Instruction must contain the following information:

(a)	Identification of the responsible Entity and instructing authority (to include ERCOT Operator’s and receiving operator’s names);

(b)	Specific Resources or TSP facilities that are the subject of the Dispatch Instruction;

(c)	Specific action required;

(d)	Current operating level or state of the Resources or TSP facilities that are the subject of the Dispatch Instruction;

(e)	Operating level or state to which such Resources or facilities will be dispatched;

(f)	Time of notification of the Dispatch Instruction;

(g)	Time at which the QSE or TSP is required to initiate the Dispatch Instruction;

(h)	Time within which the QSE or TSP is required to complete the Dispatch Instruction;

(i)	Verbal Dispatch Instruction (VDI) reference number; and

(j)	Other information relevant to that Dispatch Instruction.

6.5.9	Emergency Operations

(1)	ERCOT, based on ERCOT System reliability needs, may issue a Dispatch Instruction requiring a Resource to move to a specific output level (“Emergency Base Point”).

(2)	A Qualifying Facility (QF) may only be ordered Off-Line in the case of an ERCOT-declared Emergency Condition with imminent threat to the reliability of the ERCOT System.  ERCOT may only Dispatch a QF below its LSL when ERCOT has declared an Emergency Condition and the QF is the only Resource that can provide the necessary relief.

(3)	ERCOT shall honor all Resource operating parameters in Dispatch Instructions under normal conditions and Emergency Conditions.  During Emergency Conditions, ERCOT may verbally request QSEs to operate its Resources outside normal operating parameters.  If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request.

(4)	A QSE may not self-arrange for Ancillary Services procured in response to Emergency Conditions.

6.5.9.1	Emergency and Short Supply Operation

(1)	ERCOT, as the single Control Area Operator, is responsible for maintaining reliability in normal and emergency operating conditions.  The Operating Guides are intended to ensure that minimum standards for reliability are maintained. Minimum standards for reliability are defined by the Operating Guides and the North American Electric Reliability Council (NERC) standards and include, but are not limited to:

(a)	Minimum operating reserve levels;

(b)	Criteria for determining acceptable operation of the frequency control system;

(c)	Criteria for determining and maintaining system voltages within acceptable limits;

(d)	Criteria for maximum acceptable transmission equipment loading levels; and

(e)	Criteria for determining when ERCOT is subject to unacceptable risk of widespread cascading outages.

(2)	ERCOT shall, to the fullest extent practicable, utilize the Day-Ahead process, the Adjustment Period process, and the Real-Time process before ordering Resources to specific output levels with Emergency Base Point instructions.  It is anticipated that, with effective and timely communication, the market-based tools available to ERCOT will avert most threats to the reliability of the ERCOT System.  However, these Protocols do not preclude ERCOT from taking any action to preserve the integrity of the ERCOT System.

(3)	Under an Emergency Condition, the ERCOT Operator may relax transmission constraints to provide additional generation at the expense of temporarily creating a security violation as long as the violation does not physically overload any single Transmission Element above its emergency limit, as defined in the ERCOT Operating Guides.  ERCOT shall report any NERC or FERC penalties assessed for violating those constraints to Market Participants and the PUCT.

6.5.9.2	Failure of the SCED Process

(1)	When the SCED process is not able to reach a solution, ERCOT shall declare an Emergency Condition.

(2)	For intervals that the SCED process fails to reach a solution, then the LMPs for the interval for which no solution was reached are equal to the LMPs in the most recently solved interval.  ERCOT shall notify the market of the failure using the Messaging System and by posting on the MIS Secure Area.

(3)	Once ERCOT declares an Emergency Condition for a SCED process failure, ERCOT may use any of the following measures:

(a)	ERCOT may direct the SCED process to relax the active transmission constraints and/or the HASLs and LASLs for specific Resources and resume calculation of LMPs by reducing the Ancillary Service Schedules for the affected Resource, if sufficient supply exists to manage total system needs.  LMPs calculated for the affected interval must be used for Settlement;

(b)	ERCOT may issue Emergency Base Points for Resources;

(c)	ERCOT may manually issue Emergency Base Points for a Resource and must communicate the Resource name, MW output requested, and start time and duration of the Dispatch Instruction to the QSE representing the Resource.

(d)	ERCOT may issue an instruction to hold the previous interval.

(e)	A Qualifying Facility (QF), a hydro-powered Resource, or a nuclear-powered Resource may be instructed by ERCOT to operate below its Low Sustained Limit only after all other Resource options have been exhausted.

(4)	The Emergency Condition continues until the SCED process can reach a solution without using the measures in Section 6.5.9.2(3).

6.5.9.3	Communication under Emergency Conditions

(1)	Effective, accurate, and timely communication between ERCOT, TSPs, and QSEs is essential.  Each QSE must be provided adequate information to make informed decisions and must receive the information with sufficient advance notice to facilitate Resource and load responses.

(2)	The type of communication ERCOT issues is determined primarily on the basis of the time available for the market to respond before an Emergency Condition occurs.  The timing of these communications could range from days in advance to immediate.  If there is insufficient time to allow the market to react, ERCOT may bypass one or more of the communication steps.

(3)	ERCOT shall consider the severity of the potential Emergency Condition as it determines which of the communications set forth in Section 6.5.9.1, Emergency and Short Supply Operation, to use.  The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System.

(4)	The following sections describe the types of communications that will be issued by ERCOT to inform all QSEs and TSPs of the operating situation.  These communications may relate to transmission, distribution, or Generation or Load Resources.  The communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition.

6.5.9.3.1	Operating Condition Notice

(1)	ERCOT will issue an Operating Condition Notice (OCN) to inform all QSEs of a possible future need for more Resources due to conditions that could affect ERCOT System reliability.  OCNs are for informational purposes only, and ERCOT exercises no additional operational authority with the issuance of this type of notice, but may solicit additional information from QSEs in order to determine whether the issuance of an Advisory, Alert, or Emergency Notice is warranted. The OCN is the first of four possible levels of communication issued by ERCOT in anticipation of a possible Emergency Condition.

(2)	When time permits, ERCOT will issue an OCN before issuing an Advisory, Alert, or Emergency Notice.  However, issuance of an OCN may not require action on the part of any Market Participant, but rather serves as a reminder to QSEs and TSPs that some attention to the changing conditions may be warranted.  OCNs serve to communicate to QSEs the need to take extra precautions to be prepared to serve the Load during times when contingencies are most likely to arise.

(3)	Reasons for OCNs include unplanned transmission Outages, and weather-related concerns such as anticipated freezing temperatures, hurricanes, wet weather, and ice storms.

(4)	ERCOT will monitor actual and forecasted weather for the ERCOT Region and adjacent NERC regions. When adverse weather conditions are expected, ERCOT may confer with TSPs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness.  Based on its assessment of the potential for adverse conditions, ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven days from the date of the request.   The specific information that may be requested shall be defined in the Operating Guides.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

(5)	QSEs and TSPs are expected to establish and maintain internal procedures for monitoring actual and forecasted weather and for implementing appropriate measures when the potential for adverse weather or other conditions (which could threaten ERCOT System reliability) arise.

6.5.9.3.2	Advisory

(1)	An Advisory is the second of four possible levels of communication issued by ERCOT in anticipation of a possible Emergency Condition.

(2)	ERCOT shall issue an Advisory for the following reasons:

(a)	When it recognizes that conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability;

(b)	When weather or ERCOT System conditions require more lead-time than the normal Day-Ahead Market allows;

;

(c)	When communications or other controls are significantly limited; or

(d)	When ERCOT Transmission Grid conditions are such that operations within first contingency criteria as defined in the Operating Guides are not likely or possible because of Forced Outages or other conditions.

(3)	The Advisory must communicate existing constraints.  ERCOT shall notify TSPs and QSEs of the Advisory, and QSEs shall notify appropriate Resources and LSEs.  ERCOT shall communicate with TSPs as needed to confirm their understanding of the condition and to determine the availability of Transmission Facilities.  For the purposes of verifying submitted information, ERCOT may communicate with QSEs.

(4)	Although an Advisory is for information purposes, ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures.  ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven days from the date of the request.   The specific information that may be requested shall be defined in the Operating Guide.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

6.5.9.3.3	Alert

(1)	An Alert is the third of four possible levels of communication issued by ERCOT in anticipation of a possible Emergency Condition.

(2)	ERCOT shall issue an Alert when ERCOT determines that:

(a)	Conditions have developed such that additional Ancillary Services are needed in the current Operating Period;

(b)	There are insufficient Ancillary Services or Energy Offers. in the Day-Ahead Market (DAM) or in a Supplemental Ancillary Services Market (SASM)

(c)	Market-based congestion management techniques embedded in SCED as specified in these Protocols will not be adequate to resolve transmission security violations;

(d)	Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission security violations; or

(3)	With the issuance of an Alert pursuant to item (2)(a) above, ERCOT may exercise its authority to immediately procure the following services from existing offers:

(a)	Regulation Services;

(b)	Responsive Reserve Services; and

(c)	Non-Spinning Reserve Services.

(4)	If the actions in paragraph (3) above do not relieve the insufficiency described in paragraph (2)(a) above, then ERCOT may issue Dispatch Instructions to Resources certified to provide the insufficient service, even though there is not an existing Ancillary Service Offer for that Resource.

(5)	If ERCOT issues an Alert because insufficient Ancillary Service Offers were received in the DAM, and if the Alert does not result in sufficient offer and the DAM is executed with insufficient offers, then ERCOT shall acquire the insufficient amount of Ancillary Services in the DRUC and shall issue Dispatch Instructions to the QSEs for Resources that were RUC-Committed to provide Ancillary Services, informing them of the requirement that the Resources be prepared to provide those Ancillary Services.

(6)	If ERCOT issues an Alert because insufficient Ancillary Service Offers were received in a SASM, and if the Alert does not result in sufficient offer and the SASM is executed with insufficient offers, then ERCOT shall acquire the insufficient amount of Ancillary Services in the next HRUC and shall issue Dispatch Instructions to the QSEs for Resources that were RUC-Committed to provide Ancillary Services, informing them of the requirement that the Resources be prepared to provide those Ancillary Services.

(7)	ERCOT shall post the Alert message electronically to the MIS Secure Area and shall provide verbal notice to all TSPs and QSEs via the Hotline.  Corrective actions identified by ERCOT must be communicated through Dispatch Instructions to all TSPs, DSPs and QSEs required to implement the corrective action.  Each QSE shall immediately notify the Market Participants that it represents of the Alert.  To minimize the effects on the ERCOT System, each TSP or DSP shall identify and prepare to implement actions, including restoration of transmission lines as appropriate and preparing for Load shedding.  ERCOT may instruct TSPs or DSPs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System.  On notice of an Alert, each QSE, TSP, and DSP shall prepare for an emergency in case conditions worsen.  ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven days from the date of the request.   The specific information that may be requested shall be defined in the Operating Guide.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

6.5.9.3.4	Emergency Notice

(1)	Emergency Notice is the fourth of four possible levels of communication issued by ERCOT in anticipation of a possible Emergency Condition.

(2)	ERCOT shall issue an Emergency Notice only for one or more of the following reasons:

(a)	ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market;

(b)	ERCOT is in an unreliable condition, as defined below;

(c)	Immediate action must be taken to avoid or relieve an overloaded Transmission Element;

(d)	ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures;

(e)	ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process;

or

(f)	The SCED process fails to reach a solution, whether or not ERCOT is using one or both of the measures specified in paragraph (3) of Section 6.5.9.2, Failure of the SCED Process.

(3)	The actions ERCOT takes during an Emergency Condition depend on the nature and severity of the situation.

(4)	ERCOT is considered to be in an unreliable condition whenever ERCOT Transmission Grid status is such that the most severe single-contingency event presents the threat of uncontrolled separation or cascading outages and/or large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of a critical Transmission Element, and no timely solution is obtainable through market processes.

(5)	If the Emergency Condition is the result of a transmission problem that puts the ERCOT System in an unreliable condition, then ERCOT shall act immediately to return the ERCOT System to a reliable condition, including instructing Resources to change output and instructing TSPs or DSPs to drop Load.

(6)	If the Emergency Condition is the result of an Ancillary Service insufficiency, then ERCOT shall follow the Emergency Electric Curtailment Plan procedures.

6.5.9.4	Emergency Electric Curtailment Plan

(1)	At times it may be necessary to reduce ERCOT System Demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing Demand during such emergencies, ERCOT shall initiate and coordinate the implementation of the Emergency Electric Curtailment Plan (EECP) following the steps set forth below in Section 6.5.9.4.2, Restoration of Market Operations.   The goal of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of cascading Outages.

(2)	ERCOT’s operating procedures must meet the following goals:

(a)	Use of market processes to the fullest extent practicable without jeopardizing the reliability of the ERCOT System;

(b)	Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(c)	Maximum use of ERCOT System capability;

(d)	Maintenance of station service for nuclear-powered Generation Resources;

(e)	Securing startup power for Generation Resources;

(f)	Operation of Generation Resources during loss of communication with ERCOT; and

(g)	Restoration of service to Loads in the manner defined in the Operating Guides.

(3)	ERCOT is responsible for coordinating with QSEs, TSPs, and DSPs to monitor ERCOT System conditions, initiating the EECP steps set forth herein, notifying all QSEs, and coordinating the implementation of the EECP steps while maintaining transmission security limits.

(4)	During the EECP, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using the DC or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with NERC scheduling guidelines.

(5)	Some of the EECP steps are not applicable if transmission security violations exist. There may be insufficient time to implement all EECP steps in sequence, however, to the extent practicable, ERCOT shall use Ancillary Services that QSEs have made available in the market to maintain or restore reliability.

(6)	ERCOT may immediately implement Step 5 of the EECP any time the steady-state system frequency is below 59.8 Hz and shall immediately implement Step 5 any time the steady-state frequency is below 59.5 Hz.

(7)	Percentages for Step 5 Load shedding must be based on the previous year’s TSP peak Loads, as reported to ERCOT, and must be reviewed by ERCOT and modified annually as required.

6.5.9.4.1	EECP Steps

(1)	Step 1

(a)	Maintain 2,300 MW of reserves from Resources comprised of:

(i)	Undeployed Responsive Reserve; and

(ii)	The amount of Non-Spinning Reserve that has been deployed but has not ramped to its specified output level.

(b)	To maintain that 2,300 MW, ERCOT shall:

(i)	Use available Resources that can be deployed to increase Responsive Reserves;

(ii)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

(iii)	Suspend any ongoing generating unit or Resource performance testing;

(iv)	Commit available Resources as necessary that can respond in the timeframe of the emergency; such commitments are settled using the HRUC process;

(v)	Use available DC Tie import capacity not already being used by QSEs and inquire about availability of BLTs;

(vi)	Request QSEs to voluntarily interrupt a DC Tie Schedule exporting power from ERCOT and, in the event no QSE will voluntarily interrupt its export schedule, ERCOT shall initiate curtailment of all non-firm export schedules in accordance with NERC Control Area energy scheduling guidelines; and

(vii)	Start RMR Units available in the time frame of the emergency. RMR Units may be loaded to full output capability as necessary.

(2)	Step 2

Maintain 1,800 MW of ERCOT’s reserve from Resources comprised of undeployed Responsive Reserve Service. ERCOT shall:

(a)	Relax confidentiality requirements of transmission operating and system capacity information, if needed to improve communications during the Emergency Condition; and

(b)	Deploy half of the Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Load providing Responsive Reserve.  ERCOT shall develop a procedure for determining which Load Resources to interrupt and to equitably allocate Load Resources to one of two deployment stacks to enable a 50% deployment, which procedure must be approved in advance by TAC.

(3)	Step 3

Maintain ERCOT undeployed Responsive Reserve Service equal to the largest Generation Resource On-Line in ERCOT. The undeployed Responsive Reserve Service may come from Load Resources capable of controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) and from Generation Resources.  To maintain that level of undeployed RRS, ERCOT:

(a)	Shall instruct TSPs and DSPs to reduce Load by using distribution voltage reduction management tools, if deemed beneficial by the TSP and DSP;

(b)	Shall instruct QSEs to interrupt all remaining Responsive Reserve supplied by Load Resources; and

(c)	May, with the approval of the affected Non-ERCOT Control Area, instruct TSPs to implement Block Load Transfers, as described in 6.5.9.5, Block Load Transfers between ERCOT and Non-ERCOT Control Areas, which transfer Load from the ERCOT Control Area to Non-ERCOT Control Areas.

(d)	ERCOT shall initiate curtailment of all remaining export schedules in accordance with NERC Control Area energy scheduling guidelines.

(4)	Step 4 – Maintain system frequency at 60 Hz

In addition to measures listed above, ERCOT shall issue an appeal through the public media for voluntary Load curtailment.

(5)	Step 5 — Maintain system frequency at 59.8 Hz or greater

In addition to measures listed above, ERCOT shall instruct, in 100 MW blocks, all TSPs and DSPs having control over distribution feeder breakers or control of breakers serving retail customers to shed Load to maintain a steady-state system frequency of 59.8 Hz. ERCOT shall allocate manual Load shedding for ERCOT-wide emergencies based on the amount of Load that is served by each TSP.

6.5.9.4.2	Restoration of Market Operations

ERCOT shall continue EECP until sufficient offers are received and deployed by ERCOT to eliminate the conditions requiring the EECP and normal SCED operations are restored.  Intermittent solutions of SCED do not set new LMPs until ERCOT declares that the EECP is no longer needed.

6.5.9.5	Block Load Transfers between ERCOT and Non-ERCOT Control Areas

Block Load Transfers (BLTs) are procedures that transfer Loads normally located in the ERCOT Control Area to a Non-ERCOT Control Area.  Similarly, when a Non-ERCOT Control Areas experience certain transmission contingency or short-supply conditions, ERCOT may agree to the implementation of BLT procedures that transfer Loads normally located in a Non-ERCOT Control Area to the ERCOT Control Area.  BLTs are restricted to the following conditions:

(a)	BLTs may occur only under a specific Dispatch Instruction from ERCOT.

(b)	BLTs that are comprised of looped systems may be tied to the other Control Area’s electrical system(s) through multiple interconnection points at the same time.  Transfers of looped configurations are permitted only if all interconnection points are netted under a single ESI ID.

(c)	BLTs of Load to the ERCOT Control Area are:

(i)	Treated as non-competitive wholesale Load in the Load Zone containing the ERCOT breaker or switch that initiated the BLT;

(ii)	Registered in a manner similar to that of Non-Opt-In Entities;

(iii)	Responsible for UFE allocations and Transmission Losses consistent with similarly situated Non Opt-In Entity metering points: and

(iv)	Permitted only if the BLT will not jeopardize the reliability of the ERCOT System.  Under an Emergency Notice, BLTs that have been implemented may be curtailed or terminated by ERCOT to maintain the reliability of the ERCOT System.

(d)	BLTs of Load from the ERCOT Control Area are treated as Resources in the ERCOT Settlement system and may only be instructed with the permission of the affected Non-ERCOT Control Area.  Under an Emergency Condition, BLTs that have been implemented may be curtailed or terminated by the Non-ERCOT Control Area to maintain the reliability of the Non-ERCOT system.

(e)	BLTs specifically exclude transfers of Load between ERCOT and Non-ERCOT Control Areas that occur behind a retail Settlement Meter.

(f)	BLTs may be used in the restoration of service to customers if the transfers will not jeopardize the reliability of the ERCOT System.

(g)	The necessary Market Participant agreements, metering, and ERCOT Settlement systems must be in place before ERCOT may implement any BLT.

(h)	BLT metering points connected to the ERCOT Transmission Grid used five or more time per year, as monitored by the TSP, must conform to ERCOT-Polled Settlement (EPS) Metering requirements as defined in Section 10, Metering, and the Settlement Metering Operating Guides.  All other BLT metering points must be revenue quality, four channel bi-directional kWh/kvarh, 15-minute Interval Data Recording (IDR) metering with remote interrogation.  ERCOT may impose additional metering requirements it considers necessary to ensure ERCOT System reliability and integrity.

(i)	Supervisory Control and Data Acquisition (SCADA) telemetry on switching devices at BLT points must be provided.

6.5.9.5.1	Registration of BLT Points

(1)	BLTs that block ERCOT Load into a non-ERCOT Control Area are treated as a Resource by ERCOT and assigned a Resource ID.  The TSP or DSP associated with the BLT Point has the responsibility for creation and maintenance of BLT Resource IDs.  An ERCOT-registered Resource Entity with an ERCOT-registered QSE affiliation must complete the applicable asset registration forms.  This asset registration form along with the metering design documentation is the basis for establishing the ERCOT data model of the BLT.

(2)	BLTs that block Non-ERCOT Load into the ERCOT System are treated as a non-competitive wholesale Load by ERCOT and assigned an ESI ID.  The TSP or DSP associated with the BLT Point has the responsibility for creation and maintenance of BLT ESI IDs.  Customers connected to the ERCOT System do not require an ESI ID if they are located behind BLT Points.  The TSP or DSP that creates the BLT Point shall provide the ESI ID associated with the BLT to ERCOT as well as notify ERCOT of the ERCOT registered LSE, and the QSE affiliation of the LSE associated with the BLT.

(3)	A “BLT Point” is the metering point for a BLT Resource ID or for a BLT ESI ID.

6.5.9.5.2	Scheduling and Operation of BLTs

(1)	The QSE for the Resource associated with a BLT Point shall include that Resource in its Current Operating Plan.  The QSE is not required to provide the Real-Time data for the BLT Point to ERCOT as would normally be provided on behalf of Resources.  The Current Operating Plan must show the availability of the Resource, but ERCOT shall confirm its availability with the Non-ERCOT system before issuing any Dispatch Instructions to the QSE and the TDSP.  Any energy delivered under such a Dispatch Instruction is treated as an Emergency Base Point instruction to the QSE.

(2)	Generation Resources connected to the portion of the ERCOT Transmission Grid included in the BLT are under no obligation, under these Protocols, to provide Ancillary Services or any other services to ERCOT while that portion of the ERCOT Transmission Grid is connected to a non-ERCOT system other than through a DC Tie.

(3)	ERCOT shall continue to include the BLT Point Load in the Settlement of the LSE Load Obligations.

6.5.9.6	Black Start

(1)	Black-Start Service is obtained by ERCOT through Black Start Agreements with QSEs for Generation Resources capable of self-starting or Generation Resources within close proximity of a non-ERCOT Control Area that are capable of starting from that non-ERCOT Control Area under a firm standby power supply contract, without support from the ERCOT System, or transmission equipment in the ERCOT System.  Generation Resources that can be started with a minimum of pre-coordinated switching operations using ERCOT transmission equipment within the ERCOT System may be considered for Black Start Service only where switching may be accomplished within one hour or less.

(2)	ERCOT may Dispatch Black-Start Service pursuant to an emergency restoration plan to begin restoration of the ERCOT System to a secure operating state after a blackout. ERCOT shall include in the restoration plan specific instructions for all Market Participants, including TSPs and DSPs, describing actions to be taken on loss of communication and other general restoration actions. ERCOT shall post the restoration plan on the MIS Secure Area within 14 days of creation or update.

6.6	Settlement Calculations for the Real-Time Energy Operations

6.6.1	Real-Time Settlement Point Prices

Real-Time energy settlements use Real-Time Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs.

6.6.1.1	Real-Time Settlement Point Price for a Resource Node

The Real-Time Settlement Point Price for a Resource Node Settlement Point is a Base-Point time-weighted average of the Real-Time LMPs.  The Real-Time Settlement Point Price for a 15-minute Settlement Interval is calculated as follows:

RTSPP	=	Σy(RNWFy * RTLMPy)

Where the Resource Node weighting factor is:

RNWFy	=	[Max (0.001, ΣrBPr, y) * TLMPy] / [Σy(Max (0.001, ΣrBPr, y) * TLMPy)]

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Settlement Point for the 15-minute Settlement Interval. |
| RTLMP y | $/MWh | Real-Time Locational Marginal Price per intervalThe Real-Time LMP at the Settlement Point for the SCED interval y. |
| BP r, y | MW | Base Point per Resource per intervalThe Base Point of Resource r, for the whole SCED interval y. |
| RNWF y | none | Resource Node Weighting Factor per intervalThe weight used in the Resource Node Settlement Point Price calculation for the portion of the SCED interval y within the Settlement Interval. |
| TLMP y | second | Duration of SCED interval per interval – The duration of the portion of the SCED interval y within the Settlement Interval. |
| Y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| R | none | A Resource at the Resource Node. The summation is taken over all Resources at that node. |

6.6.1.2	Real-Time Settlement Point Price for a Load Zone

The Real-Time Settlement Point Price for a Load Zone Settlement Point is based on the state-estimated Load in MW and the time-weighted average Real-Time LMPs at Electrical Buses that are included in the Load Zone.  The Real-Time Settlement Point Price for a Load Zone Settlement Point for a 15-minute Settlement Interval is calculated as follows:

RTSPP	=	ΣyΣb (RTLMP b, y * LZWF b, y)

For all Load Zones except DC Tie Load Zones:

LZWF b, y 	=	(SEL b, y * TLMP y) / [ΣyΣb(SEL b, y * TLMP y)]

For a DC Tie Load Zone:

LZWF y 	=	[Max (0.001, SEL y)* TLMP y)] / [Σy[Max (0.001, SEL y)* TLMPy)]

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSPP | $/MWh | Real-Time Settlement Point PriceThe Real-Time Settlement Point Price at the Settlement Point, for the 15-minute Settlement Interval. |
| RTLMP b, y | $/MWh | Real-Time Locational Marginal Price at bus per intervalThe Real-Time Settlement Point Price at Electrical Bus b in the Load Zone, for the SCED interval y. |
| LZWF b, y | none | Load Zone Weighting Factor per bus per intervalThe weight used in the Load Zone Settlement Point Price calculation for Electrical Bus b, for the portion of the SCED interval y within the 15-minute Settlement Interval. |
| SEL b, y | MW | State Estimator Load at bus per intervalThe Load from State Estimator for Electrical Bus b in the Load Zone, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the SCED interval y. |
| Y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| B | none | An Electrical Bus in the Load Zone. The summation is over all of the Electrical Buses in the Load Zone. |

6.6.1.3	Real-Time Settlement Point Price for a Hub

The Real-Time Settlement Point Price at a Hub is determined according to the methodology included in the definition of that Hub in Section 3.5.2, Hub Definitions.

6.6.2	Load Ratio Share

6.6.2.1	ERCOT Total Adjusted Metered Load

ERCOT total Adjusted Metered Load (excluding the DC Tie export associated with the QSEs under the “Oklaunion Exemption”) for a 15-minute Settlement Interval is calculated as follows:

RTAMLTOT	=	ΣqΣpRTAML q, p

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTAMLTOT | MWh | Real-Time Adjusted Metered Load Total—The total Adjusted Metered Load in ERCOT, for the 15-minute Settlement Interval. |
| RTAML q, p | MWh | Real-Time Adjusted Metered Load per QSE per Settlement Point—The sum of the Adjusted Metered Load at the Electrical Buses that are included in Settlement Point p, represented by QSE q, for the 15-minute Settlement Interval. |
| Q | none | A QSE. The summation is over all of the QSEs with metered readings in that interval. |
| P | none | A Settlement Point. The summation is over all of the Settlement Points. |

6.6.2.2	QSE Load Ratio Share for a 15-Minute Settlement Interval

Each QSE’s Load Ratio Share for a 15-minute Settlement Interval is calculated as follows:

LRS q	=	(ΣpRTAML q, p) / RTAMLTOT

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| LRS q | none | Load Ratio Share per QSE—The Load Ratio Share as defined in Section 2, Definitions and Acronyms, for QSE q, for the 15-minute Settlement Interval. |
| RTAML q, p | MWh | Real-Time Adjusted Metered Load per Settlement Point per QSE—The sum of the Adjusted Metered Load at the Electrical Buses that are included in Settlement Point p, represented by QSE q, for the 15-minute Settlement Interval. |
| RTAMLTOT | MWh | Real-Time Adjusted Metered Load Total—The total Adjusted Metered Load in ERCOT, for the 15-minute Settlement Interval. |
| P | none | A Settlement Point. The summation is over all of the Settlement Points. |

6.6.2.3	QSE Load Ratio Share for an Operating Hour

Each QSE’s Load Ratio Share for an Operating Hour is calculated as follows:

HLRS q	=	(Σ4i=1ΣpRTAML q, p, i) / (Σ4i=1RTAMLTOT i)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| HLRS q | none | Hourly Load Ratio Share per QSE—The Load Ratio Share as defined in Section 2, Definitions and Acronyms, for QSE q, for the hour. |
| RTAML q, p, i | MWh | Real-Time Adjusted Metered Load per Settlement Point per QSE by interval—The sum of the Adjusted Metered Load at the Electrical Buses that are included in the Settlement Point p, represented by QSE q for the 15-minute Settlement Interval i. |
| RTAMLTOT i | MWh | Real-Time Adjusted Metered Load Total by interval—The total Adjusted Metered Load in ERCOT, for the 15-minute Settlement Interval i. |
| P | None | A Settlement Point. The summation is over all of the Settlement Points. |
| I | none | A 15-minute Settlement Interval in the Operating Hour. The summation over all of the Settlement Intervals of the Operating Hour. |

6.6.3	Real-Time Energy Charges and Payments

6.6.3.1	Real-Time Energy Imbalance Payment or Charge at a Resource Node

(1)	The payment or charge to each QSE for Energy Imbalance Service is calculated based on the Real-Time SPP for the following amounts at a particular Resource Node Settlement Point:

(a)	The energy produced by all its Generation Resources at the Settlement Point; plus

(b)	The amount of its Self-Schedules with sink specified at the Settlement Point; plus

(c)	The amount of its Energy Bids cleared in the DAM at the Settlement Point; plus

(d)	The amount of its Energy Trades at the Settlement Point where the QSE is the buyer; minus

(e)	The amount of its Self-Schedules with source specified at the Settlement Point; minus

(f)	The amount of its Energy Offers cleared in the DAM at the Settlement Point; minus

(g)	The amount of its Energy Trades at the Settlement Point where the QSE is the seller

(2)	The payment or charge to each QSE for Energy Imbalance Service at a Resource Node Settlement Point for a given 15-minute Settlement Interval is calculated as follows:

RTEIAMTq, p	=	(-1) * RTSPP p * {ΣrRTMG q, p, r + (SSSK q, p * ¼) + (DAEP q, p * ¼) + (RTQQEP q, p * ¼) – (SSSR q, p * ¼) – (DAES q, p * ¼) – (RTQQES q, p * ¼)}

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTEIAMTq, p | $ | Real-Time Energy ImbalanceAmount per QSE per Settlement Point—The payment or charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| RTMG q, p, r | MWh | Real-Time Metered Generation per QSE per Settlement Point per Resource—The Real-Time energy produced by the Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| SSSK q, p | MW | Self-Schedule with Sink at Settlement Point per QSE per Settlement Point—The QSE q’s Self-Schedule with sink at Settlement Point p, for the 15-minute Settlement Interval. |
| DAEP q, p | MW | Day-Ahead Energy Purchase per QSE per Settlement Point—The QSE q’s Energy Bids at Settlement Point p cleared in the DAM, for the hour that includes the 15-minute Settlement Interval. |
| RTQQEP q, p | MW | Real-Time QSE-to-QSE Energy Purchase per QSE per Settlement PointThe amount of MW bought by QSE q through Energy Trades at Settlement Point p, for the 15-minute Settlement Interval. |
| SSSR q, p | MW | Self-Schedule with Source at Settlement Point per QSE per Settlement Point—The QSE q’s Self-Schedule with source at Settlement Point p, for the 15-minute Settlement Interval. |
| DAES q, p | MW | Day-Ahead Energy Sale per QSE per Settlement Point—The QSE q’s Energy Offers at Settlement Point p cleared in the DAM, for the hour that includes the 15-minute Settlement Interval. |
| RTQQES q, p | MW | Real-Time QSE-to-QSE Energy Sale per QSE per Settlement PointThe amount of MW sold by QSE q through Energy Trades at Settlement Point p, for the 15-minute Settlement Interval. |
| q |  | A QSE. |
| p |  | A Resource Node Settlement Point. |
| r |  | A Generation Resource. |

(3)	The total net payments and charges to each QSE for Energy Imbalance Service at all Resource Node Settlement Points for the 15-minute Settlement Interval is calculated as follows:

RTEIAMTQSETOT q	=	ΣpΣr RTEIAMT q, p

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTEIAMTQSETOT q | $ | Real-Time Energy Imbalance Amount QSE Total per QSEThe total net payments and charges to QSE q for Real-Time Energy Imbalance at all Resource Node Settlement Points for the 15-minute Settlement Interval. |
| RTEIAMT q, p | $ | Real-Time Energy Imbalance Amount per QSE per Settlement Point—The payment or charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |

6.6.3.2	Real-Time Energy Imbalance Payment or Charge at a Load Zone

(1)	The payment or charge to each QSE for Energy Imbalance Service is calculated based on the Real-Time SPP for the following amounts at a particular Load Zone Settlement Point:

(a) 	The amount of its Self-Schedules with sink specified at the Settlement Point; plus

(b) 	The amount of its Energy Bids cleared in the DAM at the Settlement Point; plus

(c) 	The amount of its Energy Trades at the Settlement Point where the QSE is the buyer; minus

(d) 	The amount of its Self-Schedules with source specified at the Settlement Point; minus

(e) 	The amount of its Energy Offers cleared in the DAM at the Settlement Point; minus

(f) 	The amount of its Energy Trades at the Settlement Point where the QSE is the seller; minus

(g) 	Tts Adjusted Metered Load at the Settlement Point.

(2)	The payment or charge to each QSE for Energy Imbalance Service at a Load Zone for a given 15-minute Settlement Interval is calculated as follows:

RTEIAMT q, p	=	(-1) * RTSPP p * { (SSSK q, p * ¼) + (DAEP q, p * ¼) + (RTQQEP q, p * ¼) – (SSSR q, p * ¼) – (DAES q, p * ¼) – (RTQQES q, p * ¼) – RTAML q, p }

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTEIAMT q, p | $ | Real-Time Energy Imbalance Amount per QSE per Settlement Point—The payment or charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| RTAML q, p | MWh | Real-Time Adjusted Metered Load per QSE per Settlement Point—The sum of the Adjusted Metered Load at the Electrical Buses that are included in Settlement Point p represented by QSE q for the 15-minute Settlement Interval. |
| SSSK q, p | MW | Self-Schedule with Sink at Settlement Point per QSE per Settlement Point—The QSE q’s Self Schedule with sink at Settlement Point p, for the 15-minute Settlement Interval. |
| DAEP q, p | MW | Day-Ahead Energy Purchase per QSE per Settlement Point—The QSE q’s Energy Bids at Settlement Point p cleared in the DAM, for the hour that includes the 15-minute Settlement Interval. |
| RTQQEP q, p | MW | Real-Time QSE-to-QSE Energy Purchase per QSE per Settlement PointThe amount of MW bought by QSE q through Energy Trades at Settlement Point p, for the 15-minute Settlement Interval. |
| SSSR q, p | MW | Self-Schedule with Source at Settlement Point per QSE per Settlement Point—The QSE q’s Self-Schedule with source at Settlement Point p, for the 15-minute Settlement Interval. |
| DAES q, p | MW | Day-Ahead Energy Sale per QSE per Settlement Point—The QSE q’s Energy Offers at Settlement Point p cleared in the DAM, for the hour that includes the 15-minute Settlement Interval. |
| RTQQES q, p | MW | Real-Time QSE-to-QSE Energy Sale per QSE per Settlement PointThe amount of MW sold by QSE q through Energy Trades at Settlement Point p, for the 15-minute Settlement Interval. |
| q |  | A QSE. |
| p |  | A Resource Node Settlement Point. |

(3)	The total net payments and charges to each QSE for Energy Imbalance Service at all Load Zones for the 15-minute Settlement Interval is calculated as follows:

RTEIAMTQSETOT q	=	ΣpRTEIAMT q, p

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTEIAMTQSETOT q | $ | Real-Time Energy Imbalance Amount QSE Total per QSEThe total net payments and charges to QSE q for Real-Time Energy Imbalance at all Load Zone Settlement Points for the 15-minute Settlement Interval. |
| RTEIAMT q, p | $ | Real-Time Energy Imbalance Amount per QSE per Settlement Point—The charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| Q | none | A QSE. |
| P | none | A Load Zone Settlement Point. |

6.6.3.3	Real-Time Energy Imbalance Payment or Charge at a Hub

(1)	The payment or charge to each QSE for Energy Imbalance Service is calculated based on the Real-Time SPP for the following amounts at a particular Hub Settlement Point:

(a) 	The amount of its Self-Schedules with sink specified at the Settlement Point; plus

(b) 	The amount of its Energy Bids cleared in the DAM at the Settlement Point; plus

(c) 	The amount of its Energy Trades at the Settlement Point where the QSE is the buyer; minus

(d) 	The amount of its Self-Schedules with source specified at the Settlement Point; minus

(e) 	The amount of its Energy Offers cleared in the DAM at the Settlement Point; minus

(f) 	The amount of its Energy Trades at the Settlement Point where the QSE is the seller.

(2)	The payment or charge to each QSE for Energy Imbalance Service at a Hub for a given 15-minute Settlement Interval is calculated as follows:

RTEIAMT q, p	=	(-1) * RTSPP p * { (SSSK q, p * ¼) + (DAEP q, p * ¼) + (RTQQEP q, p * ¼) – (SSSR q, p * ¼) – (DAES q, p * ¼) – (RTQQES q, p * ¼) }

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTEIAMT q, p | $ | Real-Time Energy Imbalance Amount per QSE per Settlement Point—The payment or charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| SSSK q, p | MW | Self-Schedule with Sink at Settlement Point per QSE per Settlement Point—The QSE q’s Self-Schedule with sink at Settlement Point p, for the 15-minute Settlement Interval. |
| DAEP q, p | MW | Day-Ahead Energy Purchase per QSE per Settlement Point—The QSE q’s Energy Bids at Settlement Point p cleared in the DAM, for the hour that includes the 15-minute Settlement Interval. |
| RTQQEP q, p | MW | Real-Time QSE-to-QSE Energy Purchase per QSE per Settlement PointThe amount of MW bought by QSE q through Energy Trades at Settlement Point p, for the 15-minute Settlement Interval. |
| SSSR q, p | MW | Self-Schedule with Source at Settlement Point per QSE per Settlement Point—The QSE q’s Self-Schedule with source at Settlement Point p, for the 15-minute Settlement Interval. |
| DAES q, p | MW | Day-Ahead Energy Sale per QSE per Settlement Point—The QSE q’s Energy Offers at Settlement Point p cleared in the DAM, for the hour that includes the 15-minute Settlement Interval. |
| RTQQES q, p | MW | Real-Time QSE-to-QSE Energy Sale per QSE per Settlement PointThe amount of MW sold by QSE q through Energy Trades at Settlement Point p, for the 15-minute Settlement Interval. |
| q |  | A QSE. |
| p |  | A Hub Settlement Point. |

(3)	The total net payments and charges to each QSE for Energy Imbalance Service at all Hubs for the 15-minute Settlement Interval is calculated as follows:

RTEIAMTQSETOT q	=	ΣpRTEIAMT q, p

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTEIAMTQSETOT q | $ | Real-Time Energy Imbalance Amount QSE Total per QSEThe total net payments and charges to QSE q for Real-Time Energy Imbalance at all Hub Settlement Points for the 15-minute Settlement Interval. |
| RTEIAMT q, p | $ | Real-Time Energy Imbalance Amount per QSE per Settlement Point—The charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| p | none | A Hub Settlement Point. |

Σp

Σp

6.6.3.4	Real-Time Energy Payment for DC Tie Import

(1)	The payment to each QSE for energy imported into the ERCOT System through each DC Tie is calculated based on the Real-Time Settlement Point Price at the DC Tie Settlement Point.  The payment for a given 15-minute Settlement Interval is calculated as follows:

RTDCIMPAMT q, p	=	(-1) * RTSPP p * (RTDCIMP q, p * ¼)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTDCIMPAMT q, p | $ | Real-Time DC Import Amount per QSE per Settlement Point—The payment to QSE q for DC Tie import through DC Tie p, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| RTDCIMP q, p | MW | Real-Time DC Import per QSE per Settlement Point—The aggregated DC Tie Schedule submitted by QSE q as an importer into the ERCOT System through DC Tie p, for the 15-minute Settlement Interval. |
| q | None | A QSE. |
| p | None | A DC Tie Settlement Point. |

(2)	The total of the payments to each QSE for all energy imported into the ERCOT System through DC Ties for the 15-minute Settlement Interval is calculated as follows:

RTDCIMPAMTQSETOT q	=	ΣpRTDCIMPAMT q, p

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTDCIMPAMTQSETOT q | $ | Real-Time DC Import Amount QSE Total per QSEThe total of the payments to QSE q for energy imported into the ERCOT System through DC Ties for the 15-minute Settlement Interval. |
| RTDCIMPAMT q, p | $ | Real-Time DC Import Amount per QSE per Settlement Point—The payment to QSE q for DC Tie import through DC Tie p, for the 15-minute Settlement Interval. |
| Q | none | A QSE. |
| P | none | A DC Tie Settlement Point. |

6.6.3.5	Real-Time Payment for a Block Load Transfer Point

(1)	The payment for the energy delivered to an ERCOT Load through a BLT Point is made to the QSE for that BLT Point for each 15-minute Settlement Interval, based on the Real-Time Settlement Point Price for the Load Zone Settlement Point where the ERCOT Load normally locates. The payment for a given 15-minute Settlement Interval is calculated as follows:

BLTRAMT q, p, bltp	=	(-1) * RTSPP p * BLTR q, p, bltp

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BLTRAMT q, p, bltp | $ | Block Load Transfer Resource Amount per QSE per Settlement Point per BLT Point—The payment to QSE q for the BLT Resource that delivers energy to Load Zone p through BLT Point bltp, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| BLTR q, p, bltp | MWh | Block Load Transfer Resource per QSE per Settlement Point per BLT Point—The energy delivered to an ERCOT Load in Load Zone p through BLT Point bltp represented by QSE q, for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| p | none | A Load Zone Settlement Point. |
| bltp | none | A BLT Point. |

(2)	The total of the payments to each QSE for all energy delivered to ERCOT Loads through BLT Points for the 15-minute Settlement Interval is calculated as follows:

BLTRAMTQSETOT q	=	ΣpΣbltpBLTRAMT q, p, bltp

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BLTRAMTQSETOT q | $ | Block Load Transfer Resource Amount QSE Total per QSEThe total of the payments to QSE q for energy delivered into the ERCOT System through BLT Points for the 15-minute Settlement Interval. |
| BLTRAMT q, p, bltp | $ | Block Load Transfer Resource Amount per QSE per Settlement Point per BLT Point—The payment to QSE q for the BLT Resource at BLT Point bltp, which delivers energy to Load Zone p, for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| p | none | A Load Zone Settlement Point. |
| bltp | none | A BLT Point. |

Σp

6.6.4.2

Σp

Σp

6.6.3.6	Real-Time Energy Charge for DC Tie Export Represented by the QSE Under the Oklaunion Exemption

(1)	The charge to a QSE that is exporting energy from the ERCOT System under the “Oklaunion Exemption” through a DC Tie associated with the exemption is calculated based on the Real-Time Settlement Point Price at the DC Tie Settlement Point.  This charge for a given 15-minute Settlement Interval is calculated as follows:

RTDCEXPAMT q, p	=	RTSPP p * (RTDCEXP q, p * ¼)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTDCEXPAMT q, p | $ | Real-Time DC Export Amount per QSE per Settlement Point—The charge to QSE q for the DC Tie exports through DC Tie p, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| RTDCEXP q, p | MW | Real-Time DC Export per QSE per Settlement Point—The aggregated DC Tie Schedule through DC Tie p submitted by QSE q that is under the “Oklaunion Exemption” as an exporter from the ERCOT area, for the 15-minute Settlement Interval. |
| Q | none | A QSE. |
| P | none | A DC Tie Settlement Point. |

(2)	The total of the charges to each QSE for all energy exported from the ERCOT System through DC Ties for the 15-minute Settlement Interval is calculated as follows:

RTDCEXPAMTQSETOT q	=	ΣpRTDCEXPAMT q, p

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTDCEXPAMTQSETOT q | $ | Real-Time DC Export Amount QSE Total per QSEThe total of the charges to QSE q for energy exported from the ERCOT System through DC Ties for the 15-minute Settlement Interval. |
| RTDCEXPAMT q, p | $ | Real-Time DC Export Amount per QSE per Settlement Point—The charge to QSE q for the DC Tie exports through DC Tie p, for the 15-minute Settlement Interval. |
| Q | none | A QSE. |
| P | none | A DC Tie Settlement Point. |

37

(2)	The total of the charges to each

ΣpΣbltp

6.6.4	Real-Time Congestion Payment or Charge for Self-Schedules

(1)	The congestion payment or charge to each QSE submitting a Self-Schedule calculated based on the difference in Real-Time SPPs at the specified sink and the source of the Self-Schedule multiplied by the amount of the Self-Schedule. The congestion charge to each QSE for each of its Self-Schedule for a given 15-minute Settlement Interval is calculated as follows:

RTCCAMT q, s 	=	(RTSPP sink, s – RTSPP source, s) * (SSQ q, s * ¼)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTCCAMT q, p | $ | Real-Time Congestion Cost Amount per QSE per Self-Schedule—The congestion charge to QSE q for its Self-Schedule s, for the 15-minute Settlement Interval. |
| RTSPP sink, s | $/MWh | Real-Time Settlement Point Price at the Sink of Self-Schedule—The Real-Time Settlement Point Price at the sink of the Self-Schedule s, for the 15-minute Settlement Interval. |
| RTSPP source, s | $/MWh | Real-Time Settlement Point Price at the Source of Self-Schedule—The Real-Time Settlement Point Price at the source of the Self-Schedule s, for the 15-minute Settlement Interval. |
| SSQ q,s | MW | Self-Schedule Quantity per Self-Schedule—The QSE q’s Self Schedule MW quantity for Self-Schedule s, for the 15-minute Settlement Interval. |
| q |  | A QSE. |
| s |  | A Self-Schedule. |

(2)	The total net congestion payments and charges to each QSE for all its Self-Schedules for the 15-minute Settlement Interval is calculated as follows:

RTCCAMTQSETOT q	=	ΣsRTCCAMT q, s

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RTCCAMTQSETOT q | $ | Real-Time Congestion Cost Amount QSE Total per QSEThe total net congestion payments and charges to QSE q for its Self-Schedules for the 15-minute Settlement Interval. |
| RTCCAMT q, s | $ | Real-Time Congestion Cost Amount per QSE per Self-Schedule—The congestion payment or charge to QSE q for its Self-Schedule s, for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| s | none | A Self-Schedule. |

6.6.5	Generation Resource Base-Point Deviation Charge

A QSE for a Generation Resource shall pay a Base-Point deviation charge if the Resource did not follow Dispatch Instructions and Ancillary Services deployments within defined tolerances, except when the Dispatch Instructions and Ancillary Services deployments violate the Resource Parameters.  The Base-Point deviation charge does not apply to Generation Resources between breaker close and the time at which the telemetered HSL becomes greater than LSL.  The desired output from a Generation Resource during a 15-minute Settlement Interval is calculated as follows:

AABP	=	Σy((BP y + BP y-1)/2 * TLMP y) / (ΣyTLMP y) +  TWAR

Where :

TWAR	=	Σy((ARI y * TLMP y) / (ΣyTLMP y)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| AABP | MW | Adjusted Aggregated Base Point—The Generation Resource’s aggregated Base Point adjusted for Ancillary Service deployments, for the 15-minute Settlement Interval. |
| BP y | MW | Base Point by interval—The Base Point for the Generation Resource at the Resource Node, for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per interval—The duration of the portion of the SCED interval y within the 15-minute Settlement Interval. |
| TWAR | MW | Time-Weighted Average Regulation – The amount of regulation that the Generation Resource should have produced based on the deployment signals as calculated by the LFC within the 15-minute Settlement Interval. |
| ARI y | MW | Average Regulation Instruction – The amount of regulation that the Generation Resource should have produced based on the deployment signals as calculated by the LFC within the SCED interval. |
| y | none | A SCED interval in the Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |

6.6.5.1	General Generation Resource Base-Point Deviation Charge

(1)	Unless one of the exceptions specified in paragraphs (2) and (3) below applies, ERCOT shall charge a Generation Resource Base-Point deviation charge for a Generation Resource other than those described in Section 6.6.5.2, IRR Generation Resource Base-Point Deviation Charge, and Section 6.6.5.3, Generators Exempt from Deviation Charges, when:

(a)	The Settlement Point Price for the Resource Node is positive; and

(b)	The telemetered generation of the Generation Resource over the 15-minute Settlement Interval is outside the tolerances defined later in this Subsection.

(2)	ERCOT may not charge a QSE a  Generation Resource Base-Point deviation charge under paragraph (1) above when both (a) and (b) apply:

(a)	The generation deviation of the Generation Resource over the 15-minute Settlement Interval is in a direction that contributes to frequency corrections that resolve an ERCOT System frequency deviation; and

(b)	The ERCOT System frequency deviation is greater than +/-0.05 Hz at any time during the 15-minute Settlement Interval.

(3)	ERCOT may not charge a QSE a Generation Resource Base-Point deviation charge under paragraph (1) above for any 15-minute Settlement Interval during which Responsive Reserve is deployed.

6.6.5.1.1	Base Point Deviation Charge for Over Generation

(1)	ERCOT shall charge a QSE for a Generation Resource for over generation that exceeds the following tolerance.  The tolerance is the greater of:

(a)	5% of the average of the Base Points in the Settlement Interval adjusted for any Ancillary Services deployments; or

(b)	5 MW for metered generation above the average of the Base Points in the Settlement Interval adjusted for any Ancillary Services deployments.

(2)	The charge to each QSE for over-generation of each Generation Resource at each Resource Node Settlement Point, if the Real-Time metered generation is greater than the upper tolerance during a given 15-minute Settlement Interval, is calculated as follows:

BPDAMT q, p, r	=	Max (0, RTSPP p) * Max [0, (TWTG q, p, r – ¼ * Max (((1 + K1) * AABP q, p, r), (AABP q, p, r + Q1)))]

Where:

TWTG	=	Σy(ATG y * TLMP y /3600 Σy)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, p, r | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| TWTG q, p, r | MWh | Time-Weighted Telemetered Generation per QSE per Settlement Point per Resource—The telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| AABP q, p, r | MW | Adjusted Aggregated Base Point per QSE per Settlement Point per Resource—The aggregated Base Point adjusted for Ancillary Service deployments, of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| ATG y | MW | Average Telemetered Generation - The average telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the SCED interval. |
| TLMP y | second | Duration of SCED interval per interval—The duration of the portion of the SCED interval y within the 15-minute Settlement Interval. |
| K1 | none | The percentage tolerance for over-generation, 5%. |
| Q1 | MW | The MW tolerance for over-generation, 5 MW. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | A non-exempt, non-IRR Generation Resource. |
| y | none | An Emergency Base Point interval or SCED interval that overlaps the 15-minute Settlement Interval. |

6.6.5.1.2	Base Point Deviation Charge for Under Generation

(1)	ERCOT shall charge a QSE for a Generation Resource for under generation if the metered generation is below the lesser of:

(a)	95% of the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments; or

(b)	The average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments minus 5 MW.

(2)	The charge to each QSE for under-generation of each Generation Resource at each Resource Node Settlement Point for a given 15-minute Settlement Interval is calculated as follows:

BPDAMT q, p, r	=	Max (0, RTSPP p) * Min (1, KP) * Max {0, {Min [((1 – K2) * ¼( AABP q, p, r )) , ¼( AABP q, p, r – Q2 )] – TWTG q, p, r}}

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, p, r | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| TWTG q, p, r | MWh | Time-Weighted Telemetered Generation per QSE per Settlement Point per Resource—The telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| AABP q, p, r | MW | Adjusted Aggregated Base Point—The aggregated Base Point adjusted for Ancillary Service deployments of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| KP | None | The coefficient applied to the Settlement Point Price for under-generation charge, 1.0. |
| K2 | None | The percentage tolerance for under-generation, 5%. |
| Q2 | MW | The MW tolerance for under-generation, 5 MW. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | A non-exempt, non-IRR Generation Resource. |

6.6.5.2	IRR Generation Resource Base-Point Deviation Charge

(1)	ERCOT shall charge a QSE for an IRR a Base-Point deviation charge if the IRR metered generation is more than 10% above its Base Point and if the Base Point is 2 MW or more below the IRR’s HSL. The deviation charge may be refunded if the IRR shows, to ERCOT’s satisfaction, that the IRR was taking the necessary control actions to produce at levels equal to or less than the Base Point but was unable to comply solely due to increasing renewable energy input.  The IRR must always take the necessary control actions, in its capability, to comply with Base Point Dispatch Instructions if the Base Point is 2 MW or more below the IRR’s HSL as soon as practicable.

(2)	The charge to each QSE for non-excused over-generation of each IRR at each Resource Node Settlement Point, if the Real-Time metered generation is greater than the upper tolerance during a 15-minute Settlement Interval, is calculated as follows:

If AABP q, p, r > (HSL q, p, r – QIRR)

BPDAMT q, p, r =	0

Otherwise

BPDAMT q, p, r =	Max (0, RTSPP p) *

Max (0, TWTGq, p, r – ¼ *AABP q, p, r * (1 + KIRR))

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, p, r | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Resource Node p, for the 15-minute Settlement Interval. |
| TWTG q, p, r | MWh | Time-Weighted Telemetered Generation per QSE per Settlement Point per Resource—The telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| AABP q, p, r | MW | Adjusted Aggregated Base Point Generation per QSE per Settlement Point per Resource—The aggregated Base Point adjusted for Ancillary Service deployments, of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval. |
| HSL q, p, r | MW | High Sustainable Limit Generation per QSE per Settlement Point per Resource—The High Sustainable Limit of Generation Resource r represented by QSE q at Resource Node p for the hour that includes the 15-minute Settlement Interval. |
| KIRR |  | The percentage tolerance for over-generation of an IRR, 10%. |
| QIRR | MW | The threshold to test the adjusted aggregated Base Point against the HSL for an IRR, 2 MW. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | An IRR. |

6.6.5.3	Generators Exempt from Deviation Charges

Generation Resource Base Point deviation charges do not apply to RMR Units, Dynamically Scheduled Resources (except as described in Section 6.4.2.2, Output Schedules for Dynamically Scheduled Resources), or Qualifying Facilities that do not submit an Energy Offer Curve for the Settlement Interval.

6.6.5.4	Base Point Deviation Payment

ERCOT shall pay the Base-Point deviation charges collected from the QSEs representing Generation Resources to the QSEs representing Load based on Load Ratio Share. The payment to each QSE for a given 15-minute Settlement Interval is calculated as follows:

LABPDAMT q	=	(-1) * BPDAMTTOT * LRS q

Where:

BPDAMTTOT	=	ΣqBPDAMTQSETOT q

BPDAMTQSETOT q	=	ΣpΣrBPDAMT q, p, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LABPDAMT q | $ | Load-Allocated Base-Point Deviation Amount per QSE—QSE q’s share of the total charge for all the Generation Resource’s Base Point deviation, based on Load Ratio Share, for the 15-minute Settlement Interval. |
| BPDAMTTOT | $ | Base-Point Deviation Amount Total—The total of Base-Point Deviation Charges to all QSEs for all Generation Resources, for the 15-minute Settlement Interval. |
| BPDAMTQSETOT q | $ | Base-Point Deviation Amount QSE Total per QSE—The total of Base-Point Deviation Charges to QSE q for all Generation Resources represented by this QSE, for the 15-minute Settlement Interval. |
| BPDAMT q, p, r | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval. |
| LSR q | none | The Load Ratio Share calculated for QSE q for the 15-minute Settlement Interval. See Section 6.6.2.2, QSE Load Ratio Share for a 15-Minute Settlement Interval. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | A Generation Resource. |

6.6.6	Reliability Must-Run Settlement

6.6.6.1	RMR Standby Payment

(1)	The Standby Payment for RMR Service is paid to each QSE representing an RMR Unit for each RMR Unit for each contracted hour under performance requirements set forth in Attachment F to Section 22 and other performance requirements in these Protocols.  For Initial Settlement, the Standby Payment is the “Estimated Standby Cost” stated in the RMR Agreement.  For Final and True-Up Settlements, the Standby Payment is based on the RMR Unit’s actual Eligible Cost.

(2)	The Standby Payment to each QSE for each RMR Unit for each hour is calculated as follows:

RMRSBAMT q, r, h	=	(-1) * RMRSBPR q, r, h

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRSBAMT q, r, h | $ | Reliability Must Run Standby Payment per QSE per Resource by hour—The Standby Payment to QSE q for RMR Unit r, for the hour h. |
| RMRSBPR q, r, h | $ per hour | Reliability Must Run Standby Price per QSE per Resource by hour—The hourly standby cost for RMR Unit r represented by QSE q, for the hour h. See item (3) below. |
| q |  | A QSE. |
| r |  | An RMR Unit. |
| h |  | An hour. |

(3)	For the Initial Settlement and resettlements executed before True-up and before actual cost data is submitted, the standby price of an RMR Unit is the “Estimated Standby Cost” stated in the RMR Agreement.  For other resettlements, the standby price of an RMR Unit for each hour is calculated as follows:

RMRSBPR q, r, h	=	RMRMNFCOST q, r / MH q, r * (1 + RMRIF * RMRCRF q, r, h * RMRARF q, r, h)

Where:

RMR Capacity Reduction Factor

If (RMRTCAP q, r, h ≥ RMRCCAP q, r) then, RMRCRF q, r, h	=	1

Otherwise

RMRCRF q, r, h	=	Max (0, 1 – 2 * (RMRCCAP q, r– RMRTCAP q, r, h)/RMRCCAP q, r)

RMR Availability Reduction Factor

If (RMRHREAF q, r, h ≥ RMRTA q, r) then, RMRARF q, r, h	=	1

Otherwise

RMRARF q, r, h	=	Max (0, 1 - (RMRTA q, r - RMRHREAF q, r, h) * 2)

RMR Hourly Rolling Equivalent Availability Factor

If (RMREH q, r, h < 4380)

RMRHREAF q, r, h	=	1

Otherwise

RMRHREAF q, r, h	=	(Σhhr=h−4379RMRACAP q, r, hr)

/ (4380 * RMRCCAP q, r)

RMR Available Capacity by hour

RMRACAP q, r, h	=	Min (HSL q, r, h, RMRCAP q, r, h, RMRTCAP q, r, h, RMRCCAP q, r)

RMR Actual Capacity by hour

If (Σy(BP q, r, y, h * TLMP y, h / 3600) < HSL q, r, h)

RMRCAP q, r, h	=	HSL q, r, h

Otherwise

If (Σ4i=1RTMG q, r, i, h ≥ (0.98 * HSL q, r, h))

RMRCAP q, r, h	=	HSL q, r, h

Otherwise

RMRCAP q, r, h	=	 Σ4i=1RTMG q, r, i, h)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRSBPR q, r, h | $ per hour | Reliability Must Run Standby Price per QSE per Resource by hour—The Standby Price for RMR Unit r represented by QSE q for the hour h. |
| RMRARF q, r, h | none | Reliability Must Run Availability Reduction Factor per QSE per Resource by hour—The availability reduction factor of RMR Unit r represented by QSE q, for the hour h. |
| RMRCRF q, r, h | none | Reliability Must Run Capacity Reduction Factor per QSE per Resource by hour—The capacity reduction factor of the RMR Unit, for the hour. |
| RMRCCAP q, r | MW | Reliability Must Run Contractual Capacity per QSE per Resource—The capacity of RMR Unit r represented by QSE q as specified in the RMR Agreement. |
| RMRTCAP q, r, h | MW | Reliability Must Run Testing Capacity by hour—The testing capacity of RMR Unit r represented by QSE q, for the hour h. |
| RMRTA q, r | none | Reliability Must Run Target Availability per QSE per Resource—The Target Availability of RMR Unit r represented by QSE q, as specified in the RMR Agreement and divided by 100 to convert a percentage to a fraction. |
| RMRHREAF q, r, h | none | Reliability Must Run Hourly Rolling Equivalent Availability Factor per QSE per Resource by hour—The equivalent availability factor of RMR Unit r represented by QSE q over 4380 hours, for the hour h. |
| RMREH q, r, h | none | Reliability Must Run Elapsed number of Hours per QSE per Resource by hour—The number of the elapsed hours of the term of the RMR Agreement for RMR Unit r represented by QSE q, for the hour h. |
| RMRACAP q, r, h | MW | Reliability Must Run Available Capacity per QSE per Resource by hour—The available capacity of RMR Unit r represented by QSE q, for the hour h. |
| RMRMNFC q, r | $ | Reliability Must Run Monthly Non-Fuel Cost per QSE per Resource—The actual non-fuel Eligible Cost of RMR Unit r represented by QSE q, for the month. |
| MH q, r | hour | Number of Hours in the Month per QSE per Resource—The total number of hours of the month, when RMR Unit r represented by QSE q is under an RMR Agreement. |
| RMRIF | none | Reliability Must Run Incentive Factor—The Incentive Factor of RMR Units under RMR Agreement. |
| RTMG q, r , i, h | MWh | Real-Time Metered Generation per QSE per Resource per interval by hour—The metered generation of RMR Unit r represented by QSE q in Real-Time at the Settlement Point (Resource Node), for the 15-minute Settlement Interval i of the hour h. |
| RMRARF q, r, h | none | Reliability Must Run Availability Reduction Factor per QSE per Resource by hour—The availability reduction factor of RMR Unit r represented by QSE q, as calculated for the hour h. |
| HSL q, r, h | MW | High Sustainable Limit per QSE per Resource by hour—The High Sustainable Limit of RMR Unit r represented by QSE q, for the hour h. |
| RMRCAP q, r, h | MW | Reliability Must Run Actual Capacity per QSE per Resource by hour—The actual capacity of RMR Unit r represented by QSE q, for the hour h. |
| BP q, r, y, h | MW | Base Point per QSE per Resource per interval by hour—The Base Point of RMR Unit r represented by QSE q, for the SCED interval y of the hour h. |
| TLMP y, h | second | Duration of SCED interval per interval—The duration of the portion of the SCED interval y in the hour h. |
| q | none | A QSE. |
| r | none | An RMR Unit. |
| h | none | An hour (a negative value denotes an hour before the given hour). |
| hr | none | The index for a given hour and all the previous 4379 hours. |
| i | none | A 15-minute Settlement Interval. |
| y | none | A SCED interval in the Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |

(4)	The total of the Standby Payments to each QSE for all RMR Units represented by this QSE for a given hour is calculated as follows:

RMRSBAMTQSETOT q	=	ΣrRMRSBAMT q, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRSBAMTQSETOT q | $ | Reliability Must Run Standby Amount QSE Total per QSEThe total of the Standby Payments to QSE q for all RMR Units represented by this QSE for the hour. |
| RMRSBAMT q, r | $ | Reliability Must Run Standby Payment per QSE per Resource—The Standby Payment to QSE q for RMR Unit r, for the hour. |
| q | none | A QSE. |
| r | none | An RMR Unit. |

6.6.6.2	RMR Payment for Energy

(1)	Payment for energy on the Initial Settlement and settlements executed before True-up and before actual cost data is submitted must be calculated using the estimated input/output curve and startup fuel as specified in the RMR Agreement, the actual energy produced and the Fuel Index Price.  The payment for energy for all other settlements must be based on actual fuel costs for the RMR Unit.  The payment for energy for each hour is calculated as follows:

RMREAMT q, r, h	=	(FIP * RMRSUFQ q, r / RMRH q, r) * RMRSUFLAG q, r, h + Σ4i=1((FIP * RMRHR q, r, i, h + RMRVCC q, r) * RTMG q, r, i, h)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMREAMT q, r, h | $ | Reliability Must Run Energy Amount per QSE per Resource by hour—The energy payment to QSE q for RMR Unit r, for the hour h. |
| FIP | $/MMBtu | Fuel Index Price—The Fuel Index Price for the Operating Day. |
| RMRSUFQ q, r | MMBtu | Reliability Must Run Startup Fuel Quantity per QSE per ResourceThe Estimated Startup Fuel specified in the RMR Agreement for RMR Unit r represented by QSE q. |
| RMRH q, r | hour | Reliability Must Run Hours—The number of hours during which RMR Unit r represented by QSE q is instructed On-Line for the Operating Day. |
| RMRSUFLAG q, r, h | none | Reliability Must Run Startup Flag per QSE per Resource by hour—The number that indicates whether or not the startup fuel cost of RMR Unit r represented by QSE q is allocated to the hour h. Its value is 1 if the startup fuel cost is allocated; otherwise, its value is 0. |
| RMRHR q, r, i, h | MMBtu /MWh | Reliability Must Run Heat Rate per QSE per Resource by Settlement Interval by hour—The multiplier determined based on the input/output curve and the Real-Time generation of RMR Unit r represented by QSE q, for the 15-minute Settlement Interval i in the hour h. |
| RMRVCC q, r | $/MWh | Reliability Must Run Variable Cost Component per QSE per Resource—The monthly cost component that is used to adjust the energy cost calculation to reflect the actual fuel costs of RMR Unit r represented by QSE q. The value is initially set to zero. For resettlements, see item (2) below. |
| RTMG q, r, i, h | MWh | Real-Time Metered Generation per QSE per Resource by Settlement Interval by hour— The Real-Time energy from RMR Unit r represented by QSE q, for the 15-minute Settlement Interval i in the hour h. |
| q | none | A QSE. |
| r | none | An RMR Unit. |
| i | none | A 15-minute Settlement Interval. |
| h | none | An Operating Hour. |

(2)	If the RMR actual fuel cost is filed in accordance with the timeline in these Protocols, the monthly RMR variable cost component is calculated for the subsequent resettlements as follows:

RMRVCC q, r	=	(RMRMFCOST q, r - ΣhRMREAMT q, r, h, Estimated) / (ΣiRTMG q, r, i)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRVCC q, r | $/MWh | Reliability Must Run Variable Cost Component per QSE per Resource—The monthly cost component that is used to adjust the energy cost calculation to reflect the actual fuel costs of RMR Unit r represented by QSE q. |
| RMRMFCOST q, r | $ | Reliability Must Run Monthly actual Fuel Cost per QSE per Resource—The monthly actual fuel cost of RMR Unit r represented by QSE q, for the month. |
| RMREC q, r, h, Estimated | $ | Reliability Must Run Energy Cost per QSE per Resource per hour estimated—The estimated energy cost of RMR Unit r represented by QSE q, for the hour h. |
| RTMG q, r, i | MWh | Real-Time Metered Generation per QSE per Resource by Settlement Interval—The Real-Time energy from RMR Unit r represented by QSE q for the 15-minute Settlement Interval i. |
| q | none | A QSE. |
| r | none | An RMR Unit. |
| h | none | An hour in the month. |
| i | none | A 15-minute Settlement Interval in the month. |

(3)	The total of the payments for energy to each QSE for all RMR Units represented by this QSE for a given hour is calculated as follows:

RMREAMTQSETOT q	=	ΣrRMREAMT q, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMREAMTQSETOT q | $ | Reliability Must Run Energy Amount QSE Total per QSEThe total of the energy payments to QSE q for all RMR Units represented by this QSE for the hour. |
| RMREAMT q, r | $ | Reliability Must Run Energy Amount per QSE per Resource by hour—The energy payment to QSE q for RMR Unit r, for the hour. |
| q | none | A QSE. |
| r | none | An RMR Unit. |

6.6.6.3	RMR Adjustment Charge

(1)	Each QSE that represents an RMR Unit shall pay a charge designed to recover the net total revenues from RUC settlements, and from Real-Time settlements received by that QSE for all RMR Units that it represents, except that the charge does not include net revenues received by the QSE for the RMR standby payments calculated under Section 6.6.6.1, RMR Standby Payment, and the RMR energy payments calculated under Section 6.6.6.2, RMR Payment for Energy.

(2)	The charge for each QSE representing an RMR Unit for a given Operating Hour is calculated as follows:

RMRAAMT q	=	(-1) * ΣpΣr(Σ4i=1 RTEIAMTq, p, i  + Σ4i=1EMREAMT q, p, r, i + RUCMWAMT q, p, r + RUCCBAMT q, p, r + RUCDCAMT q, p, r + Σ4i=1VSSEAMT q, p, r, i + Σ4i=1VSSVARAMT q, r, i)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRAAMT q | $ | RMR Adjustment Charge per QSE—The charge to QSE q for all RMR Units represented by this QSE, for the revenues received for the same RMR Units from RUC settlements and Real-Time settlements, for the hour. |
| RTEIAMTq, p, i | $ | Real-Time Energy Imbalance Amount per QSE per Settlement Point—The payment or charge to QSE q for the Real-Time Energy Imbalance at Settlement Point p, for the 15-minute Settlement Interval. |
| EMREAMT q, p, r, i | $ | Emergency Energy Amount per QSE per Settlement Point per unit per interval—The payment to QSE q for the additional energy produced by RMR Unit r at Resource Node p in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval i. |
| RUCMWAMT q, p, r | $ | RUC Make-Whole Amount per QSE per Settlement Point per unit—The amount calculated for RMR Unit r committed in RUC at Resource Node p to make whole the startup and minimum energy cost of this unit, for the hour. See Section 5.7.1, RUC Make-Whole Payment. |
| RUCCBAMT q, r | $ | RUC Clawback Charge per QSE per unit—The RUC Clawback Charge to QSE q for RMR Unit r, for the hour. See Section 5.7.2, RUC Clawback Charge. |
| RUCDCAMT q, p, r | $ | RUC Decommitment Amount per QSE per Settlement Point per unit—The amount calculated for RMR Unit r at Resource Node p represented by QSE q due to ERCOT de-commitment, for the hour. |
| VSSEAMT q, p, r, i | $ | Voltage Support Service Energy Amount per QSE per Settlement Point per unit per interval —The compensation to QSE q for ERCOT-directed power reduction from RMR Unit r at Resource Node p to provide VSS, for the 15-minute Settlement Interval i. |
| VSSVARAMT q, r, i | $ | Voltage Support Service var Amount per QSE per Unit—The payment to QSE q for the VSS provided by RMR Unit r, for the 15-minute Settlement Interval i. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | An RMR Unit. |
| i | none | A 15-minute Settlement Interval in the hour. |

6.6.6.4	RMR Charge for Unexcused Misconduct

(1)	If a Misconduct Event, as defined in the RMR Agreement, is not excused as provided in the RMR Agreement, then ERCOT shall charge the QSE that represents the RMR Unit an unexcused misconduct amount of $10,000 for each unexcused Misconduct Event as follows:

RMRNPAMT q, r	=	$10,000

The above variable is defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRNPAMT q, r | $ | Reliability Must Run Unexcused Misconduct Charge per QSE per Resource—The charge to QSE q for the unexcused Misconduct Event of RMR Unit r for an Operating Day. |
| q | None | A QSE. |
| r | none | An RMR Unit. |

(2)	The total of the charges to each QSE for unexcused Misconduct Events of all RMR Units represented by this QSE for a given Operating Day is calculated as follows:

RMRNPAMTQSETOT q	=	ΣrRMRNPAMT q, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RMRNPAMTQSETOT q | $ | Reliability Must Run Unexcused Misconduct Amount QSE Total per QSEThe total of the charges to QSE q for unexcused Misconduct Events of the RMR Units represented by this QSE for the Operating Day. |
| RMRNPAMT q, r | $ | Reliability Must Run Unexcused Misconduct Charge per QSE per Resource—The charge to QSE q for the unexcused Misconduct Event of RMR Unit r for the Operating Day. |
| q | none | A QSE. |
| r | none | An RMR Unit. |

6.6.6.5	RMR Service Charge

The total RMR cost for all RMR Units less the amount received from Day-Ahead Market, RUC processes, Real-Time operations and Ancillary Service markets for all RMR Units is allocated to the QSEs representing loads based on Load Ratio Share.  The RMR Service charge to each QSE for a given hour is calculated as follows:

LARMRAMT q	=	(-1) * (RMRSBAMTTOT + RMREAMTTOT 
+ RMRAAMTTOT + Σ4i=1DARMRCHAMTTOT + RMRNPAMTTOT / H) * HLRS q

Where:

RMR Standby Amount Total

RMRSBAMTTOT	=	ΣqRMRSBAMTQSETOT q

RMR Energy Amount Total

RMREAMTTOT	=	ΣqRMREAMTQSETOT q

RMR Adjustment Charge Total

RMRAAMTTOT	=	ΣqRMRAAMT q

RMR Non-Performance Amount Total

RMRNPAMTTOT	=	ΣqRMRNPAMTQSETOT q

Day-Ahead RMR Unit Charge Total

DARMRCHAMTTOT	=	ΣqΣpΣr DARMRCHAMTQSETOT q

ΣqΣpΣr

The above variables are defined as follows:

| Variable |  | Unit |  | Definition |
| --- | --- | --- | --- | --- |
| LARMRAMT q |  | $ |  | Load-Allocated Reliability Must Run Amount per QSE—The amount charged to QSE q based on its Load Ratio Share of the difference between the amount paid to all QSEs for RMR Service under this Section 6.6.6, Reliability Must Run Settlement, and the amount that would have been paid to the QSEs for the same RMR Units if they were not providing RMR Service under the other parts of this Section, Section 5, Transmission Security Analysis and Reliability Unit Commitment, and Section 4, Day-Ahead Operations, for the hour. |
| RMRSBAMTTOT |  | $ |  | RMR Standby Amount Total—The total of the standby payments to all QSEs for all RMR Units, for the hour. |
| RMREAMTTOT |  | $ |  | RMR Energy Amount Total—The total of the energy cost payments to all QSEs for all RMR Units, for the hour. |
| RMRAAMTTOT |  | $ |  | RMR Adjusted Amount Total—The total of the adjusted amounts from all QSEs representing RMR Units for the revenues received for these units from RUC, Real-Time Operations and Ancillary Service Markets, for the hour. |
| DARMRCHAMTTOT |  | $ |  | Day-Ahead RMR Unit Charge Total - The total of the Day-Ahead RMR Unit Charge to all QSEs for all RMR Units for the hour. |
| RMRNPAMTTOT |  | $ |  | RMR Non-Performance Amount Total—The total of the charges to all QSEs for unexcused misconduct events of all RMR Units, for the Operating Day. |
| HLRS q |  | none |  | The hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| RMRSBAMTQSETOT q |  | $ |  | Reliability Must Run Standby Amount QSE Total per QSEThe total of the Standby Payments to QSE q for the RMR Units represented by the same QSE for the hour. |
| RMREAMTQSETOT q |  | $ |  | Reliability Must Run Energy Amount QSE Total per QSEThe total of the energy payments to QSE q for the RMR Units represented by the same QSE for the hour. |
| RMRAAMT q |  | $ |  | RMR Adjusted Amount per QSE—The adjustment from QSE q standby payments and energy payments for all RMR Units represented by this QSE, for the revenues received for the same RMR Units from RUC, Real-Time Operations and Ancillary Service Markets, for the hour. |
| RMRNPAMTQSETOT q |  | $ |  | Reliability Must Run Unexcused Misconduct Amount QSE Total per QSEThe total of the charges to QSE q for unexcused Misconduct Events of the RMR Units represented by the same QSE for the Operating Day. |
| DARMRCHAMTQSETOT q |  | $ |  | Day-Ahead RMR Unit Charge QSE Total per QSEThe total of the Day-Ahead RMR Unit Charge to QSE q for the DAM-committed RMR Units represented by this QSE for the hour. |
| q |  | none |  | A QSE. |
| p |  | none |  | A Resource Node Settlement Point. |
| r |  | none |  | An RMR Unit. |
| i |  | none |  | A 15-minute Settlement Interval in the hour. |
| H |  | none |  | The number of hours of the Operating Day. |

6.6.7	Voltage Support Settlement

6.6.7.1	Voltage Support Service Payments

(1)	All other Generation Resources shall be eligible for compensation for Reactive Power production in accordance with Section 6.5.7.7, Voltage Support Service, only if ERCOT issues a Dispatch Instruction that results in the following unit operation:

(a)	When ERCOT instructs the Generation Resource to exceed its URL and the Generation Resource provides additional Reactive Power, then ERCOT shall pay for the additional Reactive Power provided at a price that recognizes the avoided cost of reactive support Resources on the transmission network.

(b)	Any real power reduction directed by ERCOT through Verbal Dispatch Instructions to provide for additional reactive capability for voltage support must be compensated as a lost opportunity payment

(2)	The payment for a given 15-minute Settlement Interval to each QSE representing a Generation Resource that operates in accordance with an ERCOT Dispatch Instruction is calculated as follows:

(a)	Depending on the Dispatch Instruction, payment for Volt Amps Reactive (var):

If VSSVARLAG q, r > 0

VSSVARAMT q, r	=	(-1) * VSSVARPR * VSSVARLAG q, r

If VSSVARLEAD q, r > 0

VSSVARAMT q, r	=	(-1) * VSSVARPR * VSSVARLEAD q, r

Where:

VSSVARLAG q, r	=	Max [0, Min (¼ * VSSVARIOL q, r, RTVAR q, r) – (¼ * URLLAG q, r)]

VSSVARLEAD q, r	=	Max {0, [(¼ * URLLEAD q, r ) – Max ((¼ * VSSVARIOL q, r), RTVAR q, r)]}

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| VSSVARAMT q, r | $ | Voltage Support Service var Amount per QSE per Generation Resource - The payment to QSE q for the VSS provided by Generation Resource r, for the 15-minute Settlement Interval. |
| VSSVARPR | $/Mvarh | Voltage Support Service var Price - The price for instructed Mvar beyond a Generation Resource’s URL currently is $2.65/Mvarh (based on $50.00/installed kvar). |
| VSSVARLAG q, r | Mvarh | Voltage Support Service var Lagging per QSE per Generation Resource - The instructed portion of the Reactive Power above the Generation Resource’s lagging URL for Generation Resource r represented by QSE q, for the 15-minute Settlement Interval. |
| VSSVARLEAD q, r | Mvarh | Voltage Support Service var Leading per QSE per Generation Resource - The instructed portion of the Reactive Power below the Generation Resource’s leading URL for Generation Resource r represented by QSE q, for the 15-minute Settlement Interval. |
| VSSVARIOL q, r | Mvar | Voltage Support Service var Instructed Output Level per QSE per Generation Resource—The instructed Reactive Power output level of Generation Resource r represented by QSE q, lagging Reactive Power if positive and leading Reactive Power if negative, for the 15-minute Settlement Interval. |
| RTVAR q, r | MVARh | Real-Time var per QSE per Resource—The netted Reactive Energy measured for Generation Resource r represented by QSE q, for the 15-minute Settlement Interval. |
| URLLAG q, r | Mvar | Unit Reactive Limit Lagging per QSE per Resource—The Unit Reactive Limit for lagging Reactive Power of the Generation Resource r represented by QSE q as determined in accordance with these Protocols. Its value is positive. |
| URLLEAD q, r | Mvar | Unit Reactive Limit Leading per QSE per Resource—The Unit Reactive Limit for leading Reactive Power of the Generation Resource r represented by QSE q as determined in accordance with these Protocols. Its value is negative. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(b)	The lost opportunity payment, if applicable:

VSSEAMT q, r		=	Max (0, RTSPP * Max (0, (HSL q, r * ¼ - RTMG q, r)) – (RTICHSL q, r – RTAIEC q, r *                        (RTMG q, r - LSL q, r * ¼)))

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| VSSEAMT q, r | $ | Voltage Support Service Energy Amount per QSE per Generation Resource—The lost opportunity payment to QSE q for ERCOT-directed VSS from Generation Resource g for the 15-minute Settlement Interval. |
| RTMG q, r | MWh | Real-Time Metered Generation per QSE per Resource—The Real-Time metered generation of Generation Resource r represented by QSE q, for the 15-minute Settlement Interval. |
| RTSPP | $ | Real-Time Settlement Point Price—The Real-Time Settlement Point Price at the Resource Node for the 15-minute Settlement Interval. - |
| RTAIEC q, r | $/MWh | Real-Time Average Incremental Energy Cost per QSE per Resource—The average incremental cost to operate (not subject to cost cap) the Generation Resource r represented by QSE q from its LSL to its metered MW output, for the 15-minute Settlement Interval. |
| RTICHSL q, r | $ | Real-Time Incremental Cost corresponding with HSL per QSE per Resource—The incremental cost to operate (not subject to cost cap) Generation Resource r represented by QSE q from its LSL to its HSL, for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(3)	The total of the payments to each QSE for the Compensated Reactive Support and ERCOT-directed power reduction to provide VSS for a given 15-minute Settlement Interval is calculated as follows:

VSSAMTQSETOT q	=	r(VSSVARAMT q, r + VSSEAMT q,r)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| VSSAMTQSETOT q | $ | Voltage Support Service Amount QSE Total per QSEThe total of the payments to QSE q for providing VSS for the 15-minute Settlement Interval. |
| VSSVARAMT q, r | $ | Voltage Support Service var Amount per QSE per Generation Resource—The payment to QSE q for the VSS provided by the Resources r, for the 15-minute Settlement Interval. |
| VSSEAMT q, p, r | $ | Voltage Support Service Energy Amount per QSE per Settlement Point per Generation Resource—The lost opportunity payment to QSE q for ERCOT-directed VSS from Generation Resource r for the 15-minute Settlement Interval for the 15-minute Settlement Interval. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

6.6.7.2	Voltage Support Charge

ERCOT shall charge each QSE representing LSEs the total payment for Voltage Support Service as specified in Section 6.6.7.1, Voltage Support Service Payments, based on a Load Ratio Share. The charge to each QSE for a given 15-minute Settlement Interval is calculated as follows:

LAVSSAMT q	=	(-1) * VSSAMTTOT * LRS q

Where:

VSSAMTTOT	=	ΣqVSSAMTQSETOT q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LAVSSAMT q | $ | Load-Allocated Voltage Support Service Amount per QSE—The charge to QSE q for VSS, for the 15-minute Settlement Interval. |
| VSSAMTTOT | $ | Voltage Support Service Amount Total—The total of payments to all QSEs providing VSS, for the 15-minute Settlement Interval. |
| VSSAMTQSETOT q | $ | Voltage Support Service Amount QSE Total per QSEThe total of the payments to QSE q for providing VSS for the 15-minute Settlement Interval. |
| LRS q | none | The Load Ratio Share calculated for QSE q for the 15-minute Settlement Interval. See Section 6.6.2.2, QSE Load Ratio Share for a 15-Minute Settlement Interval. |
| q | none | A QSE. |

6.6.8	Black Start Capacity

6.6.8.1	Black Start Capacity Payment

(1)	ERCOT shall pay an hourly standby fee to QSEs representing Black Start Resources.  This standby fee is determined through a competitive annual bidding process, with an adjustment for reliability based on a 6-month rolling availability equal to 85% in accordance with the Black Start Agreement in Section 22, ERCOT Protocols Agreements.

(2)	ERCOT shall pay a Black Start standby payment to each QSE for each Black Start Resource.  The payment for each hour is calculated as follows:

BSSAMT q, r, h	=	(-1) * BSSPR q, r * BSSARF q, r, h

Where:

Black Start Service Availability Reduction Factor

If (BSSHREAF q, r, h  0.85)

BSSARF q, r, h 	= 	1

Otherwise

BSSARF q, r, h 	= 	Max (0, 1 - (0.85 - BSSHREAF q, r, h) * 2)

Black Start Service Hourly Rolling Equivalent Availability Factor

If (BSSEH q, r, h < 4380)

BSSHREAF q, r, h	=	1

Otherwise

BSSHREAF q, r, h	=	(Σhhr=h−4379 BSSAFLAG hr) / 4380

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BSSAMT q, r, h | $ | Black Start Service Amount per QSE per Resource by hour—The standby payment to QSE q for the Black Start Service (BSS) provided by Resource r, for the hour h. |
| BSSPR q, r | $ per hour | Black Start Service Price per QSE per Resource—The standby price of BSS Resource r represented by QSE q, as specified in the BSS Agreement. |
| BSSARF q, r, h | none | Black Start Service Availability Reduction Factor per QSE per Resource by hour—The availability reduction factor of Resource r represented by QSE q under the BSS Agreement, for the hour h. |
| BSSHREAF q, r, h | none | Black Start Service Hourly Rolling Equivalent Availability Factor per QSE per Resource by hour—The equivalent availability factor of the BSS Resource r represented by QSE q over 4380 hours, for the hour h. |
| BSSEH q, r, h | none | Black Start Service Elapsed number of Hours per QSE per Resource by hour—The number of the elapsed hours of BSS Resource r represented by QSE q since the beginning of the BSS Agreement, for the hour h. |
| BSSAFLAG q, r, h | none | Black Start Service Availability Flag per QSE per Resource by hour—The flag of the availability of BSS Resource r represented by QSE q, 1 for available and 0 for unavailable, for the hour h. |
| q | none | A QSE. |
| r | none | A BSS Resource. |
| h | none | An hour. |
| hr | none | The index of a given hour and the previous 4379 hours. |

(3)	The total of the payments to each QSE for all BSS Resources represented by this QSE for a given hour is calculated as follows:

BSSAMTQSETOT q	=	ΣrBSSAMT q, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BSSAMTQSETOT q | $ | Black Start Service Amount QSE Total per QSEThe total of the payments to QSE q for BSS provided by all the BSS Resource represented by this QSE for the 15-minute Settlement Interval. |
| BSSAMT q, r | $ | Black Start Service Amount per QSE per Resource—The standby payment to QSE q for the Black Start Service (BSS) provided by Resource r, for the hour. |
| q | none | A QSE. |
| r | none | A BSS Resource. |

6.6.8.2	Black Start Capacity Charge

ERCOT shall allocate the total Black Start Service Capacity payment to the QSEs representing Loads based on a Load Ratio Share.  The resulting charge to each QSE for a given hour is calculated as follows:

LABSSAMT q	=	(-1) * BSSAMTTOT * HLRS q

Where:

BSSAMTTOT	=	ΣqBSSAMTQSETOT q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LABSSAMT q | $ | Load-Allocated Black Start Service Amount per QSE—The charge allocated to QSE q for the Black Start Service, for the hour. |
| BSSAMTQSETOT q | $ | Black Start Service Amount QSE Total per QSE—The Black Start Service payment to QSE q for BSS Resource r, for the hour. |
| HLRS q | none | The hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| q | none | A QSE. |

6.6.9	Emergency Operations Settlement

Due to Emergency Conditions, additional compensation for each Generation Resource for which ERCOT provides an Emergency Base Point may be awarded to the QSE representing the Generation Resource. If the Emergency Base Point is higher than the SCED Base Point immediately before the Emergency Condition and the Settlement Point Price at the Resource Node is lower than the Generation Resource’s Energy Offer Curve price at the Emergency Base Point, ERCOT shall pay the QSE additional compensation for the additional energy above the SCED Base Point.

6.6.9.1	Payment for Emergency Power Increase directed by ERCOT

(1)	If the Emergency Base Point issued to a Generation Resource is higher than the SCED Base Point immediately before the Emergency Condition, then ERCOT shall pay the QSE an additional compensation for the Resource at its Resource Node Settlement Point.  The payment for a given 15-minute Settlement Interval is calculated as follows:

EMREAMT q, p, r	=	(-1) * EMREPR q, p, r * EMREq, p, r

Where:

EMREPR q, p, r	=	Max (0, EBPWAPR q, p, r – RTSPP p)

EBPWAPR q, p, r	=	Σy(EBPPR q, p, r, y * EBP q, p, r, y * TLMP y) /

Σy(EBPq, p, r, y * TLMP y)

EMRE q, p, r	=	Max (0, Min (Σy(EBP q, p, r, y * TLMPy / 3600), RTMG q, p, r) – ¼ * BP q, p, r)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| EMREAMT q, p, r | $ | Emergency Energy Amount per QSE per Settlement Point per Resource—The payment to QSE q as additional compensation for the additional energy produced by Generation Resource r at Resource Node p in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval. |
| EMREPR q, p, r | $/MWh | Emergency Energy Price per QSE per Settlement Point per Resource—The compensation rate for the additional energy produced by Generation Resource r at Resource Node p represented by QSE q in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval. |
| EMRE q, p, r | MWh | Emergency Energy per QSE per Settlement Point per Resource—The additional energy produced by Generation Resource r at Resource Node p represented by QSE q in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval. |
| EBPWAPR q, p, r | $/MWh | Emergency Base Point Weighted Average Price per QSE per Settlement Point per Resource—The weighted average of the energy prices corresponding with the Emergency Base Points on the Energy Offer Curve for Resource r at Resource Node p represented by QSE q, for the 15-minute Settlement Interval. |
| BP q, p, r | MW | Base Point per QSE per Settlement Point per Resource—The Base Point of Resource r at Resource Node p represented by QSE q from the SCED prior to the Emergency Condition. |
| EBP q, p, r, y | MW | Emergency Base Point per QSE per Settlement Point per Resource by interval—The Emergency Base Point of Resource r at Resource Node p represented by QSE q for the Emergency Base Point interval or SCED interval y. If a Base Point instead of an Emergency Base Point is effective during the interval y, its value equals the Base Point. |
| EBPPR q, p, r, y | $/MWh | Emergency Base Point Price per QSE per Settlement Point per Resource by interval—The Real-Time energy offer price corresponding with the Emergency Base Point of Resource r at Resource Node p represented by QSE q, for the Emergency Base Point interval or SCED interval y. |
| RTSPP p | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval. |
| RTMG q, p, r | MWh | Real-Time Metered Generation per QSE per Settlement Point per Resource—The metered generation of Resource r at Resource Node p represented by QSE q in Real-Time for the 15-minute Settlement Interval. |
| TLMP y | second | Duration of Emergency Base Point interval or SCED interval per interval—The duration of the portion of the Emergency Base Point interval or SCED interval y within the 15-minute Settlement Interval. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | A Generation Resource. |
| y | none | An Emergency Base Point interval or SCED interval that overlaps the 15-minute Settlement Interval. |

(2)	The total additional compensation to each QSE for emergency power increases of Generation Resources for the 15-minute Settlement Interval is calculated as follows:

EMREAMTQSETOT q	=	ΣpΣrEMREAMT q, p, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| EMREAMTQSETOT q | $ | Emergency Energy Amount QSE Total per QSEThe total of the payments to QSE q as additional compensation for emergency power increases of the non-RMR Generation Resources represented by this QSE for the 15-minute Settlement Interval. |
| EMREAMT q, p, r | $ | Emergency Energy Amount per QSE per Settlement Point per Resource—The payment to QSE q as additional compensation for the additional energy produced by Generation Resource r at Resource Node p in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval. |
| q | None | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | A Generation Resource. |

6.6.9.2	Charge for Emergency Power Increases

Each QSE shall pay a charge for emergency power increases based on its Load Ratio Share of the total additional compensation for all Generation Resources that ERCOT provides Emergency Base Points higher than the SCED Base Point prior to the Emergency Condition. The charge to each QSE for a given 15-minute Settlement Interval is calculated as follows:

LAEMREAMT q	=	(-1) * EMREAMTTOT * LRS q

Where:

EMREAMTTOT	=	ΣqEMREAMTQSETOT q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LAEMREAMT q | $ | Load-Allocated Emergency Energy Amount per QSE—The QSE q’s Load-Allocated amount of the total payments for all the Generation Resources with Real-Time Emergency Base Points, for the 15-minute Settlement Interval. |
| EMREAMTTOT | $ | Emergency Energy Amount TotalThe total of the payments to all QSEs as additional compensation for emergency power increases of the Generation Resources for the 15-minute Settlement Interval. |
| EMREAMTQSETOT q | $ | Emergency Energy Amount QSE Total per QSEThe total of the payments to QSE q as additional compensation for emergency power increases of the Generation Resources represented by this QSE for the 15-minute Settlement Interval. |
| LSR q | none | The Load Ratio Share calculated for QSE q for the 15-minute Settlement Interval. See Section 6.6.2.2, QSE Load Ratio Share for a 15-Minute Settlement Interval. |
| q | none | A QSE. |

6.6.10	Real-Time Revenue Neutrality Allocation

(1)	ERCOT must be revenue-neutral in each Settlement Interval. Each QSE receives an allocated share, on a Load Ratio Share basis, of the net amount of:

(a)	Real-Time Energy Imbalance payments or charges under Section 6.6.3.1, Real-Time Energy Imbalance Payment or Charge at  a Resource Node;

(b)	Real-Time Energy Imbalance payments or charges under Section 6.6.3.2, Real-Time Energy Imbalance Payment or Charge at a Load Zone;

(c)	Real-Time Energy Imbalance payments or charges under Section 6.6.3.3, Real-Time Energy Imbalance Payment or Charges at a HUB;

(d)	Real-Time energy payments under Section 6.6.3.4, Real-Time Energy Payment for DC Tie Import;

(e)	Real-Time energy payments under Section 6.6.3.5, Payment for a Block Load Transfer Point;

(f)	Real-Time energy charge under Section 6.6.3.6, Charge for an Export Represented by a QSE under the Oklaunion Exemption;

(g)	Real-Time congestion payments or charges under Section 6.6.4, Real-Time Congestion Payment or Charge for Self Schedules;

(h)

Real-Time energy charges under Section 6.6.4.3, Real-Time Energy Charge for Energy Sale through Energy Trades;

(i)	Real-Time energy charges under Section 6.6.4.4, Real-Time Energy Charge for DC Tie Export represented by the QSE under Oklaunion Exemption; and

(j)	Real-Time payments or charges to the CRR Owners under Section 7.9.2,  Real-Time CRR Payments and Charges; and

(2)	The Real-Time Revenue Neutrality Allocation for each QSE for a given 15-minute Settlement Interval is calculated as follows:

LARTRNAMT q	=	(-1) * (RTEIAMTTOT + BLTRAMTTOT + RTBTBIMPAMTTOT + RTBTBEXPAMTTOT + RTCCAMTTOT +    RTOBLAMTTOT / 4 + RTOPTAMTTOT / 4 + RTOPTRAMTTOT /4) * LRS q

Where:

Total Real-Time Energy Imbalance payment (or charge) at Settlement Point (or Hub)

RTEIAMTTOT	=	ΣqRTEIAMTQSETOT q

Σq

Total Real-Time payment for Block Load Transfer Resources

BLTRAMTTOT	=	ΣqBLTRAMTQSETOT q

Σq

Total Real-Time payment for DC Tie Imports

RTBTBIMPAMTTOT	=	ΣqRTDCIMPAMTQSETOT q

Total Real-Time charge for DC Tie Exports (under “Oklaunion Exemption”)

RTBTBEXPAMTTOT	=	ΣqRTDCEXPAMTQSETOT q

Total Real-Time Congestion Payment or Charge for Self Schedules

RTCCAMTTOT	=	ΣqRTCCAMTQSETOT q

Σq

Total Real-Time payment or charge for PTP Obligations

RTOBLAMTTOT	=	ΣoRTOBLAMTOTOT o

Total Real-Time payment for PTP Options

RTOPTAMTTOT	=	ΣoRTOPTAMTOTOT o

Total Real-Time payment for PTP Options with Refund

RTOPTRAMTTOT	=	ΣoRTOPTRAMTOTOT o

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| LARTRNAMT q | $ | Load-Allocated Real-Time Revenue Neutrality Amount per QSE—The QSE q’s share of the total Real-Time revenue neutrality amount, for the 15-minute Settlement Interval. |
| RTEIAMTTOT q | $ | Real-Time Energy Imbalance Amount Total The Total net payments and charges for Real-Time Energy Imbalance at all Settlement Points (Resource, Load Zone, or Hub) for the 15-Minute Interval. |
| BLTRAMTTOT | $ | Block Load Transfer Resource Amount TotalThe total of the payments for energy delivered into the ERCOT System through BLT Points for the 15-minute Settlement Interval. |
| RTBTBIMPAMTTOT | $ | Real-Time DC Import Amount Total—The summation of payments for DC Tie import, for the 15-minute Settlement Interval. |
| RTDCEXPAMTTOT | $ | Real-Time DC Export Amount Total—The summation of charges to all QSE that are under the “Oklaunion Exemption” for DC Tie export, for the 15-minute Settlement Interval. |
| RTCCAMTTOT q | $ | Real-Time Energy Congestion Cost Amount TotalThe total net congestion payments and charges for all of the Self-Schedules for the 15-minute Settlement Interval. |
| RTOBLAMTTOT | $ | Real-Time Obligation Amount Total—The sum of all payments and charges for PTP Obligations settled in Real-Time, for the hour that includes the 15-minute Settlement Interval. |
| RTOPTAMTTOT | $ | Real-Time Option Amount Total—The sum of all payments for PTP Options settled in Real-Time, for the hour that includes the 15-minute Settlement Interval. |
| RTOPTRAMTTOT | $ | Real-Time Option with Refund Amount Total—The sum of all payments for PTP Options with Refund settled in Real-Time, for the hour that includes the 15-minute Settlement Interval. |
| RTEIAMTQSETOT q | $ | Real-Time Energy Imbalance Amount QSE Total per QSE The Total net payments and charges to the QSE q for Real-Time Energy Imbalance at all Settlement Points (Resource, Load Zone, or Hub) for the 15-Minute Interval. |
| BLTRAMTQSETOT q | $ | Block Load Transfer Resource Amount QSE Total per QSEThe total of the payments to QSE q for energy delivered into the ERCOT System through BLT Points for the 15-minute Settlement Interval. |
| RTBTBIMPAMTQSETOT q | $ | Real-Time DC Import Amount QSE Total per QSEThe total of the payments to QSE q for energy imported into the ERCOT System through DC Ties for the 15-minute Settlement Interval. |
| RTBTBEXPAMTQSETOT q | $ | Real-Time DC Export Amount QSE Total per QSEThe total of the charges to QSE q for energy exported from the ERCOT System through DC Ties for the 15-minute Settlement Interval. |
| RTCCAMTQSETOT q | $ | Real-Time Energy congestion Cost Amount QSE Total per QSE The total net congestion payments and charges to QSE q for its Self-Schedules for the 15-minute Settlement Interval. |
| RTOBLAMTOTOT o | $ | Real-Time Obligation Amount Owner Total per owner —The net of payments or charges for all the PTP Obligations, held by the CRR Owner o and settled in Real-Time, for the hour that includes the 15-minute Settlement Interval. See Section 7.9.2.1, Payments and Charges for PTP Obligations Settled in Real-Time, paragraph (2). |
| RTOPTAMTOTOT o | $ | Real-Time Option Amount Owner Total per owner—The total payment for all the PTP Options, held by the CRR Owner o and settled in Real-Time, for the hour that includes the 15-minute Settlement Interval. See Section 7.9.2.2, Payments for PTP Options Settled in Real-Time, paragraph (2). |
| RTOPTRAMTOTOT o | $ | Real-Time Option with Refund Amount Owner Total per owner —The payment for the PTP Options with Refund, held by the CRR Owner o and settled in Real-Time, for the hour that includes the 15-minute Settlement Interval. See Section 7.9.2.3, Payments for NOIE PTP Options with Refund Settled in Real-Time, paragraph (2). |
| LSR q | none | The Load Ratio Share calculated for QSE q for the 15-minute Settlement Interval. See Section 6.6.2.2, QSE Load Ratio Share for a 15-Minute Settlement Interval. |
| q | none | A QSE. |
| o | none | A CRR Owner. |

6.7	Real-Time Settlement Calculations for the Ancillary Services

6.7.1	Payments for Ancillary Service Capacity Sold in a Supplemental Ancillary Service Market

If a SASM is executed for one or more Operating Hours for any reason, ERCOT shall pay QSEs for their Ancillary Service Offers cleared in the SASM, based on the MCPC for that SASM and that service.  By service and by SASM, the payment to each QSE for a given Operating Hour is calculated as follows:

(1)	For Reg-Up, if applicable:

PCRUAMT q, m	=	(-1) * MCPCRU m * PCRU q, m

Where:

PCRU q, m	=	ΣrPCRUR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PCRUAMT q, m | $ | Procured Capacity for Reg-Up Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide Reg-Up, for the hour. |
| MCPCRU m | $/MW per hour | Market Clearing Price for Capacity for Reg-Up by market —The MCPC for Reg-Up from the market m, for the hour. |
| PCRU q, m | MW | Procured Capacity for Reg-Up by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Up, for the hour. |
| PCRUR r, q, m | MW | Procured Capacity for Reg-Up from Resource per Resource per QSE by market—The Reg-Up capacity quantity awarded to QSE q in the market m for Resource r for the hour. |
| m | none | A SASM. |

(2)	For Reg-Down, if applicable:

PCRDAMT q, m	=	(-1) * MCPCRD q, m * PCRD q, m

Where:

PCRD q, m	=	ΣrPCRDR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PCRDAMT q, m | $ | Procured Capacity for Reg-Down Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide Reg-Down, for the hour. |
| MCPCRD m | $/MW per hour | Market Clearing Price for Capacity for Reg-Down by market—The MCPC for Reg-Down from the market m, for the hour. |
| PCRD q, m | MW | Procured Capacity for Reg-Down by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Down, for the hour. |
| PCRDR r, q, m | MW | Procured Capacity for Reg-Down from Resource per Resource per QSE by market—The Reg-Down capacity quantity awarded to QSE q in the market m for Resource r for the hour |
| m | none | A SASM. |

(3)	For Responsive Reserve, if applicable:

PCRRAMT q, m	=	(-1) * MCPCRR m * PCRR q, m

Where:

PCRR q, m	=	ΣrPCRRR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PCRRAMT q, m | $ | Procured Capacity for Responsive Reserve Amount by QSE by market—The payment to QSE q for the Ancillary Service Offer cleared in the market m to provide Responsive Reserve, for the hour. |
| MCPCRR m | $/MW per hour | Market Clearing Price for Capacity for Responsive Reserve by market—The MCPC for Responsive Reserve from the market m, for the hour. |
| PCRR q, m | MW | Procured Capacity for Responsive Reserve by QSE by market—The portion of QSE q Ancillary Service Offers cleared in the market m to provide Responsive Reserve, for the hour. |
| PCRRR r, q, m | MW | Procured Capacity for Responsive Reserve from Resource per Resource per QSE by market—The Responsive Reserve capacity quantity awarded to QSE q in the market m for Resource r for the hour. |
| m | none | A SASM. |

(4)	For Non-Spin, if applicable:

PCNSAMT q, m	=	(-1) * MCPCNS m * PCNS q, m

Where:

PCNS q, m	=	ΣrPCNSR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PCNSAMT q, m | $ | Procured Capacity for Non-Spin Amount by QSE by market—The payment to QSE q for Ancillary Service Offer cleared in the market m to provide Non-Spin, for the hour. |
| MCPCNS m | $/MW per hour | Market Clearing Price for Capacity for Non-Spin by market—The MCPC for Non-Spin from the market m, for the hour. |
| PCNS q, m | MW | Procured Capacity for Non-Spin by QSE by market—The portion of QSE q’s Ancillary Service Offer cleared in the market m to provide Non-Spin, for the hour. |
| PCNSR r, q, m | MW | Procured Capacity for Non-Spin from Resource per Resource per QSE by market—The Non-Spin capacity quantity awarded to QSE q in the market m for Resource r for the hour. |
| m | none | A SASM. |

6.7.2	Charges for Ancillary Service Capacity Replaced Due to Failure to Provide

A charge to each QSE that fails on its Ancillary Service Supply Responsibility, whether or not a SASM is executed due to its failure to supply, is calculated based on the greatest of the MCPC in the DAM or any SASM for the same Operating Hour.  By service, the charge to each QSE for a given Operating Hour is calculated as follows:

(1)	For Reg-Up, if applicable:

RUFQAMT q	=	Maxm(MCPCRU m) * RUFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RUFQAMT q | $ | Reg-Up Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| MCPCRU m | $/MW per hour | Market Clearing Price for Capacity for Reg-Up by market—The MCPC for Reg-Up in the market m, for the hour. |
| RUFQ q | MW | Reg-Up Failure Quantity per QSE—QSE q total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(2)	For Reg-Down, if applicable:

RDFQAMT q	=	Maxm(MCPCRD m) * RDFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RDFQAMT q | $ | Reg-Down Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| MCPCRD m | $/MW per hour | Market Clearing Price for Capacity for Reg-Down by market—The MCPC for Reg-Down in the market m, for the hour. |
| RDFQ q | MW | Reg-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(3)	For Responsive Reserve, if applicable:

RRFQAMT q	=	Maxm(MCPCRR m) * RRFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RRFQAMT q | $ | Responsive Reserve Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Responsive Reserve, for the hour. |
| MCPCRR m | $/MW per hour | Market Clearing Price for Capacity for Responsive Reserve per market—The MCPC for Responsive Reserve in the market m, for the hour. |
| RRFQ q | MW | Responsive Reserve Failure Quantity per QSE - QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Responsive Reserve, for the hour. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(4)	For Non-Spin, if applicable:

NSFQAMT q	=	Maxm(MCPCNS m) * NSFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| NSFQAMT q | $ | Non-Spin Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Non-Spin, for the hour. |
| MCPCNS m | $/MW per hour | Market Clearing Price for Capacity for Non-Spin by market—The MCPC for Non-Spin in the market m, for the hour. |
| NSFQ q | MW | Non-Spin Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Non-Spin, for the hour. |
| m | none | The DAM or a SASM for the given Operating Hour. |

6.7.3	Adjustments to Cost Allocations for Ancillary Services Procurement

Each QSE, for which ERCOT purchases Ancillary Service capacity in the DAM and SASMs (if any), is charged for the QSE’s share of the net costs incurred for each service.  For each QSE, its share of the DAM costs has been calculated in Section 4.6.4, Settlement of Ancillary Services Procured in the DAM; its share of the net total costs incurred in both DAM and SASMs less its DAM charge is calculated in this section.

(1)	For Reg-Up, if applicable:

(a)	The net total costs for Reg-Up for a given Operating Hour is calculated as follows:

RUCOSTTOT	=	(-1) * (ΣmPCRUAMTTOT m + RUFQAMTTOT)

Where:

Total payment of DAM or SASM procured capacity for Reg-Up by market

PCRUAMTTOT m	=	ΣqPCRUAMT q, m

Total charge of failure on Ancillary Service Supply Responsibility for Reg-Up

RUFQAMTTOT	=	ΣqRUFQAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RUCOSTTOT | $ | Reg-Up Cost Total—The net total costs for Reg-Up for the hour. |
| PCRUAMTTOT m | $ | Procured Capacity for Reg-Up Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for Reg-Up, for the hour. |
| PCRUAMT q, m | $ | Procured Capacity for Reg-Up Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for Reg-Up, for the hour. |
| RUFQAMTTOT | $ | Reg-Up Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for Reg-Up, for the hour. |
| RUFQAMT q | $ | Reg-Up Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for Reg-Up for the Operating Hour is calculated as follows:

RUCOST q	=	RUPR * RUQ q

Where:

RUPR	=	RUCOSTTOT / RUQTOT

RUQTOT	=	ΣqRUQ q

RUQ q	=	RUONET q –  ΣmRUSQ q, m

RUONET q	=	(Σq(ΣmRUSQq,m + ΣmPCRUq,m – ΣmRURPq,m – RUFQq)) * HLRSq + RUCSq – RUCPq + ΣmRURPq,m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RUCOST q | $ | Reg-Up Cost per QSE—QSE q’s share of the net total costs for Reg-Up, for the hour. |
| RUPR | $/MW per hour | Reg-Up Price—The price for Reg-Up calculated based on the net total costs for Reg-Up, for the hour. |
| RUCOSTTOT | $ | Reg-Up Cost Total—The net total costs for Reg-Up for the hour. See item (a) above. |
| RUQTOT | MW | Reg-Up Quantity Total—The sum of every QSE’s portion of its net Ancillary Service Obligation that is not self-supplied with its Resource capacity in either DAM or any SASM, for the hour. |
| RUQ q | MW | Reg-Up Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation that is not self-supplied with its Resources capacity in either DAM or any SASM, for the hour. |
| RUONET q | MW | Reg-Up Obligation Net per QSE—The net Ancillary Service Obligation of QSE q, for the hour. |
| RUSQ q, m | MW | Reg-Up Supplied Quantity per QSE per market—The capacity for Reg-Up to be supplied with Resources represented by QSE q to meet its Ancillary Service Obligation and/or its Ancillary Service Trades, for the market m, for the hour. |
| PCRU q, m | MW | Procured Capacity for Reg-Up per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Up, for the hour. |
| RUFQ q | MW | Reg-Up Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| HLRS q |  | The hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| RUCS q | MW | Reg-Up Capacity Sale per QSE—The total Reg-Up capacity shown in Ancillary Service Trades with QSE q as a seller, for the hour. |
| RUCP q | MW | Reg-Up Capacity Purchase per QSE—The total Reg-Up capacity shown in Ancillary Service Trades with QSE q as a buyer, for the hour. |
| RURP q, m | MW | Reg-Up Replacement per QSE per market—The Reg-Up capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in the market m, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the Reg-Up for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTRUAMT q	=	RUCOST q – DARUAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRUAMT q | $ | Real-Time Reg-Up Amount per QSE—The adjustment to QSE q’s share of the costs for Reg-Up, for the hour. |
| RUCOST q | $ | Reg-Up Cost per QSE—QSE q’s share of the net total costs for Reg-Up, for the hour. |
| DARUAMT q | $ | Day-Ahead Reg-Up Amount per QSE—QSE q’s share of the DAM cost for Reg-Up, for the hour. |
| q | none | A QSE. |

(2)	For Reg-Down, if applicable:

(a)	The net total costs for Reg-Down for a given Operating Hour is calculated as follows:

RDCOSTTOT	=	(-1) * (ΣmPCRDAMTTOT m + RDFQAMTTOT)

Where:

Total payment of DAM or SASM procured capacity for Reg-Down by market

PCRDAMTTOT m	=	ΣqPCRDAMT q, m

Total charge of failure on Ancillary Service Supply Responsibility for Reg-Down

RDFQAMTTOT	=	ΣqRDFQAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RDCOSTTOT | $ | Reg-Down Cost Total—The net total costs for Reg-Down for the hour. |
| PCRDAMTTOT m | $ | Procured Capacity for Reg-Down Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for Reg-Down, for the hour. |
| PCRDAMT q, m | $ | Procured Capacity for Reg-Down Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for Reg-Down, for the hour. |
| RDFQAMTTOT | $ | Reg-Down Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for Reg-Down, for the hour. |
| RDFQAMT q | $ | Reg-Down Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for Reg-Down for the Operating Hour is calculated as follows:

RDCOST q	=	RDPR * RDQ q

Where:

RDPR	=	RDCOSTTOT / RDQTOT

RDQTOT	=	ΣqRDQ q

RDQ q	=	RDONET q –  ΣmRDSQ q, m

RDONET q	=	(Σq(ΣmRDSQ q, m + ΣmPCRD q, m – ΣmRDRP q, m – RDFQ q)) *  HLRS q + RDCS q – RDCP q + ΣmRDRP q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RDCOST q | $ | Reg-Down Cost per QSE—QSE q’s share of the net total costs for Reg-Down, for the hour. |
| RDPR | $/MW per hour | Reg-Down Price—The price for Reg-Down calculated based on the net total costs for Reg-Down, for the hour. |
| RDCOSTTOT | $ | Reg-Down Cost Total—The net total costs for Reg-Down for the hour. See item (a) above. |
| RDQTOT | MW | Reg-Down Quantity Total—The sum of every QSE’s portion of its net Ancillary Service Obligation that is not self-supplied with its Resource capacity in either DAM or any SASM, for the hour. |
| RDQ q | MW | Reg-Down Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation that is not self-supplied with its Resources capacity in either DAM or any SASM, for the hour. |
| RDONET q | MW | Reg-Down Obligation Net per QSE—The net Ancillary Service Obligation of QSE q, for the hour. |
| RDSQ q, m | MW | Reg-Down Supplied Quantity per QSE per market—The capacity for Reg-Down to be supplied with Resources represented by QSE q to meet its Ancillary Service Obligation and/or its Ancillary Service Trades, for the market m, for the hour. |
| PCRD q, m | MW | Procured Capacity for Reg-Down per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Down, for the hour. |
| RDFQ q | MW | Reg-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| HLRS q |  | The hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| RDCS q | MW | Reg-Down Capacity Sale per QSE—The total Reg-Down capacity shown in Ancillary Service Trades with QSE q as a seller, for the hour. |
| RDCP q | MW | Reg-Down Capacity Purchase per QSE—The total Reg-Down capacity shown in Ancillary Service Trades with QSE q as a buyer, for the hour. |
| RDRP q, m | MW | Reg-Down Replacement per QSE per market—The Reg-Down capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in the market m, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the Reg-Down for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTRDAMT q	=	RDCOST q – DARDAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRDAMT q | $ | Real-Time Reg-Down Amount per QSE—The adjustment to QSE q’s share of the costs for Reg-Down, for the hour. |
| RDCOST q | $ | Reg-Down Cost per QSE—QSE q’s share of the net total costs for Reg-Down, for the hour. |
| DARDAMT q | $ | Day-Ahead Reg-Down Amount per QSE—QSE q’s share of the DAM cost for Reg-Down, for the hour. |
| q | none | A QSE. |

(3)	For Responsive Reserve, if applicable:

(a)	The net total costs for Responsive Reserve for a given Operating Hour is calculated as follows:

RRCOSTTOT	=	(-1) * (ΣmPCRRAMTTOT m + RRFQAMTTOT)

Where:

Total payment of DAM or SASM procured capacity for Responsive Reserve by market

PCRRAMTTOT m	=	ΣqPCRRAMT q, m

Total charge of failure on Ancillary Service Supply Responsibility for Responsive Reserve

RRFQAMTTOT	=	ΣqRRFQAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RRCOSTTOT | $ | Responsive Reserve Cost Total—The net total costs for Responsive Reserve for the hour. |
| PCRRAMTTOT m | $ | Procured Capacity for Responsive Reserve Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for Responsive Reserve, for the hour. |
| PCRRAMT q, m | $ | Procured Capacity for Responsive Reserve Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for Responsive Reserve, for the hour. |
| RRFQAMTTOT | $ | Responsive Reserve Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for Responsive Reserve, for the hour. |
| RRFQAMT q | $ | Responsive Reserve Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Responsive Reserve, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for Responsive Reserve for the Operating Hour is calculated as follows:

RRCOST q	=	RRPR * RRQ q

Where:

RRPR	=	RRCOSTTOT / RRQTOT

RRQTOT	=	ΣqRRQ q

RRQ q	=	RRONET q –  ΣmRRSQ q, m

RRONET q	=	(Σq(ΣmRRSQ q, m + ΣmPCRR q, m – ΣmRRRP q, m – RRFQ q)) *   HLRS q + RRCS q – RRCP q + ΣmRRRP q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RRCOST q | $ | Responsive Reserve Cost per QSE—QSE q’s share of the net total costs for Responsive Reserve, for the hour. |
| RRPR | $/MW per hour | Responsive Reserve Price—The price for Responsive Reserve calculated based on the net total costs for Responsive Reserve, for the hour. |
| RRCOSTTOT | $ | Responsive Reserve Cost Total—The net total costs for Responsive Reserve for the hour. See item (a) above. |
| RRQTOT | MW | Responsive Reserve Quantity Total—The sum of every QSE’s portion of its net Ancillary Service Obligation that is not self-supplied with its Resource capacity in either DAM or any SASM, for the hour. |
| RRQ q | MW | Responsive Reserve Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation that is not self-supplied with its Resources capacity in either DAM or any SASM, for the hour. |
| RRONET q | MW | Responsive Reserve Obligation Net per QSE—The net Ancillary Service Obligation of QSE q, for the hour. |
| RRSQ q, m | MW | Responsive Reserve Supplied Quantity per QSE per market—The capacity for Responsive Reserve to be supplied with Resources represented by QSE q to meet its Ancillary Service Obligation and/or its Ancillary Service Trades, for the market m, for the hour. |
| PCRR q, m | MW | Procured Capacity for Responsive Reserve per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Responsive Reserve, for the hour. |
| RRFQ q | MW | Responsive Reserve Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Responsive Reserve, for the hour. |
| HLRS q |  | The hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| RRCS q | MW | Responsive Reserve Capacity Sale per QSE—The total Responsive Reserve capacity shown in Ancillary Service Trades with QSE q as a seller, for the hour. |
| RRCP q | MW | Responsive Reserve Capacity Purchase per QSE—The total Responsive Reserve capacity shown in Ancillary Service Trades with QSE q as a buyer, for the hour. |
| RRRP q, m | MW | Responsive Reserve Replacement per QSE per market—The Responsive Reserve capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in the market m, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the Responsive Reserve for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTRRAMT q	=	RRCOST q – DARRAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRRAMT q | $ | Real-Time Responsive Reserve Amount per QSE—The adjustment to QSE q’s share of the costs for Responsive Reserve, for the hour. |
| RRCOST q | $ | Responsive Reserve Cost per QSE—QSE q’s share of the net total costs for Responsive Reserve, for the hour. |
| DARRAMT q | $ | Day-Ahead Responsive Reserve Amount per QSE—QSE q’s share of the DAM cost for Responsive Reserve, for the hour. |
| q | none | A QSE. |

(4)	For Non-Spin, if applicable:

(a)	The net total costs for Non-Spin for a given Operating Hour is calculated as follows:

NSCOSTTOT	=	(-1) * (ΣmPCNSAMTTOT m + NSFQAMTTOT)

Where:

Total payment of DAM or SASM procured capacity for Non-Spin by market

PCNSAMTTOT m	=	ΣqPCNSAMT q, m

Total charge of failure on Ancillary Service Supply Responsibility for Non-Spin

NSFQAMTTOT	=	ΣqNSFQAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| NSCOSTTOT | $ | Non-Spin Cost Total—The net total costs for Non-Spin for the hour. |
| PCNSAMTTOT m | $ | Procured Capacity for Non-Spin Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for Non-Spin, for the hour. |
| PCNSAMT q, m | $ | Procured Capacity for Non-Spin Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for Non-Spin, for the hour. |
| NSFQAMTTOT | $ | Non-Spin Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for Non-Spin, for the hour. |
| NSFQAMT q | $ | Non-Spin Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures on its Ancillary Service Supply Responsibility for Non-Spin, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for Non-Spin for the Operating Hour is calculated as follows:

NSCOST q	=	NSPR * NSQ q

Where:

NSPR	=	NSCOSTTOT / NSQTOT

NSQTOT	=	ΣqNSQ q

NSQ q	=	NSONET q –  ΣmNSSQ q, m

NSONET q	=	(Σq(ΣmNSSQ q, m + ΣmPCNS q, m – ΣmNSRP q, m – NSFQ q)) *   HLRS q + NSCS q – NSCP q + ΣmNSRP q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| NSCOST q | $ | Non-Spin Cost per QSE—QSE q’s share of the net total costs for Non-Spin, for the hour. |
| NSPR | $/MW per hour | Non-Spin Price—The price for Non-Spin calculated based on the net total costs for Non-Spin, for the hour. |
| NSCOSTTOT | $ | Non-Spin Cost Total—The net total costs for Non-Spin for the hour. See item (a) above. |
| NSQTOT | MW | Non-Spin Quantity Total—The sum of every QSE’s portion of its net Ancillary Service Obligation that is not self-supplied with its Resource capacity in either DAM or any SASM, for the hour. |
| NSQ q | MW | Non-Spin Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation that is not self-supplied with its Resources capacity in either DAM or any SASM, for the hour. |
| NSONET q | MW | Non-Spin Obligation Net per QSE—The net Ancillary Service Obligation of QSE q, for the hour. |
| NSSQ q, m | MW | Non-Spin Supplied Quantity per QSE per market—The capacity for Non-Spin to be supplied with Resources represented by QSE q to meet its Ancillary Service Obligation and/or its Ancillary Service Trades, for the market m, for the hour. |
| PCNS q, m | MW | Procured Capacity for Non-Spin per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Non-Spin, for the hour. |
| NSFQ q | MW | Non-Spin Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Non-Spin, for the hour. |
| HLRS q |  | The hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| NSCS q | MW | Non-Spin Capacity Sale per QSE—The total Non-Spin capacity shown in Ancillary Service Trades with QSE q as a seller, for the hour. |
| NSCP q | MW | Non-Spin Capacity Purchase per QSE—The total Non-Spin capacity shown in Ancillary Service Trades with QSE q as a buyer, for the hour. |
| NSRP q, m | MW | Non-Spin Replacement per QSE per market—The Non-Spin capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in the market m, for the hour. |
| q | none | A QSE. |
| m | none | The DAM or a SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the Non-Spin for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTNSAMT q	=	NSCOST q – DANSAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTNSAMT q | $ | Real-Time Non-Spin Amount per QSE—The adjustment to QSE q’s share of the costs for Non-Spin, for the hour. |
| NSCOST q | $ | Non-Spin Cost per QSE—QSE q’s share of the net total costs for Non-Spin, for the hour. |
| DANSAMT q | $ | Day-Ahead Non-Spin Amount per QSE—QSE q’s share of the DAM cost for Non-Spin, for the hour. |
| q | none | A QSE. |