| PRR Number | 631 | PRR Title | Black Start Bid Procedures and Compensation for Testing |
| --- | --- | --- | --- |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 6.10.3.6 System Black Start Capability |  |
| Requested Resolution (Normal or Urgent) |  | Normal |  |
| Revision Description |  | This PRR establishes a process that requires ERCOT to perform the simulation studies (the cost of which will be uplifted to the entire market through the ERCOT Administrative Fee) of Black Start Resources called for in Protocol Section 6.10.3.6(1)(f), rather than require the simulation to be done by the prospective Black Start Resource owner before the final Black Start Service awards are made by ERCOT. In addition, this PRR establishes a payment mechanism to reimburse Resource Owners for costs incurred in the qualification and/or testing of Black Start Resources. |  |
| Reason for Revision |  | Currently, ERCOT requires, as part of the Black Start Service bidding process (which is not currently incorporated in the ERCOT Protocols), potential providers of Black Start Service to either: - provide simulation test results proving that the proposed Black Start Resource can meet the qualification test described in Protocol Section 6.10.3.6(1)(f), or - perform an operational test or a simulation test to meet the criteria described in Protocol Section 6.10.3.6(1)(f) after a Black Start Service bid is awarded to the resource,. Because of the high cost and risk associated with performing a simulation test for each potential Black Start unit prior to qualification, nearly all potential Black Start Service providers select the second option described above. This essentially negates the desire of ERCOT to have information that will allow it to properly evaluate bids and because verification is done after a Black Start bid is awarded, prospective suppliers are forced to include in their bid price an estimate of their cost of the test (either simulation or operational) potentially increasing the cost of Black Start Service to the market. Also because each simulation test may be done based on different assumptions by different entities (e.g., consultants or utilities), there is the potential for inconsistent results which could lead ERCOT to select improper or inadequate Black Start resources. This PRR attempts to create a more efficient and consistent process that will allow ERCOT to properly evaluate and select Black Start Service Resources. In addition, there is currently no compensation mechanism provided in the Protocols for QSE’s who must assist Black Start Service Resources perform their qualification tests (e.g., the “next start unit” referred to in Protocol Section 6.10.3.6(1)(f)). |  |
| Credit Implications (Yes or No, and summary of impact) |  | No |  |
| Timeline |  |  |  |
| Date Posted |  | 9/6/05 |  |
| Please see the Master List on the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Henry Durrwachter |
| E-mail Address | hdurrwachter@txu.com |
| Company | TXU Wholesale |
| Company Address | 1717 Main Street, Dallas TX 75201 |
| Phone Number | (214) 875-9285 |
| Fax Number | (214) 875-9480 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | Requires ERCOT to perform or contract with a consultant to perform simulation studies of all Black Start Resources that offer to provide Black Start Service. | Not Known | Assures that ERCOT has a consistent evaluation of the simulation of Black Start Resources. |
| MARKET SEGMENT |  |  |  |
| Consumer | None | None | Provides a more efficient bid evaluation process of Black Start Service providers which could result in lower overall costs of Black Start Service. |
| LSE: General, Including NOIE | Simulation study may require submittal of detailed generating unit information and operating parameters. | None | Provides a more efficient bid evaluation process of Black Start Service providers which could result in lower overall costs of Black Start Service. Reduces risk associated with bidding Black Start Service. |
| LSE: CR & REP | None | None | Provides a more efficient bid evaluation process of Black Start Service providers which could result in lower overall costs of Black Start Service. |
| QSE | Simulation study may require submittal of detailed generating unit information and operating parameters. | None | Provides a more efficient bid evaluation process of Black Start Service providers which could result in lower overall costs of Black Start Service. Reduces risk associated with bidding Black Start Service. |
| Resource | Simulation study may require submittal of detailed generating unit information and operating parameters. | None | Reduces risk associated with bidding Black Start Service and provides compensation for Resources used to qualify Black Start Resources |
| TDSP | None | None | None |

Proposed Protocol Language Revision

6.10.3.6	System Black Start Capability

(1)	Qualification will be provided to any Black Start Resource that has met the following requirements:

(a)	Verified control communication path performance;

(b)	Verified primary and alternate voice circuits for receipt of instructions;

(c)	Passed the basic starting test;

(d)	Passed the line energizing test;

(e)	Passed the Load carrying test;

(f)	Has started the next start unit, or has started the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or has been demonstrated through simulation studies conducted by ERCOT, to be capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate Black Start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource, or the Generation Resource Entity to ERCOT within thirty (30) days or less;

(g)	If not starting itself, has an ERCOT approved firm standby power contract with deliverability under ERCOT blackout circumstances from another power pool that can be finalized upon selection as a Black Start Resource;

(h)	If not starting itself, has an ERCOT approved agreement with the necessary TDSPs for access to another power pool, for coordination of switching during a Black Start event, for coordination of maintenance through the ERCOT Outage scheduler for all non-redundant transmission startup feeds; and

(i)	If dependent upon non-ERCOT transmission Resources, agreements providing this Transmission Service have been provided in the proposal.

(2)	On successful demonstration of system Black Start Service capability, ERCOT shall qualify the Black Start Resource as being permitted to provide the system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource.  Qualification shall be valid for one year from the date of the last successful Basic Starting test, three years from the date of the last successful line energizing test, or six (6) years from the date of the last successful Load carrying test, whichever is earliest.  Qualification shall be revoked if the Black Start Resource fails to perform successfully during an actual restoration event, until the Black Start Resource is successfully retested.  Retesting is only required for the aspect of system Black Start Service capability (basic starting, line energizing, or Load carrying) for which the Black Start Resource failed.

(a)	Basic Starting Test:

(i)	The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another power pool, without support from the ERCOT System, is tested annually, either as a stand-alone test or part of the line energizing and Load carrying tests.  The test is run during a one-week period agreed on in advance by the Black Start Resource and ERCOT’ and must not cause Outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(ii)	ERCOT shall confirm the dates of the test with the Black Start Resource;

(iii)	At a time during a previously agreed test week window not previously disclosed to the Black Start Resource, ERCOT will initiate the test;

(iv)	The Black Start Resource, including all auxiliary Loads, will be isolated from the ERCOT power system, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of another power pool through a firm standby agreement will connect to the external grid, start-up, carry internal Load, disconnect from the external grid if not supplied through a black start capable DC Tie, and continue equivalently to what is required of other Black Start units;

(v)	The Black Start Resource will start without assistance from the ERCOT System, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract;

(vi)	The Black Start Resource must remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least thirty (30) minutes; and

(vii)	The Black Start Resource must have verified that its Volts/Hz relay, over excitation limiter, and under excitation limiter are set properly and that no protection devices will trip the unit within the required reactive range.  Data to verify these settings will be provided to ERCOT.

(b)	Line Energizing Test:

(i)	The ability of the Black Start Resource to energize transmission will be tested when conditions permit as determined by the TDSP but at least once every three years.  Tests will be conducted at a time agreed on by the Black Start Resource, TDSP, and ERCOT;

(ii)	Sufficient transmission will be de-energized such that when it is energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan calls for the Black Start Resource to supply.  ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource;

(iii)	Conduct a Basic Starting Test;

(iv)	ERCOT will direct the Black Start Resource to energize the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line.  Alternatively, if ERCOT agrees, the transmission line can be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed; and

(v)	The Black Start Resource must remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or external Loads and controlling voltage for at least thirty (30) minutes.

(c)	Load Carrying Test:

(i)	The ability of the Black Start Resource to remain stable and to control voltage and frequency while supplying restoration power to the Load that ERCOT’s restoration plan calls for the Black Start Resource to supply shall be tested as conditions permit, but at least once (1) every six (6) years;

(ii)	Conduct a Basic Starting Test;

(iii)	Conduct a line energizing test; and

(iv)	The TDSP operator will direct picking up sufficient Load to demonstrate the Black Start Resource’s capability to supply the required power identified in ERCOT’s restoration plan, while maintaining voltage and frequency for at least thirty (30) minutes.

(3)	Qualification shall be revoked for that calendar year if the Black Start Resource fails to perform successfully during an actual ERCOT System black out event and the unit has been declared available, as defined in Section 9B(1) of the “Standard Form Black Start Agreement.”

- As part of the bidding process for Black Start Service, the Generation Entity shall supply ERCOT with the necessary information (as specified in the Black Start Service bid package) to adequately simulate the qualification test specified in Section 6.10.3.6(f).

- ERCOT shall perform or use a consultant to perform the simulation studies of Black Start Resources bidding to supply Black Start Service specified in Section 6.10.3.6(f) to determine whether the Black Start Resource is qualified to provide Black Start Service.

- If a Black Start Resource performs the next start unit test specified in Section 6.10.3.6(f), then ERCOT shall pay the Resource Owner of the next start unit utilized in the test the lesser of $x,xxx (amount of payment to be determined) per test or the actual verifiable costs incurred by the Resource Owner during the test, substantiated by detailed documentation approved by ERCOT.  The costs of any tests of Black Start Resources shall be uplifted to Market Participants in the same manner as all other Black Start Service Costs.

- If a Black Start Resource performs the next start unit motor test specified in Section 6.10.3.6(f), then ERCOT shall pay the Resource Owner of the next start unit utilized in the test the lesser of $yyy (amount of payment to be determined) per test or the actual verifiable costs incurred by the Resource Owner during the test, substantiated by detailed documentation approved by ERCOT. The costs of any tests of Black Start Resources shall be uplifted to Market Participants in the same manner as all other Black Start Service Costs.