## Slide 1
April 17, 2006 EECP Event

## Slide 2: Day Ahead Studies
16:00 April 16 Replacement Study
  Peak load forecast – 49,018 MW
  On-line peak capacity scheduled – 50,661 MW
ERCOT procured additional 2,542 MW RPRS and OOMC for HE 16 and 17 on April 17
01:00 April 17 Replacement Study
  Peak load forecast – 49,591 MW
  On-line peak capacity scheduled – 54,382 MW
  No need seen for additional capacity

## Slide 3: April 17 – Pre-EECP
Load tracking above forecast
13:00 Replacement Study
  Peak load forecast – 51,114 MW
  On-line peak capacity scheduled – 55,234 MW
    Included 490 MW that tripped between 12:00 and 13:00
  Resource Plans also showed 1,700 MW off-line capacity available within 30 minutes
  No need seen for additional capacity
Actual demand at 14:00 was 49,194 MW

## Slide 4
Resource Plan at 16:00:
4/16 16:00 Study: 45,721 MW
4/17 01:00 Study: 45,850 MW
4/17 12:56 Study: 44,212 MW
Max Capacity at 16:00:
4/16 16:00 Study: 50,661 MW
4/17 01:00 Study: 54,382 MW
4/17 12:56 Study: 55,234 MW

## Slide 6
Month Year (2004) | MAPE for MTLF run at 16:00 Day Ahead | MAPE for MTLF run at Midnight
January-04 | 4.757416436 | 4.853383292
February-04 | 4.806754576 | 4.500958182
March-04 | 2.89408747 | 2.869912145
April-04 | 3.234206188 | 3.113976758
May-04 | 3.931541671 | 3.773933677
June-04 | 4.85159291 | 4.664441484
July-04 | 5.072650727 | 3.575245869
August-04 | 4.098733008 | 4.090108368
September-04 | 3.662364562 | 3.623070312
October-04 | 3.846329069 | 3.408705934
November-04 | 3.604728623 | 3.569435965
December-04 | 4.176752316 | 4.095488092
Average MAPE for 2004 | 4.078096 | 3.84488834

## Slide 7
Month Year (2005) | MAPE for MTLF run at 16:00 Day Ahead | MAPE for MTLF run at Midnight
January-05 | 5.018276719 | 4.74737179
February-05 | 3.466789097 | 3.4134489
March-05 | 3.413694056 | 3.340420141
April-05 | 3.370482626 | 3.258156289
May-05 | 4.208054364 | 4.052219539
June-05 | 3.910375027 | 3.609840619
July-05 | 5.216269583 | 4.622393522
August-05 | 4.857837292 | 4.462858638
September-05 | 6.239396251 | 5.024027056
October-05 | 4.513001614 | 4.250068312
November-05 | 4.531634562 | 4.36897252
December-05 | 5.9473064 | 5.937565071
Average MAPE for 2005 | 4.557759799 | 4.257278533

## Slide 8
Month Year (2006) | MAPE for MTLF run at 16:00 Day Ahead | MAPE for MTLF run at Midnight
January-06 | 4.78850099 | 4.816914369
February-06 | 4.809157545 | 4.812567462
March-06 | 4.951597243 | 4.897006282
April-06 | 5.589504926 | 5.448872452
Average MAPE for 2006 | 5.034690176 | 4.993840141