## Slide 1: Frequency Control Task Force
Report to WMS
July 19th, 2006

## Slide 2: Overview
PRR 673 Adjust SCE Performance Charge Scale Factor
  2 options presented for WMS review
  Vote on recommendation for PRS
Follow Up on SCE-related work
Governor Response Service
  Summary of FCTF and PDCWG discussions
  WMS guidance on next steps

## Slide 3: PRR 673
Result of June TAC discussion on appropriate level of financial incentive for SCE performance by Resource QSEs and desire to automatically adjust performance charge based on overall ERCOT performance.
2 options discussed at FCTF
  Both based on ERCOT CPS_1 score
  Both can move up or down each month
  Both set a maximum and minimum value for Scale Factor
  Both are automatic (PRR not needed to adjust performance charge in the future)

## Slide 4: PRR 673 Option 1
SF = 1 when ERCOT CPS_1 = 130
SF increases 0.1 each point below 130 and decreases 0.1 each point above 130

## Slide 5: PRR 673 Option 2
SF = 1 when ERCOT CPS_1 = 125 to 140
SF increases 0.1 each point below 125 and decreases 0.1 each point above 140

## Slide 6: ERCOT CPS_1

## Slide 7: Follow Up on SCE-related work
Ongoing report of persistence forecasting methodology for Uncontrollable Renewable Resources: periodic updates from ERCOT Staff on results – any measurable improvement in BES, RGS, or other areas?
Ongoing monitoring of SCE performance
  ERCOT CPS_1 scores
  QSE SCE performance
  SCE Performance Charges / Credits

## Slide 8: Summary of FCTF & PDCWG GRS discussions
PDCWG analysis shows that Primary Frequency Response (governor response + natural load response) is not sufficient in the system today.
Governor Response helps to arrest frequency deviations for both high frequency and low frequency excursions.
ERCOT’s system bias should be 420 MW/0.1 Hz deviation.

## Slide 9: Summary of FCTF & PDCWG GRS discussions
GRS should be a bid-in A/S, expressed in MW/0.1Hz frequency deviation, and can be self-provided.
All governors should be in service and free to respond but enforcement should not include non-bidders in an “energy-only” market design.
GRS should be portfolio-based in Zonal market and unit-specific in Nodal market.
Difficult to envision effective load participation – but possibility not yet ruled out.

## Slide 10: Possible Directions for FCTF efforts on GRS
Submit GRS PRR for Zonal Market and NPRR for Nodal Market.
Submit GRS NPRR for Nodal Market only.
Submit GRS NPRR for Nodal Market only and authorize ERCOT Operations to procure additional RRS in the Zonal Market in quantities sufficient to produce the required system response.
Do nothing further on this issue and disband the FCTF.