## ERCOT Operations Report

## ROS & OWG

## May 2006

Frequency control   59.9 > F > 60.1

| Disturbance Data |  |  |
| --- | --- | --- |
| Time | Frequency |  |
| 5/5 23:02 | 59.815 | 6 units/ 2 trains at station. 809 MW lost |
| 5/8 6:21 | 59.886 | 160 MW trip. Pre disturbance frequency = 59.38 And all 880 MW of Up Regulation exhausted. |
| 5/12 22:37 | 59.895 | 620 MW trip |
| 5/15 8:57 | 59.884 | 5 units/ 2 trains at station. 697 MW lost |
| 5/16 8:28 | 59.874 | 415 MW unit trip |
| 5/18 2:32 | 59.800 | 700 MW |
| 5/20 13:18 | 59.888 | 370 MW |
| 5/21 20:02 | 59.871 | 500 MW |
| 5/23 12:47 | 59.893 | 425 MW |

Deployed Responsive (14) (Reported Above)

| 5/4 6:42 | 5/16 8:28 |
| --- | --- |
| 5/5 23:02 | 5/18 2:32 |
| 5/8 6:20 | 5/18 22:05 |
| 5/9 12:08 | 5/20 13:18 |
| 5/9 14:41 | 5/21 20:02 |
| 5/12 22:37 | 5/23 12:47 |
| 5/15 8:56 | 5/31 10:33 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | May-05 | Apr 06 |  | May-06 |
| --- | --- | --- | --- | --- |
| DFW | 35 | 23 | 34 |  |
| E RIO | 55 | 166 | 125 |  |
| W RIO | 33 | 194 | 128 |  |
| Laredo | 71 | 66 | 85 |  |
| Bryan Area | 24 | 61 | 91 |  |
| Corpus | 31 | 1 | 13 |  |
| North | 0 | 9 | 38 |  |
| San Antonio | 0 | 17 | 51 |  |
| Western | 5 | 20 | 47 |  |
| Austin | 0 | 18 | 35 |  |
| Northeast | 0 | 12 | 0 |  |
| South | 0 | 19 | 55 |  |
| Houston | 28 | 49 | 154 |  |
|  | 282 | 655 | 856 |  |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| contingency | overload | Days |
| --- | --- | --- |
| Gibbons Creek - Greens Prairie & Gibbons Creek - East 138 kV | Dansby - Atkins 138 kV | 18 |
| Marion - Zorn & Marion - Clear Springs 345 kV | Seguin - Seguin West 138 kV | 14 |
| Odessa EHV 138/345 kV Auto | Olifin - Nylon Tap 138 kV | 13 |
|  | South - Houston | 12 |
|  | North - Houston | 10 |
| Marion - Zorn & Marion - Clearsprings 345kV | Seguin - West Seguin 138kV | 9 |
|  | North - West | 6 |
| Hill Country – Marion & STP 345 kV | Marion - Skyline 345 kV | 5 |
| Rio Honda 345/138 kV auto | S McAllen-Hidalgo 69 kV | 5 |
| Odessa EHV - Moss 138 kV | Olefin Switch - General Tire 138 kV | 4 |
| Greenville Steam 138/69 kV kV Auto | Greenville Steam 138/69 kV Auto | 4 |
|  | South - North | 4 |
| King - Roans Prairie & Tomball 345 kV | Tomball 345/138 kV Auto | 3 |
| Marion - Hill Country and Marion - Skyline 345 kV | Raymond Barker - Verde Creek 138 kV | 3 |
| Dilley Switch - North Laredo 138kV | North Laredo - Asherton 138kV | 2 |
| North Edinburg 345/138kV Auto | Magic Valley Burns – Rio Hondo 138kV | 2 |
| San Miguel - Sigmor 138kV | Kenedy Switch - Kenedy 69kV | 2 |
| Skyline - Marion and Skyline - STP 345kV | Hill Country – Marion 345 kV | 2 |
| STP - Skyline & Whitepoint 345 kV | Blessing - Lolita 138 kV | 2 |
| Texas A&M - Atkins 138 kV | Atkins - Briarcrest 69 kV | 2 |
| Ferguson - Wirtz 138 kV | Ferguson - Sherwood Shores 138 kV | 1 |
| Gibbons Creek - Twin Oaks 345kV | Watson Chapel - Robertson 138kV | 1 |
| Graham - Benbrook & Parker 345 kV | Stephenville - Lingleville 138 kV | 1 |
| Jewett 345/138 kV auto | Trinidad - Winkler BEPC 138 kV | 1 |
| Lon Hill - Nelson Sharp 345 kV | MVEC (Weslaco) – MVEC (Heidelburg) 138 kV | 1 |
| Lon Hill-Coleto Creek 345 kV | Kennedy Switch - Kennedy Sub 69 kV | 1 |
| Lon Hill - Coleto Creek 345kV | Victoria-Warburton 138kV | 1 |
| Lytton Springs - Zorn & Austrop – Zorn 345 kV | San Marcos – Canyon 138 kV | 1 |
| McNeil LCRA - Round Rock 138 kV | Howard Lane Tap – McNeil LCRA 138 kV | 1 |
| North Edinburg 345/138kV Auto | MV Burns - MV Heidelburg 138kV | 1 |
| North belt - King & Cedar Bayou 345kV | Tomball 345/138kV auto | 1 |
| Odessa EHV - Moss 138 kV | General Tire SW - Rexall 138 kV | 1 |
| Odessa EHV Sw - Moss Sw 138kV | Huntsman - Odessa EHV Sw 138kV | 1 |
| Permian Basin – General Tire 138 kV | Permian Basin - Moss Sw 138 kV | 1 |
| STP - DOW 18 and STP - DOW 27 345 kV | Fayetteville - Willow Springs LCRA 138 kV | 1 |
| Dilley Sw - San Miguel 138kV | Derby - Pearsall 138kV | 1 |
| North Edinburg Auto | Weslaco to Hidelburg 138kV | 1 |
| Sonora - Friend Ranch 138kV | Friend Ranch - Ozona 69kV | 1 |
| West Levee 345/138 kV auto | Industrial Blve - Compton St. | 1 |
| Zorn-Hays 345 kV | Raybar-Verde Creek 138 kV | 1 |
| Enterprise - Trinidad and Enterprise - Martin Lake 345 kV | Nacogdoches 345/138 kV auto | 1 |
| Morgan Creek 345/138 kV auto | Morgan Creek 345/138kV auto | 1 |
| North Edinburg 345/138 kV Auto | Weslaco - Hidelburg 138 kV | 1 |
|  | Northeast - North | 1 |

New RAP

None.

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 05/31/2006 | Day Ahead Desk V3R25 | 265 |
| 05/22/2006 | Transmission & Security Desk - Block Load Transfer | 264 |
| 05/22/2006 | Day Ahead Desk - V3R24 | 263 |
| 05/11/2006 | 2006 ERCOT Methodologies for Determining Ancillary Service Requirements | 262 |
| 05/17/2006 | Shift Supervisor - SMP Alarm | 261 |
| 05/11/2006 | Shift Supervisor V3R26 | 260 |
| 05/10/2006 | Shift Supervisor Desk V3R25 | 259 |
| 05/04/2006 | Transmission & Security Desk V3R69 | 258 |
| 05/03/2006 | Day Ahead Desk V3R23 | 257 |

Blackout/Load Shed incidences

None

Major system voltage problems

None

Voltage Instructions

None

Major Computer Problems, Enhancements & Fixes

None

Communication

5/10	19:20-20:30	ERCOT lost network connectivity to EMS control, MOI application and hot lines to both TDSP and QSE.  ERCOT held balancing energy interval 19:45 and resumed normal deployments for 21:30 interval.

5/23	ERCOT held Real Time Balancing 10:15 interval due to the 10:30 interval not solving.

ERCOT peak (Unofficial)

5/25	17:00	55,050

Other

5/22	05:22	4 units and 1 138 kV line tripped at a station.

5/28	16:53	Bus trip during thunderstorms. Lost 1 138/69 kV transformer, 2 138 kV lines, and 40 MW load.

Alerts, OCN, and Emergency Notices

| 1-May | 10:49 | 18:00 | OCN | Capacity Shortage hrs 17 and 18 |
| --- | --- | --- | --- | --- |
|  | 13:30 | 18:00 | Alert | Capacity Shortage hrs 17 and 18 |
|  | 15:50 | 23:00 | Transmission Alert | Loss of San Miguel Switchyard 138kv to San Miguel Switchyard 69kv loads Derby to Pearsall 69kv. |
|  | 15:50 | 23:00 | Transmission Alert | Loss of Rio Hondo 345/138kv transformer loads Hidalgo to South McAllen 69kv. |
|  | 15:50 | 23:00 | Transmission Alert | Loss of Odessa EHV to Moss 138kv loads Olefin Switch to General Tire 138kv. |
| 2-May | 15:09 | 22:50 | Transmission Alert | Loss of Rio Hondo 345/138kv transformer loads Hidalgo to South McAllen 69kv. |
| 3-May | 15:28 | 22:50 | Transmission Alert | Loss of Rio Hondo 345/138kv transformer loads Hidalgo to South McAllen 69kv. |
|  | 15:29 | 19:00 | Transmission Alert | Loss of Lon Hill to Coleto Creek 345 KV Line loads Kennedy Switch to Kennedy Sub 69 KV line |
|  | 15:33 | 16:51 | Transmission Alert | Loss of South McAllen T1 138/69 KV Auto loads La Palma to Rangerville 69 KV line |
| 4-May | 15:44 | 20:05 | Transmission Alert | Loss of Rio Hondo 345/138kv transformer loads Hidalgo to South McAllen 69kv. |
| 4-May | 16:00 | 18:45 | Transmission Alert | Loss of San Miguel Sw to Sigmor 138 kV Line loads Kennedy Switch to Kennedy Sub 69 kV line |
| 5-May | 16:00 | 23:17 | Transmission Alert | Loss of Rio Hondo 345/138 kV transformer loads Hidalgo to South McAllen 69 kV line. |
|  | 16:00 | 23:17 | Transmission Alert | Loss of San Miguel Sw to Sigmor 138 kV Line loads Kennedy Switch to Kennedy Sub 69 kV line |
|  | 16:00 | 23:17 | Transmission Alert | Loss of Pleasanton to Moore 138 kV Line loads Dilley to Pearsall 69 kV line |
| 8-May | 15:00 | 23:55 | Transmission Alert | Loss of San Miguel Switchyard 138kv to San Miguel Switchyard 69kv loads Derby to Pearsall 69kv. |
| 9-May | 3:00 | 4:25 | OCN | Capacity Shortage hrs 17 and 18 |
|  | 11:00 | 13:00 | OCN | Capacity shortage HE 1700 |
|  | 14:03 |  | Transmission Alert | Loss of San Miguel Switchyard 138kv to San Miguel Switchyard 69kv loads Derby to Pearsall 69kv. |
|  | 14:27 | 23:40 | Transmission Alert | Loss of Javelina to Highway 9 138 kV line loads Morris to Westside 138 kV line |
|  | 15:00 | 19:00 | Advisory | A situation is emerging that has the reasonable expectation of leading ERCOT into an insecure state |
| 10-May | 4:00 | 14:30 | Alert | Second Replacement Reserve Service Market opened |
|  | 12:03 | 15:14 | Transmission Alert | Loss of Javelina to Highway 9 138 kV line loads Morris to Westside 138 kV line |
|  | 15:13 | 19:30 | Transmission Alert | Loss of San Miguel Switchyard 138kv to San Miguel Switchyard 69kv loads Derby to Pearsall 69kv. |
|  | 15:37 | 19:30 | Transmission Alert | Loss of San Miguel Sw to Sigmor 138 kV Line loads Kennedy Switch to Kennedy Sub 69 kV line |
| 11-May | 0:19 | 15:35 | Transmission Alert | Loss of Kingsville - Alice 138kv loads Falfurrias 138/69kv transformer. |
|  | 3:00 | 3:45 | Alert | Second Replacement Reserve Service Market opened |
| 13-May | 16:25 | 19:30 | Transmission Alert | Loss of San Miguel Switchyard 138kv to San Miguel Switchyard 69kv loads Derby to Pearsall 69kv. |
| 14-May | 15:40 | 19:00 | Transmission Alert | Loss of the North Edinburg 345/138kv auto loads Rio Hondo to Magic Valley Burns 138kv. |
|  | 15:40 | 19:00 | Transmission Alert | Loss of the Dilley Switch to North Laredo Switch 138kv loads the Asherton to North Laredo Switch 138kv. Loss of Bates to Garza 138kv loads North Laredo Switch to Asherton 138kv. |
|  | 15:40 | 19:00 | Transmission Alert | Loss of San Miguel Switchyard 138kv to San Miguel Switchyard 69kv loads Derby to Pearsall 69kv. |
|  | 15:40 | 19:00 | Transmission Alert | Loss of San Miguel 138kv to San Miguel 69kv sub loads the Pleasanton 138/69kv transformer. |
| 18-May | 23:05 |  | OCN | 5/19/06 Capacity shortage hours 17, 18, 19. |
|  | 23:50 |  | Alert | Second Replacement Reserve Service Market opened |
| 19-May | 0:15 | 3:30 | Alert | Second Replacement Reserve Service Market opened |
|  | 0:15 | 3:30 | OCN | 5/19/06 Capacity shortage hours 17, 18, 19. |
| 24-May | 15:45 | 22:00 | Transmission Alert | Loss of the Asherton 138/69KV tr or the Asherton to Escondido 138KV line loads the Uvalde 138/69KV tr |
| 26-May | 22:00 | 5/28 23:26 | Emergency Notice | Emergency Notice posted for the Laredo Area during Laredo 3 Forced Outage |
| 28-May | 16:53 | 18:28 | Transmission Alert | Transmission Alert for loss of Roma Sw - Falcon 138 kV overloads San Diego - Freer 69 kV due to a Forced Outage on the Laredo 138 kV bus that also caused 40 MW of load loss. |