| ### Provide Advanced Notice of Diminishing Responsive Reserve |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Guidelines for issuing advance notice of diminishing Physical Responsive Reserves. Physical Responsive Reserve is not Responsive Reserve Service. All notices and EECP will be called on Physical Responsive Reserve. |
| 1 | IF Total Responsive Reserve is equal to or less than 3000 MW, or greater than 2500MW, issue an Operating Condition Notice (OCN). |
| NOTE: | Follow OCN Procedures as required per section 2.6.1. |
| 2 | IF Total Responsive Reserve is equal to or less than 2500 MW, and greater than 2300MW, issue an Alert. |
| NOTE: | Follow Alert Procedures as required per section 2.6.3. |
| 2a | Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. |
| 2b | Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing. |
| 2c | Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive reserves. |
| 3 | IF Responsive Reserve is below 2300MW, begin implementing EECP Step 1. |
| NOTE: | Follow EECP Procedures as required per section 2.6.6 |