## Slide 1
Report on Lessons Learned – Hurricane Rita November 10, 2005 ROS Meeting Austin Control Center (MET Center)

## Slide 2: It is better to be missed than hit…
ERCOT was not significantly impacted by hurricane RITA.
ENTERGY was significantly impacted; and ERCOT is attempting to learn from their experience.
ERCOT does not yet have a response.

## Slide 3: ERCOT is able to setup and execute Block Load Transfer rapidly
ERCOT was able to quickly implement block load transfers within the market structure
  Registration – Financial qualification was done quickly through picking an existing representative in ERCOT. We were able to push through the database in 1 day what normally takes 3-4 days. Registered delivery point as a new NOIE LSE. The LSE pointed to an existing QSE. Set EZID as a wholesale delivery point. Nothing went to MOS.
  We are required by protocol to have metering at BLT’s– Centerpoint and TXU got meters installed and registered EZIDs at ERCOT very quickly.

## Slide 4: Backup Center activation
Several QSE’s/TDSP’s activated their emergency backup centers/plans.
  Some QSE’s have backup centers
  Some delegate another service provider to provide services
In general, this was successful.
  One center did not successfully communicate during the storm period.
Storm impact was minimal

## Slide 5: Loss of Communications
ERCOT implemented a plan for loss of communications
ERCOT procured satellite telephones for the event.
It was not needed during this event

## Slide 6: ERCOT Can expect timely government action if needed
Actions:
  Governor issued order suspending eminent domain requirements for temporary facilities
  On 9/27 PUCT issued order suspending CCN requirements and allowing ERCOT TDSPs to extend service in area
  DOE agreed to issue order maintaining ERCOT’s FERC exemption for these emergency connections

## Slide 7: ERCOT does NOT have an effective method of forecasting load in either Commercial or Operational systems
We should expect high UFE amounts on and around projected hurricanes landfall
We should expect high errors in the ERCOT operational load forecast.

## Slide 8: ERCOT has sent a list of questions to Entergy…
What did you learn from your experiences with hurricanes this summer?
What would you do differently when preparing for hurricanes in the future?
Do you have an existing emergency plan that deals with hurricanes? Can you share it?
Did you shut down plants in preparation for the storm? Should you have?
What advice can you give us on how to prepare?
Should we have a special emergency plan for hurricane preparation?
Do you set distribution relays to one-shot near the coast?
Can you advise us on how to plan for fuel curtailments/issues?
Do you believe additional units should be gotten on line, or should we reduce the number of units online so we can get under the load?
What did you do with staff? Did you put people in critical locations?

## Slide 9
Lessons Learned from Block Load Transfers following Hurricane Rita
Reliability and Operations Subcommittee Meeting
January 13, 2006

## Slide 10: Lesson’s Learned
Purpose: Brief evaluation of Block Load Transfers (BLTs) in the aftermath of Hurricane Rita to pick up load in Entergy Gulf States Service territory
Involved Parties:
TXU Energy Delivery – Deep East Texas Cooperative BLT (≈10 MWs)
Centerpoint – Crosby Station BLT (≈80 MWs)
Entergy Gulf States

## Slide 11: Lesson’s Learned
Physical Issues:
Very little ERCOT can do. Work needed to block load over and all closely associated activities are between TDSPs.
One-line drawings delivered ASAP are very important for a timely transfer (acceptable format)
Contractual issues between the TDSP’s (how to compensate TDSPs for work) can slow up transfer

## Slide 12: Lesson’s Learned
Commercial Issues:
Need to create a LSE in ERCOT’s system was a hindrance
Contractual Issues between the TDSPs should be considered in advance of the need to use an emergency BLT
Settlement quality metering during a BLT for emergency restoration (.2% vs .6% CT accuracy)
Frequency for providing metering data as well as method for providing data

## Slide 13: Lesson’s Learned
Recommendations:
ERCOT will investigate the creation entities and their relationships ahead of time (LSE for BLT into ERCOT; RE for BLT into other control area).
Metering CT accuracy (.6%) will be allowed for emergency load restoration.
ERCOT recommends actual meter data be provided before initial settlement run. Use of default profiles would introduce significant error if used.
ERCOT will be flexible as to the format for data submittal (Loadstar, Excel, etc.).
Investigate clearing Interstate Commerce issues in advance for BLTs that could block loads across state lines.
Develop checklist for entities to use as a guide to prepare for an emergency.

## Slide 14: SMEPA – Lessons Learned During Storm
1. Alarms/Events (Avg 25k/day) – During Katrina 6.5K every two minutes.
1. Set your alarm priorities.
2. Make sure your archive size is sufficient.
3. Keep a unit spinning off-line.
4. Put the Control Center on emergency power before the storm.
5. You set up in the Control Center for real-time database and display modifications and additions.
6. Single transmission one-line with NSP
7. Limit access to the main control room

## Slide 15: SMEPA – Lessons Learned Day After
1. Approximately 1500 miles of destroyed/down high voltage
transmission
2. Almost all distribution, distribution/transmission down/destroyed
3. No ties or communication with other utilities (Isolated)
4. One unit spinning, supplying it’s own load
5. All communications to plants - Dead
6. All roads, state highways, interstate highways – Completely Blocked
7. All SCADA communications – Dead
8. All voice, cell and internet communications – Dead
9. Main control center running on backup generator
10.All stores, gas stations, supply houses – Closed (extended time)
11.Employee travel impossible to home or to work
12.Employees at work had no clue about their families or homes the main control room

## Slide 16: SMEPA –First Needs
1. Long term fuel for Control Center emergency generator
2. Fuel for SMEPA and contractor vehicles
3. Food and water for local, plant and field personnel.
4. No motels – Housing for contract and SMEPA personnel
5. No running water – facilities for both men and women
6. Purchasing
7. Who is in charge (Emergency organization list)
1. Overall coordination – from Control Center
2. Transmission, Generation/Fuels, Facility Needs, SCADA,
Communications (Phone, Radio, Internet, E-Mail)

## Slide 17: SMEPA – Additional Needs
1. Satellite phones
2. Additional consoles (Switch, ES), Power Application Studies
3. PI Playback
4. Have a management command center outside the control center
5. Critical Loads, Hospitals, SMEPA facility, VP Call
6. Fly transmission lines/substations – visually (open/closed)
7. Transmission restoration based on
1. Critical load list
2. Available generation / Can you sustain voltage
3. Load needed to stabilize generation
4. Line/Substation condition

## Slide 18: SMEPA – Additional Needs
1. Transmission
1. Assemble crews (Road passage, ROW passage, Pole/Wire)
2. Coordinate work to be done
3. Coordinate transmission and distribution to same area
2. Generation
1. Fuel supply
2. Damage - cooling towers, etc.
3. CIS network including internet, e-mail (no outside network for over a week)
4. Phone communications – satellite (some phone communications
out for two to three months) – SCADA & Land Lines
5. Communications – Radio, Microwave

## Slide 19: SMEPA – Lessons
Radio Needs
Satellite – Phone, SCADA, Internet
Mapboard – NSP, Lines of Resolution
Personnel Location by crew/team/individual (GPS)
Procedures and Emergency Organization Chart
Reclosers - Off
Test black-start plan, units-Isoch, Frequency source, 60HZ
Written Event Log – Lines put in service, Transformers heated
Ties closed, …
The guiding principal: 1. Safety 2. Reliability 3. Economics
After restoration
  1. Fix patched lines
  2. Complete right of way clearing

## Slide 20
FPL Preparedness plan Excerpts from the Geisha Testimony – FPL response to FLA PUC

## Slide 21: Plan Objective
  To safely restore the greatest number of customers in the least amount of time
    Meeting this objective is the most prudent response after a major storm.
      Planning
      Training
      Adherence to established storm processes
      Execution

## Slide 22: Key Components
Disaster response policies and procedures
Adjustable internal organizational structures based on the required response
Timeline of activities to assure rapid notification and response;
Mutual assistance agreements and vendor contracts and commitments
Plans for movement of resources, personnel, materials, and equipment to areas requiring service restoration
Communication and notification plans for employees, customers, community leaders, emergency operating centers, and regulators

## Slide 23: Key Components
An established centralized command center with an organization for command and control of emergency response forces
Checklists and conference call agendas to organize, plan, and report situational status
Damage assessment modeling and reporting procedures;
Field and aerial patrols to assess damage
Comprehensive circuit patrols to gather vital information needed to identify the resources required for effective restoration
Systems necessary to support outage management procedures and customer communications.

## Slide 24: Staffing
All business units in the company identify personnel for staffing the emergency response organization. In many cases, employees assume roles different than their regular responsibilities. Training is conducted for many storm personnel each year regardless of whether they are in a new role or a role in which they have served many times. This includes training on processes that range from analytical and clerical to reinforcing restoration processes for managers and directors.

## Slide 25: Logistics
Increasing material inventory
Establishing staging site plans
Expanding and verifying lodging arrangements
Securing agreements and contracts for
  Catering
  Busing
  Office trailers
All of these agreements and activities provide the foundation to begin any restoration effort.

## Slide 26: Logistics - Functions
Acquisition, preparation and coordination of:
  Staging sites, environmental, salvage, lodging, laundry, buses, caterers, ice and water, office trailers, light towers, generators, port-o-lets, security guards, communications, and fuel delivery.

## Slide 27: Testing the plan
Annual, full scale drill
  Active participation from employees represented from every business unit in the company.
  Begin 72 hours from the mock hurricane’s forecasted time and date of impact.
  Simulate
    Damage assessments
    Communications
    Acquiring resources
    Updating storm systems

## Slide 28: Response to a Storm Threat – 72 Hours out
Staff meteorologists are monitoring conditions
Initiate preliminary preparations for addressing internal and external resource requirements, logistics needs, and system operation conditions.
General Office Command Center (GOCC) is activated
Storm personnel are alerted
Resource requirements are forecasted
Initial restoration plans are developed
Contingency resources are activated
Available resources from mutual assistance utilities are identified

## Slide 29: Response to a Storm Threat – 48 Hours out
Computer models are run based on the projected intensity and path of the storm to forecast
  Damage
  Restoration workload
  Potential customer outages
Commitments are confirmed for restoration personnel, materials, and logistics support
Identify staging site locations based on expected path of storm

## Slide 30: Response to a Storm Threat – 24 Hours out
Positioning personnel and supplies to begin restoration as soon as it is safe to do so
Continuously re-run Damage models
Community leaders and County Emergency Operations Centers are contacted to share FPL’s restoration plans
Verify critical infrastructure facilities
Provide information to the news media, customers and community leaders regarding storm preparation, what to do in the event of an outage, as well as public safety messages.

## Slide 31: 5/30 DHS Report Florida utility prepares for major hurricanes.
  ‘Earlier this month the Florida Public Service Commission concluded that Florida Power & Light had not done enough to limit hurricane damage to the power grid following Hurricane Wilma in 2005. Up to 6.5 million people were left without lights, air conditioning, or hot water. FPL has instituted a five-point plan dubbed “Storm Secure”, to make major steps to strengthen its transmission and distribution system and make it better able to withstand hurricane-force winds, said Geisha Williams, FPL’s vice president of distribution. She said Storm Secure, launched on January 30, was only just getting underway, however. And while FPL has improved its reliability by about 50% since 1997, Williams acknowledged it still has a long way to go. “It won’t be overnight; it’s going to take a long time,” said Williams, referring to a key goal of “hardening” the electric grid to withstand wind gusts up to 150 mph.’