## Slide 1: CenterPoint Dynamic Reactive Project TAC 8/30/2006

## Slide 2: Description of Project
3 Sites Considered
2 Sites Selected
  Bellaire
  Crosby
Estimated Cost $20 – 25 M for devices and all construction.
In-Service by Peak 2008.

## Slide 3
Projects Needed for Reliability
Operation Guide 3.1.4.6, Protective Relaying Requirement:
  “Generator terminal voltage deviations exceed five percent (5%) but are within ten percent (10%) of the rated design voltage and persist for less than 10.0 seconds.”
Load Shedding Limit:
  Limit the amount of load shedding to less than 1250 MW to avoid possible over frequency tripping, loss of significant local demand, and mitigate risk of cascading regional blackout.
Load and Generation Forecast for Houston Area:
  Demand exceeded local generation in 2005, in 2007, demand will exceed local generation by 2,000 MW, in 2009 close to 3,000MW.

## Slide 4: Houston Area Generation Vs. Load
Houston Area Retirements

## Slide 5: Independent Review Results
With Houston area retired/mothballed units in the case, the Dynamic Reactive Devices were not needed.
With neither the Houston area retired/mothballed units nor the Dynamic Reactive Devices, several Houston area generating units did not meet requirements of Op. Guide 3.1.4.6.
Without the Houston area retired/mothballed units but with the Dynamic Reactive Devices, all Houston area generating units met requirements of Op. Guide 3.1.4.6.

## Slide 6: Multiple Facility Forced Outages
ERCOT Surveyed Transmission Operators to determine frequency of extreme events resulting in two or more components removed or cascading out or service – NERC Category D
Results Showed:
  Average 19.71 events per year
  Average 3.89 circuits removed per event
  Average Time Between Events – 16.67 Days
Similar MAAC Data compiled by PPL Electric Utilities showed an average of 18.4 events per year with 2.4 to 2.6 circuits removed per event.

## Slide 7
Stakeholder Review
The Stakeholder review period for this project was held in April 2006.
There have been no dissenting comments on this package of projects.
ROS Dynamic Working Group supports project.

## Slide 8
ERCOT Support For the Project
ERCOT supports the need for this project, as described, and asks that TAC endorse approval by the Board