## Slide 1: ROS Review of 4/17/06 EECP Event
ROS met on 5/15/06 to review the ERCOT Operations Report for the 4/17/06 EECP event.
ROS had no significant issues with the data in the report, or with ERCOT actions taken during the event
Issues identified for additional discussion / possible improvement:
Reliance on 100% of indicated reserve capability
Improved advance notice to participants
Dispatch / control of additional reserves
Clarity /adequacy of communication
Timing of manual LAAR deployment
Timing of Public Appeals
Discussion of these points at subsequent ROS meetings resulted in a determination of more appropriate EECP event triggers and actions at various EECP steps.

## Slide 2: ROS Proposed Refinements to EECP
Point 1: Historically, indicated reserves overstate the true capability of online generation. This delays initiation of EECP, and creates confusion as to how severe circumstances truly are.
Point 2: Current EECP procedures can be improved to optimize market participant response during the event, and during recovery from the event.
Point 3: Certain actions can be taken prior to entering EECP that can reduce the severity and/or the need for additional measures.
ROS and OWG have developed OGRR 186 in response, along with the necessary PRR. These should reach TAC this September (depending on urgency voting).

## Slide 3: ROS Solution to Reserve Monitoring
Physical Responsive Capability (PRC):
For the purpose of determining the probable amount of online responsive reserves that will in fact respond to system emergencies, generating unit capabilities will be reduced by the RDF when determining responsive reserve capabilities.
Reserve Discount Factor (RDF):
Proposed by ERCOT, approved by ROS. Initial determination shows the RDF should be 7%.
The PRC will be used by ERCOT when determining the appropriate Emergency Notification and appropriate EECP Steps.
Preliminary studies show approximately 1,000 MW of discounted reserves during recent high load days.
Maximum allowable LaaR Contribution towards RRS is not affected.

## Slide 4: Example of PRC on Responsive Monitoring
100 MW unit operating at 50 MW (today)
Responsive capability (20% rule) = 20.0 MW
100 MW unit operating at 50 MW (after change)
Responsive capability (20% rule) = 20%*(100 - 7%) = 18.6 MW
100 MW unit operating at 90 MW (today)
Responsive capability = (100 - 90) = 10.0 MW
100 MW unit operating at 90 MW (after change)
Responsive capability = (100 - 7%) - 90 = 3.0 MW
100 MW unit operating at 100 MW has no reserve in either case

## Slide 5: ROS Proposed EECP Actions
PRIOR TO EECP:
Start RMR Units available in the time frame of the emergency and load them to full capability. (was in Step1)
Deploy Replacement and Non-Spin resources. (was in Step 1)
DECLARE EECP STEP 1:
When PRC plus RRS from LaaR is less than 2300 MW.
Issue appeal to public for voluntary load reduction. (was in Step 3)
Other actions remain the same.
DECLARE EECP STEP 2:
When PRC plus RRS from LaaR is less than 1750 MW.
Manual removal of LaaR load still occurs at this Step.
DECLARE EECP STEP 3:
When ERCOT cannot maintain 59.8 Hz.
Firm load shed in 100 MW blocks occurs at this Step.
NO STEP 4

## Slide 6: Related ERCOT Procedure Changes
Distribution to all interested parties of daily ERCOT reports to the PUC on EECP Potential
Issue an OCN when PRC plus RRS on LaaR shows less than 3000 MW on peak.
Issue an Alert when PRC plus RRS on LaaR shows less than 2500 MW on peak.
ERCOT Operations is prepared to implement the entire package of proposed modifications to the EECP on very short notice, and requests early approval.