## ERCOT Operations Report

## ROS & OWG

## June 2006

Frequency control   59.9 > F > 60.1

| Disturbance Data |  |  |
| --- | --- | --- |
| Time | Frequency |  |
| 6/4/2006 13:41 | 59.881 | Unit trip. 350 MW lost. |
| 6/5/2006 11:38 | 59.884 | Unit trip. 571 MW lost. |
| 6/22/2006 19:17 | 59.875 | Unit trip. 580 MW lost. |
| 6/23/2006 15:59 | 59.883 | Unit trip. 420 MW lost. |

Last occurrence of > .1 Hz deviation without a unit trip April to present (4/9 06:00)

Deployed Responsive (6) (Reported Above)

6/2 7:04

6/4 13:41

6/5 11:38

6/22 6:13

6/22 19:17

6/23 15:59

Day Ahead Capacity Purchases

| Historical Totals | June-05 | May 06 | June-06 |
| --- | --- | --- | --- |
| DFW | 84 | 34 | 84 |
| E RIO | 90 | 125 | 129 |
| W RIO | 34 | 128 | 90 |
| Laredo | 90 | 85 | 87 |
| Bryan Area | 32 | 91 | 128 |
| Corpus | 29 | 13 | 3 |
| North | n/a | 38 | 18 |
| San Antonio | 0 | 51 | 83 |
| Western | 24 | 47 | 30 |
| Austin | n/a | 35 | 71 |
| Northeast | n/a | 0 | 1 |
| South | n/a | 55 | 35 |
| Houston | 15 | 154 | 144 |
|  | 398 | 856 | 903 |

|  | RMR | OOMC | RPRS |
| --- | --- | --- | --- |
| DFW | 0 | 34 | 50 |
| E RIO | 87 | 5 | 37 |
| W RIO | 0 | 45 | 45 |
| Laredo | 85 | 0 | 2 |
| Bryan Area | 0 | 64 | 64 |
| Corpus | 0 | 0 | 3 |
| North | 0 | 1 | 17 |
| San Antonio | 0 | 1 | 82 |
| Western | 0 | 2 | 28 |
| Austin | 0 | 0 | 71 |
| Northeast | 0 | 0 | 1 |
| South | 0 | 0 | 35 |
| Houston | 0 | 0 | 144 |
|  | 172 | 152 | 579 |

OOME / Congestion Management Activity  (113)

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| contingency | overload | Days |
| --- | --- | --- |
| Marion - Zorn & Clear Springs 345 kV | Seguin - Seguin West 138kV | 29 |
| Gibbons Creek - Greens Prairie & East 138kV | Dansby - Atkins 138kV | 10 |
| Bluff Creek - Oak Creek 138kV | Abilene South - Bluff Creek 138kV | 9 |
| Morgan Creek 345/138kV #1 Autotransformer | Morgan Creek 345/138kV #2 Autotransformer | 5 |
| Mt. Enterprise - Trinidad & Martin Lake - Stryker Creek 345 kV | Nacogdoches 345/138 kV Autotransformer | 5 |
| Lake Pauline - Vernon 138 kV | Vernon - Chillicothe Vernon Tap 69 kV | 4 |
| Odessa 345/138 kv Auto 2 | Odessa 345/138 kv Auto 1 | 4 |
| Lytton Springs - Zorn & Austrop 345 kV | San Marcos - Canyon 138 kV | 3 |
| Dilley Sw - San Miguel Sw 138kV | Derby - Pearsall 69kV | 2 |
| Lytton Springs - Zorn & Austrop 345 KV | Canyon-Rohr 138 KV | 2 |
| Odessa 345/138 kv Auto 1 | Odessa 345/138 kv Auto 2 | 2 |
| Roanoke Sw-Parker-Eagle Mt 345 KV | Rhome-Chisolm 138 KV | 2 |
| Stryker Creek to Trinidad 345 kV | Stryker SES-Dailville 138kV | 2 |
| Temple Pecan Creek - Tradinghouse & Temple Sw - Lake Creek 345 kV | Lake Creek - Temple Pecan Creek 138 kV | 2 |
| Marion - Hill Country & Skyline 345 kV | Kendall - Comfort 138 kV | 2 |
| Trinidad - Stryker Creek & Mt. Enterprise 345 kV | Stryker Creek - Dialville 138 kV | 2 |
| 345/138kV Garfield Transformer 1 | 345/138kV Garfield Transformer 2 | 1 |
| 138/69kV Asherton Auto | 138/69kV Uvalde Auto | 1 |
| Eagle Mountain - Weatherford 138kV | Rhome - Chisolm 138kV | 1 |
| Fisher Road - Oklaunion & Bowman 345kV | Vernon - Grayback 69kV | 1 |
| Gibbons Creek - Greens Prairie 138kV | Dansby - Atkins 138kV | 1 |
| Hamilton - Balcones 138kV | Magplant - Northland 138kV | 1 |
| Hill Country - Marion & STP 345kV | Marion - Skyline 345kV | 1 |
| Menard - Gillespie 138kv | Menard 138/69kv autotransformer | 1 |
| Morgan Creek 345/138kV #2 Autotransformer | Morgan Creek 345/138kV #1 Autotransformer | 1 |
| Morgan Creek - China Grove Switch 138 kV | Morgan Creek 138/69 kV Autotransformer #3 | 1 |
| Nelson Sharpe - Rio Hondo 345kV | MVEC Weslaco - MVEC Heidelburg 138kV | 1 |
| Oran TU - Weatherford Sw 138 kV | West TMPP - Weatherford 69 kV | 1 |
| Sandow - Temple 345kV | Robertson - Watson Chappel 138kV | 1 |
| Sargent Road - Watermill 345kV | Norwood Switch 345/138kv autotransformer | 1 |
| Sargent Road - Watermill Switch 345 kV | Cedar Hill Switch - Mountain Creek 138 kV | 1 |
| STP - Skyline & Whitepoint 345kV line | Blessing - Lolita 138kV | 1 |
| Stryker Creek to Trinidad 345 kV | Lufkin Sw - Lufkin Chippermill 138kV | 1 |
| Temple Sw - Killeen Sw - Sandow 345 KV | Belton - Harker Heights 138 KV | 1 |
| North Belt to King and Cedar Bayou 138kV | GBY345/138kV Auto #2 | 1 |
| San Miguel to Sigmor 138kV | Victoria to Fannin 69kV | 1 |
| Midland East - Odessa EHV 345kV | Odessa EHV to Odessa Sw 138kV | 1 |
| Pawnee to Lon Hill 345kV | Kennedy Sw to Kennedy 69kV | 1 |
| Marion - Hill Country & Skyline 345 kV | Seguin - West Seguin 138 kV | 1 |
| Marion - Hill Country & Skyline 345 kV | Verde Creek - Bandera LCRA 138 kV | 1 |
| North Belt to King and Cedar Bayou 138kV | Tomball 345/138 kV Autotransformer | 1 |
| Sargent Road - Watermill Switch 345 kV | Norwood Switch 345/138 kV Autotransformer | 1 |
| Trinidad - Stryker Creek & Mt. Enterprise 345 kV | Athens Tap - Athens North Switch 138kV | 1 |
| Wynn Joyce 138/69 kV Transformer | Apollo - Naaman 69 kV | 1 |
| Big Brown - Jewett 345 kV | Trinidad - Winkler BEPC 138 kV | 1 |

Zonal OC1’s

| CSC | Days |
| --- | --- |
| South - Houston | 21 |
| North - West | 14 |
| South - North | 9 |
| North - Houston | 6 |
| West – North | 2 |

New RAPs

2006 Summer RAPs are posted at: http://oldercot.ercot.com/tmaps/ListMaps.cfm?GroupID=60

- Under Operations review

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 06/26/2006 | Day Ahead Desk - Temporary Solution for RPRS Selecting Certain Blackstart Resources | 271 |
| 06/07/2006 | Maintenance Level 2 & 3 Outages - Frequency Control Desk | 270 |
| 06/01/2006 | Day Ahead Desk-Instructions on Scaling of the MTLF | 269 |
| 06/01/2006 | Transmission & Security Desk V3R71 | 268 |
| 06/01/2006 | Frequency Control Desk V3R37 | 267 |
| 06/09/2006 | Transmission and Generation Energize Approval Procedure | 266 |
| 06/26/2006 | Day Ahead Desk - Temporary Solution for RPRS Selecting Certain Blackstart Resources | 271 |
| 06/07/2006 | Maintenance Level 2 & 3 Outages - Frequency Control Desk | 270 |
| 06/01/2006 | Day Ahead Desk-Instructions on Scaling of the MTLF | 269 |

In service notification procedure posted 6/9 (POB 266)

Blackout/Load Shed incidences

6/12 19:42 The following elements were lost:

- Manor – Cedar Hill LCRA 138kV line locked out

- Dessau – Daffin Gin 138kV line locked out

- Dessau – Sprinkle 138kV line locked out

- Double Circuit Dessau – McNeil 138kV lines locked out

- Decker – Sprinkle 138kV line locked out

- Capacitor bank on the 138kV bus at Round Rock tripped

- Decker – McNeil 138kV line was open ended at Decker

- Howard Lane – Techridge 138kV line was open ended at Howard Lane

- Daffin Gin – Austrop 138kV line was open ended at Daffin Gin

- Fiskville – McNeil 138kV line was open ended at Fiskville

3 generators were also lost. 8,828 customers were without power for less than an hour. A fault was detected on phase A near Decker and some relaying issues were suspected at Dessau. An investigation revealed that a post insulator failed on the Decker – Sprinkle 138kV line and the appropriate repairs were made the following week.

Major system voltage problems

None

Voltage Instructions

None

Major Computer Problems, Enhancements & Fixes

Waiting on info from EMMS group.

Communication

None

ERCOT peak (Unofficial)

6/13	15:58	59,018		5/25	17:00	55,050

Other

None

Alerts, OCN, and Emergency Notices

| 1-June | 16:00 | 18:19 | Transmission Alert | Loss of Cedar Hill Sw – Watermill 345kV overloads the Watermill 345/138kV Auto |
| --- | --- | --- | --- | --- |
|  | 16:00 | 18:18 | Transmission Alert | Loss of Norwood Sw - Liggett Sw and - Cedar Hill Sw 345kV overloads the Cedar Hill Sw transformer. |
| 7-June | 18:28 | 20:00 | Transmission Alert | Loss of Valley SES – Commerce Sw 138 kV causes voltage collapse in the area. |
| 9-June | 23:00 | 23:45 | Alert | Second Replacement Reserve Service Market opened for Saturday 06/10/06. |
| 10-June | 00:30 | 24:00 | Emergency Notice | For the Laredo area due to outage on XXXX. |
| 11-June | 0:15 | 24:00 | Emergency Notice | For the Laredo area due to outage on XXXX. |
| 12-June | 0:15 | 10:50 | Emergency Notice | For the Laredo area due to outage on XXXX. |
|  | 14:00 | 22:00 | Transmission Alert | Gibbons Crk-Greens Prairie-Gibbons Creek-East 138 line overloads Dansby-Atkins 138kV above first contingency limit. |
| 14-June | 17:05 | 19:50 | Transmission Alert | At thermal limit on Sandow 345/138 KV Transformer |
| 19-June | 13:49 | 23:00 | Transmission Alert | loss of San Miguel Switchyard 138 kV - San Miguel Switchyard 69 kV overloads Derby - Pearsall 69 kV line. |
|  | 14:04 | 23:00 | Transmission Alert | Transmission Alert issued for loss of Dilley Switch - North Laredo Switch & San Miguel Switchyard 138 kV overloads Derby - Pearsall 69 kV line. |
|  | 14:08 | 23:00 | Transmission Alert | loss of Asherton 138/69 kV Autotransformer overloads the Uvalde 138/69 kV Autotransformer. |
| 20-June | 11:45 | 22:00 | Transmission Alert | loss of Asherton – Escondido 138 kV overloads Uvalde – Asphalt Mines 138 kV |
|  | 11:45 | 22:00 | Transmission Alert | loss of Asherton 138/69 kV Autotransformer overloads Uvalde 138/69 kV Autotransformer. |
|  | 14:13 | 21:30 | Transmission Alert | loss of San Miguel – Pearsall 138 kV overloads Moore - Downie 138 kV line. |
|  | 14:13 | 21:30 | Transmission Alert | loss of San Miguel Switchyard 138 kV - San Miguel Switchyard 69 kV overloads Derby - Pearsall 69 kV |
| 21-June | 01:00 | 01:45 | Alert | second Replacement Reserve Service Market opened for Wednesday 06/21/06 |
|  | 15:22 | 20:55 | Transmission Alert | loss of San Miguel Switchyard 138 kV - San Miguel Switchyard 69 kV overloads Derby - Pearsall 69 kV |
| 22-June | 15:52 | 21:00 | Transmission Alert | loss of Lake Creek - Jewett 138 kV overloads Navarro - Richland 69 kV line. |
|  | 15:53 | 21:00 | Transmission Alert | loss of San Miguel Switchyard 138 kV - San Miguel Switchyard 69 kV overloads Derby - Pearsall 69 kV line |
|  | 16:14 | 21:00 | Transmission Alert | loss of Big Brown - Jewett 345 kV overloads Trinidad - Winkler BEPC 138 kV line. |
| 23-June | 15:14 | 21:30 | Transmission Alert | loss of San Miguel Switchyard 138 kV - San Miguel Switchyard 69 kV overloads Derby - Pearsall 69 kV line |
| 24-June | 14:54 | 19:00 | Transmission Alert | San Miguel 138/69 kV Auto overloads Derby - Pearsall 69 kV line. |
|  | 14:54 | 19:00 | Transmission Alert | loss San Miguel to Sigmor 138kv line overloads Pleasanton Auto |
| 25-June | 11:14 | 12:30 | OCN | capacity shortage hours 16:00 to 18:00 |
|  | 12:30 | 15:00 | Alert | capacity shortage hours 16:00 to 18:00 |
|  | 13:12 | 15:00 | OCN | shortage of UBES bids for hours 16:00 to 19:00 |
|  | 15:25 | 20:00 | Transmission Alert | loss of San Miguel 138/69 kV Auto overloads Derby - Pearsall 69 kV line. |
|  | 15:25 | 20:00 | Transmission Alert | loss of Jewett - Palestine 138kV overloads Palestine - Elkhart 69kV. |