| ### Provide Advanced Notice of Diminishing Responsive Reserve |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves. |
| 1 | IF Total Responsive Reserve is equal to or less than 3300 MW, but greater than 3000MW, issue an Operating Condition Notice (Refer to section 2.6.1 “Issue an Operating Notice (OCN)”). |
| 2 | IF Total Responsive Reserve is equal to or less than 3000MW, but greater than 2500MW, issue an Advisory (Refer to section 2.6.2 “Issue an Advisory”). |
| 3 | IF Total Responsive Reserve is equal to or less than 2500 MW, but greater than 2300MW, issue an Alert (Refer to section 2.6.3 “Issue an Alert”). |
| 3a | Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. |
| 3b | Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing. |
| 3c | Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive reserves. |
| 4 | IF Responsive Reserve is below 2300MW, begin implementing EECP Step 1 (Refer to section 2.6.6 “Implement EECP”). |