## Slide 1: SIMPLE TRANSMISSION OUTAGE
Notes: In order to convey our interpretation of a simple outage, let’s go over a few definitions.

## Slide 2: Nodal Protocol Definition
2.26 Simple Transmission Outage
A Planned Outage or Maintenance Outage of any Transmission Element in the Network Operations Model such that when the Transmission Element is removed from its normal service, absent a Forced Outage of other Transmission Elements, the Outage does not cause a topology change in the LMP calculation and thus cannot cause any LMPs to change with or without the Transmission Element that is suffering the Outage.
Notes: First, the Protocol definition
A Planned Outage or Maintenance Outage of any Transmission Element in the Network Operations Model such that when the Transmission Element is removed from its normal service, absent a Forced Outage of other Transmission Elements, the Outage does not cause a topology change in the LMP calculation and thus cannot cause any LMPs to change with or without the Transmission Element that is suffering the Outage.

## Slide 3: Topology Definition
Topology refers to the shape of a network, or the network's layout. How different nodes in a network are connected to each other and how they communicate are determined by the network's topology. Topologies are either physical or logical.

## Slide 4: Network Topologies
Individual symbols in each example represent a Load, a Generator, or a Bus

## Slide 5: Electrical Network Definition
An electrical network is an interconnection of electrical elements such as resistors, inductors, capacitors, and switches. It can be as small as an integrated circuit on a silicon chip, or as large as an electricity distribution or transmission network.

## Slide 6: Simple Transmission Outage boundaries
Outage must not cause a topology change in the LMP calculation.
Outage request must be submitted at least 1 day prior to the requested start date.
Shall not cause congestion

## Slide 7: Simple Transmission Outage boundaries
Shall not violate applicable reliability standards.
Limited to 12 hours or less in duration.
restoration time shall not exceed 1 hour.

## Slide 8: Example 1:
ERCOT Model must indicate switch position is normally open
Line can be taken out as a simple outage.
A
D
C
B
Individual symbols represent a Load or a Bus

## Slide 9: Example 2:
cb
cb
cb
cb
cb
cb
cb
cb
cb
cb
Line can be taken out as a simple outage.
Bus Outage
cb
cb

## Slide 10
Generator
Load or Bus
Generator
Line can be taken out as a simple outage.
Generator breakers can be taken out as a Simple Outage provided the Unit is on a Planned Outage.
Example 3:
cb
cb
cb
cb

## Slide 11: Example 1:
Switching of energized Transmission voltage level devices that directly connect to normally open-ended line segments and will not swap load or change load flow direction.
Notes: LMPs are calculated using a DC solution.

## Slide 12: Example 2:
With certain restrictions, an ongoing bus outage may be expanded to include directly connected lines that were open-ended by the bus outage if the requesting TO controls all involved equipment. The line(s) must have a single switch or breaker to isolate it from the remaining energized system. To qualify for this expansion, the opposite end of the line/equipment newly included in the existing outage must be isolated from the next bus through opening a single switch or breaker.

## Slide 13: Example 3:
Maintenance work on breakers that directly connect to a generator if the unit is scheduled off line due to a planned or forced outage. The maintenance work may be expanded to include the line open ended by that breaker, if the line segment can be isolated by a single switch or breaker. The maintenance must end prior to the unit becoming available and must not delay the unit’s ability to return to service nor affect the unit(s)’ capability.

## Slide 14
Questions ?

## Slide 15: Topology Definition
Topology refers to the shape of a network, or the network's layout. How different nodes in a network are connected to each other and how they communicate are determined by the network's topology. Topologies are either physical or logical. Below are diagrams of the most common network topologies.
Mesh Topology
  Devices are connected with many redundant interconnections between network nodes. In a true mesh topology every node has a connection to every other node in the network.
Bus Topology
All devices are connected to a central cable, called the bus or backbone.
Ring Topology
All devices are connected to one another in the shape of a closed loop, so that each device is connected directly to two other devices, one on either side of it.
Tree Topology
A hybrid topology. Groups of star-configured networks are connected to a linear bus backbone.
Notes: Topology refers to the shape of a network, or the network's layout. How different nodes in a network are connected to each other and how they communicate are determined by the network's topology. Topologies are either physical or logical.