## Slide 1
M. Kezunovic, G. Huang, TAMU
M. Grady, S. Santoso, UT Austin
W-J. Lee, UT Arlington
ERCOT, August 11, 2006
©2006 Mladen Kezunovic. All rights reserved
Use of synchronized sampling in substations and system-wide applications

## Slide 2: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 3: CCET and TEES
CCET:
- Formed in September 2005
- Funded by members: TXU, CNP, AEP-Texas, Austin
Energy, Freescale, National Instruments
- Focused on commercialization investments
TEES:
- State Agency managed by Texas A&M University
- Leader of a consortium of universities (TxCEE)
- Interested in working with CCET on development of
new solutions (Synchronized Sampling Project)

## Slide 4: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 5: Scope of Work
Introduce new concept of data integration and information exchange
Explore the use of synchronized samples
Make products to facilitate the use
Demonstrate the benefits
Define a commercialization path

## Slide 6: The Main Idea
Transmission Line
Current
Transformer
Bus
Contact
“A”
Contact
“B”
Capacitive
Voltage
Transformer
)
Current
Voltage
(
(
CBM
DPR
DFR
CB

## Slide 7: Background
CFL
MS
PE
EMS
LMS
FL
IS
SC
RC
DFR
CBM
DPR
RTU
SOE
A
S
A
S
A
A
S
A
S
A
S
LEVEL I
CENTRALIZED LOCATION
LEVEL II
SUBSTATION
LEVEL III
SWITCHYARD INTERFACE

## Slide 8: Concept
DPRs
CBMs
RTUs
DFRs
SERs
PLCs
Data Integration
Information Exchange
PQ
Meters
Database:
Raw and pre-processed measurements
System configuration data

## Slide 9: Information Users
Summary
Report
Comprehensive
Report
Brief Report
Engineer
Dispatcher
Technician
Reports can be customized according to the need of a particular category of users and disseminated via fax, e-mail, website, pager, etc.

## Slide 10
Email, Fax, Hosting, WWW, Pager Notification
Intranet Internet
Wide-area networks
(hubs, routers, gateways)
System wide analysis
Mobile Agent Server
System wide control
COMTRADE IEC 61850
Substation Analysis and Control
RTU
DPR
SER
CBM
PMU
DFR
GPS
Substation Analysis and Control
DFR
RTU
SER
PMU
DPR
CBM
GPS

## Slide 11: Scope of Work
Task #1: Development of New Field Equipment (CB Monitor, field test set)
Task#2: Deployment of new applications (substations, control Center, ERCOT)
Task #3: Exploration of new services (Calibration Lab and Economic study of benefits)

## Slide 12: Products
Substations:
- Circuit Breaker Monitor (CBM), Task#1A
- CBM analysis (CBMA), Task#2B&2D
- DFR analysis (DFRA), Task#2B&2D
- DPR analysis (DPRA), Task#2B&2D
- Integrated substation analysis, Task#2C&2D
Test Equipment:
- Certification and calibration lab, Task#3A
- Field test equipment for GPS-enabled IEDs,
Task #1B

## Slide 13: Products
Control Center:
- Fault location, Task#2B&2D
ERCOT:
- Alarm Processor, Task#2A
- Voltage Security, Task#2A
- Sate Estimator, Task#2A
- Model Verification, Task#2A
Study of Economic Benefits, Task#3B

## Slide 14: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Automated Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 15: Substation applications
Developed CBM
Developed CBMA, DPRA, DFRA
Performed testing in TAMU labs
Designed client-server architecture
Started field demonstration

## Slide 16: Substation Application Overall Architecture

## Slide 17: IED connections Field Setup

## Slide 18: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 19: ERCOT Analysis Applications
Use of Synchronized samples
- Alarm Processor
- Voltage Security
- State Estimator
- Model Verification
Graphical Interfaces for operators

## Slide 20: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 21: Synchronized sampling utilization
Take advantage of synchronized samples coming from variety of IEDs (DFRs, DPRs, CBMs, etc)
Use extracted features from the measured data (phasors, switching times, parameters)
Correlated features using GPS-precision time-stamps

## Slide 22: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 23: Field deployment and demonstration
Alarm Processor:
- Automate Cause-effect analysis of
alarms using GPS synchronization
- Use data from other IEDs in
addition to RTUs
- Incorporate the information into
SCADA database
- Make enhancement to existing
operator displays
- Archive detailed information and
raw data for reporting purposes

## Slide 24: Field deployment and demonstration
Voltage Security:
- Calculate static stability margin index for
the voltage regulated buses
- Use of GPS-synchronized measurements
from IEDs located at neighboring buses
- Use voltage stability index for estimating
security margin of transactions
- Make enhancement to existing operator
displays by introducing a warning
- Archive trends for future training uses and
transaction estimated

## Slide 25: Field deployment and demonstration
State Estimator:
- Use GPS-synchronized data from
other IEDs in addition to RTUs
- Incorporate Synchronized Phasor
measurements to improve accuracy
- Improve Topology Processor by
using Synchronized CBM status data
- Make enhancement to existing
operator displays with time-stamps
- Monitor performance of the existing
SE by comparing the results with
GPS-synchronized measurements

## Slide 26: Field deployment and demonstration
Model Verification:
- Use GPS-Synchronized measurements
from other IEDs in addition to RTUs
- Compare system responses (measured)
against simulations (using models)
- Measure dynamic responses (machines
and loads) and estimate parameters
- Make enhancement to existing operator
displays by adding measurements
- Update the models “Continuously”

## Slide 27: Benefits
Reliability of ERCOT system
Technology demonstration
Leveraging R&D funds
Products development to meet ERCOT needs

## Slide 28: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 29: ETF Application
April 3, 2006: CCET Board Approval
August 3, 2006: TO’s feedback
August 11, 2006: ROS vote
August ???, 2006: CCET Board Approval of the commercialization plan
September???, 2006: ERCOT Board Approval
September 27, 2006: ETF Application Deadline
Nov/Dec 2006: ETF award decision
January 2007: start of work

## Slide 30: Outline
Who are we: CCET and TEES
What have we proposed to do: Scope of Work
What have we already accomplished: Substation Applications
What is the opportunity available to ERCOT: Analysis Applications
What is the scope of work for ERCOT: Synchronized Sampling Utilization
What are the expected deliverables and benefits: Field Deployment and Demonstration
What is the timing: ETF Application
Conclusion

## Slide 31: Conclusions
Initial substation developments will be completed in FY2006 and demonstrated in FY2007
Host utility in FY2006 will be CNP (two substations) with a possible extension to AEP-Texas and TXU in FY2007
Development of ERCOT applications will be initiated in FY2007
ETF support will bring match-funding for FY2007
Other match-funding will come from EPRI, DOE and ERCOT (pending budget approval)
Three TxCEE universities will be involved in development; TEES will be the Lead institution
Commercialization plan will be outlined