## Slide 1: PDCWG Report Aug 10, 2006 Objectives
Frequency Performance June and July
ERCOT CPS1
RMS1 data and NERC Outlier assessment.
ERCOT Frequency Response and Shoulder Month Bias recommendation
ERCOT Frequency below 59.910 and Responsive Reserve Service not deployed (July 27, 2006)

## Slide 2: PDCWG Report Objectives Continued
Joint meeting with the WMS FCTF
Nodal assignment
  Non-Spin deployment
  Bias Setting
ERCOT support
  Operations
  Compliance

## Slide 10
The NERC Resources Subcommittee is demonstrating the usefulness of RMS1 data in evaluating interconnection frequency and reliability. RMS1 “Outlier” days were identified and events that contribute to the higher RMS1 values were reported.

## Slide 11: ERCOT Frequency Response Performance
Point “B” and “B+30” frequency response is calculated
  Shoulder months (Oct-April) performance “averaged” for ERCOT frequency control Bias setting.
  Summer months (May-Sept) performance “averaged” for ERCOT frequency control Bias setting.
2005-2006 Shoulder month Bias calculated to be 520.25 MW/0.1 Hz.

## Slide 12
Trend line 30 event rolling average

## Slide 13
Trend line 30 event rolling average

## Slide 14
Trend line 30 event rolling average

## Slide 15
Trend line 30 event rolling average

## Slide 16
Trend line 25 event rolling average

## Slide 17
ERCOT Seasonal Frequency Response (Oct ’05 through Apr ’06)
Average of B & B+30 = 520.25 MW/0.1 Hz

## Slide 18: Responsive Reserve Service not deployed

## Slide 19: Market Participant Frequency Values

## Slide 20: FCTF and PDCWG Joint Meeting
PDCWG recommended that the ERCOT minimum frequency response from resources (that respond to high and low frequency deviation outside +/- 0.036 Hz) be 420 MW/0.1 Hz
  The FCTF reported to WMS that the minimum ERCOT frequency Bias should be 420 MW/0.1 Hz. This is considerably lower than the PDCWG’s recommendation since Bias includes firm load’s response to frequency.
The PDCWG recommended that all resources must have an operating governor and that the governor must be in service.
  The FCTF recommends that non-bidders of Governor Response Service are not required to have governors in service.

## Slide 21: Joint Meeting Continued
The FCTF recommended that there should be a Governor Response Service. The PDCWG agreed.
The FCTF wants the bid process to be on a portfolio basis in a zonal market and per unit basis in a nodal market.
  The PDCWG expressed concerns that a unit operating at its LOL or HOL and awarded GRS would be unable to respond beyond these limits. The PDCWG agreed that individual resource performance measurements would be necessary in the nodal market.

## Slide 22: Nodal Market Frequency Control Bias Setting and Non Spin Deployment Procedure
Bias Setting determination should be similar to zonal market procedure. Draft procedure is included.
Non-Spin Deployment
  Different than present zonal deployment.
    Presently an energy deployment that has caused some frequency control problems at both the beginning deployment period and recall period.
    Nodal Non-Spin is a capacity deployment with on-line resources making reserved non-spin capacity available to SCED and off-line resources brought on-line to LOL and its capacity made available to SCED. Non-spin capacity is then deployed like all other capacity available to SCED.

## Slide 23: Nodal Non-Spin Deployment
30 minutes from notification of deployment to time non-spin capacity is made available to SCED.
ERCOT Operations should be able to deploy Non-spin at any time.
  In response to a Resource loss to restore Responsive Reserves if capacity available to SCED is less than needed to restore RRS and a minimum Reg Up reserve.
  In response to capacity shortages due to Load Forecast errors, capacity limits on resources or non-congested capacity available to SCED is less than minimum capacity reserve limit. This limit could be similar to the present 7% paper reduction in available reserves.
  In response to maintaining a minimum amount of Up Regulation Service availability for peak load.

## Slide 24: ERCOT Operations and Compliance working group support
Thanks to Jeff Healy and Robert Staples for their past support and hard work they gave the PDCWG.
Thanks to Chad Thompson for his interim support of the PDCWG.