| NPRR Number | 019 | NPRR Title | Black Start Testing Requirements |
| --- | --- | --- | --- |
| Nodal Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 8.1.2.2.6, System Black Start Capability |  |
| Revision Description |  | Specifies the requirements for starting the next start Resource; Specifies which tests are allowed to be run simultaneously. |  |
| Reason for Revision |  | ERCOT's practice of conducting next start Resource tests when new next start Resources are selected is not documented. Also, the Protocols are unclear as to which tests may be conducted simultaneously. |  |
| Reason for Revision (from Transition Plan Task Force (TPTF) Charter Scope) |  | (1) Revisions resulting from Commission orders; (2) Clarifications of Protocol language that do not change the intent or technical specifications of the Protocols; (3) Correction of technical errors or processes that are found to not be technically feasible; (4) Revisions to the Protocols necessary to implement the results of the value engineering analysis or to otherwise avoid severe cost impacts; or (5) Other (describe): Make corresponding changes to nodal Protocols proposed in PRR682. |  |
| TPTF Review (Yes or No, and summary of conclusion) |  |  |  |
| Credit Implications (Yes or No, and summary of impact) |  | None. |  |
| Timeline |  |  |  |
| Date Posted |  | 8/23/06 |  |
| Please access the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | David Wood on behalf of Black Start Task Force |
| E-mail Address | david.wood@austinenergy.com |
| Company | Austin Energy |
| Company Address | 301 West Ave. Austin, Tx. 78701 |
| Phone Number | 512-322-6940 |
| Fax Number | 512-476-9420 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive NPRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the NPRR.

| Assumptions | 1 | NPRR documents current practices. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | None | None |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Clearly defines Black Start testing practices |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

Proposed Nodal Protocol Language Revision

8.1.2.2.6	System Black Start Capability

(1)	A Resource is qualified to be a Black Start Resource if it has met the following requirements:

(a)	Verified control communication path performance;

(b)	Verified primary and alternate voice circuits for receipt of instructions;

(c)	Passed the Basic Starting Test;

(d)	Passed the Line-Energizing Test;

(e)	Passed the Load-Carrying Test; and

(f) 	Has started the next-start unit, or has started the next-start unit’s largest required motor and satisfied the next-start unit’s minimum startup Load requirements; or has been demonstrated to the satisfaction of ERCOT staff through simulation studies conducted by the Black Start Service provider or a qualified third party, to be capable of starting the next-start unit’s largest required motor while meeting the next-start unit’s minimum startup Load requirements.  Potential Black Start Service bidders may request next-start unit information from ERCOT prior to the selection process to satisfy this requirement.  ERCOT shall require this information from the designated next-start unit as follows:  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate black start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource, or the Generation Resource Entity to ERCOT within 30 days or less;

(g)	If not starting itself, has an ERCOT-approved firm standby power contract with deliverability under ERCOT blackout circumstances from a provider not inside the ERCOT Interconnection that can be finalized upon selection as a Black Start Resource;

(h)	If not starting itself, has an ERCOT approved agreement with the necessary TDSPs for access to another power pool, for coordination of switching during a black-start event, for coordination of maintenance through the ERCOT Outage scheduler for all non-redundant transmission startup feeds; and

(i)	If dependent upon non-ERCOT transmission resources, agreements providing this Transmission Service have been provided in the proposal.

(2)	On successful demonstration of system Black Start Service capability, ERCOT shall certify that the Black Start Resource is capable of providing system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource.  Qualification is valid for one year from the date of the last successful Basic Starting Test, three years from the date of the last successful Line-Energizing Test, or six years from the date of the last successful Load-Carrying Test, whichever is earliest.  ERCOT shall revoke the Resource’s qualification if the Black Start Resource fails to perform successfully during an actual restoration event, until the Black Start Resource is successfully retested.  Retesting is required only for the aspect of system Black Start Service capability (basic starting, line-energizing, or Load-carrying) for which the Black Start Resource failed.

(a)	The “Basic Starting Test” includes the following:

(i)	The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another provider not inside the ERCOT Interconnection, without support from the ERCOT System;

(ii)	Annual testing, either as a stand-alone test or part of the Line Energizing and Load Carrying Tests, and the test is preformed during a one-week period agreed to in advance by the Black Start Resource and ERCOT and must not cause outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(iii)	Confirmation of the dates of the test with the Black Start Resource by ERCOT;

(iv)	Initiation of the test at a time during a previously agreed test week window not previously disclosed to the Black Start Resource;

(v)	Isolation of the Black Start Resource, including all auxiliary Loads, from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT Interconnection if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of a non-ERCOT Control Areae ERCOT Interconnection through a firm standby agreement will connect to the non-ERCOT Control Areaprovider not inside thn, start-up, carry internal Load, disconnect from the non-ERCOT Control Areaprovider not inside the ERCOT Interconnectiough a black-start capable DC Tie, and continue equivalently to what is required of other Black Start Resources;

(vi)	The ability of the Black Start Resource to start without assistance from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT Interconnection if the startup power is supplied by a firm standby contract;

(vii)	The ability of the Black Start Resource to remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least 30 minutes; and

(viii)	The Black Start Resource must have verified that its Volts/Hz relay, over-excitation limiter, and under-excitation limiter are set properly and that no protection devices will trip the Black Start Resource within the required reactive range. The Resource Entity for the Black Start Resource shall provide ERCOT with data to verify these settings.

(b)	The “Line-Energizing Test” must be conducted at a time agreed on by the Black Start Resource, TSP or DSP, and ERCOT and includes the following:

(i)	Energizing transmission with the Black Start Resource when conditions permit as determined by the TSP or DSP but at least once every three years;

(ii)	De-energizing sufficient transmission in such manner that when energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan requires the Black Start Resource to supply.  ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource;

(iii)	Conducting a Basic Starting Test;

(iv)	Energizing transmission with the Black Start Resource of the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line.  Alternatively, if ERCOT agrees, the transmission line may be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed; and

(v)	Stable operation of the Black Start Resource (in both frequency and voltage) while supplying only its auxiliary Loads or external Loads for at least 30 minutes.

(vi)	This test can be performed together with the Basic Starting Test in one thirty (30) minute interval.

(c)	The “Load-Carrying Test”  shall be tested as conditions permit, but at least once every six years and includes the following:

(i)	Stable operation of the Black Start Resource (in both frequency and voltage) while supplying restoration power to Load specified by ERCOT’s restoration plan for the Black Start Resource.

(ii)	Conducting a Basic Starting Test;

(iii)	Conducting a Line-Energizing Test; and

(iv)	The TSP or DSP operator for the Black Start Resource shall direct picking up sufficient Load to demonstrate the Black Start Resource’s capability to supply the required power identified in ERCOT’s restoration plan, while maintaining voltage and frequency for at least 30 minutes.

(v)	This test can be performed together with the Basic Starting Test and Line Energizing test in one thirty (30) minute interval.

(d)	Next Start Resource Test:

(i)	The ability of a Black Start Resource to start up the Next Start unit’s largest required motor while continuing to remain stable and control voltage and frequency shall be tested. This test shall be repeated when a new next start unit is selected;

(ii)	Conduct a Basic Starting Test;

(iii)	Conduct a Line Energizing Test;

(iv)	Conduct a Load Carrying Test as a stand-alone test or part of the Next Start Resource Test;

(v)	The Black Start Resource must remain stable (in both voltage and frequency) and controlling voltage for thirty (30) minutes; and

(vi)	This test can be performed together with the Basic Starting Test, Line Energizing Test, and Load Carrying Test in one thirty (30) minute interval.

(3)	ERCOT shall revoke the Resource’s qualification as a Black Start Resource for that year in the event the Black Start Resource fails to perform successfully during an actual ERCOT System blackout event and the Resource has been declared available, as defined in Section 9B(1) of Section 22, Attachment A, Standard Form Black Start Agreement.