Texas Nodal

Energy Management System

Software Requirements Specification

For SCADA

Version 0.8

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 8/4/2006 | 0.3 | Edits, revisions and new requirements by A. Boecker | A. Boecker |
| 8/7/2006 | 0.4 | General formatting clean up and verification. Use Cases removed. New requirements added. | KEMA |
| 8/16/2006 | 0.5 | Edits and revisions | A. Boecker |
| 8/23/2006 | 0.6 | Implement comments from IDA and Testing group | J Mandavilli/A Boecker |
| 8/23/2006 | 0.7 | Implement comments from IDA and Testing group | J Mandavilli/A Boecker |
| 8/25/2007 | 0.8 | Implement comments from IDA received on 8/24/06 | J Mandavilli/ A Boecker |

Table of Contents

1.	Supervisory Control and Data Acquisition (SCADA)	3

1.1	Proposed System Scope	3

1.2	Business processes impacted	3

1.3	AS Is and To Be Processes	3

1.3.1	As Is SCADA	3

1.3.2	To Be SCADA	3

1.3.3	Differences between the As Is and To Be	3

1.3.4	Standard SCADA functionality:	3

1.4	Assumptions and Dependencies	3

2.	Definitions and Acronyms	3

2.1	Definitions	3

Resource	3

All-Inclusive Generation Resource	3

All-Inclusive Resource	3

Generation Resource	3

Load Resource	3

Non-Modeled Generator	3

2.2	Acronyms and Abbreviations	3

3.	Functional Requirements	3

4.	Supplementary Requirements	3

5.	Protocol Coverage	3

6.	Sub-Process Coverage	3

Software Requirements Specification

# Supervisory Control and Data Acquisition (SCADA)

SCADA is a sub-system of the Energy management System (EMS). Its primary function is serving as the dispatching and telemetry interface to QSE and TDSP organizations.

SCADA outputs will be used as inputs to the State Estimator application, Alarming Application, Load Frequency Control, and other EMS and MMS applications.  ERCOT currently monitors approximately 20,000 analog measurements, and 28,000 status measurements.  It is expected that compliance with nodal protocols will require the expansion of SCADA telemetered points to over 30,000 analog measurements and 40,000 status measurements.

ERCOT currently sends approximately 700 analog values using SCADA.  This number will increase to approximately 6900 analog values before Texas Nodal.  With Texas Nodal, ERCOT will initially be sending approximately 7900 analog values.

## Proposed System Scope

ERCOT plans to implement a new Nodal Market in 2009. Sections 3, 4 and 6 of the Nodal Protocols describe the various requirements for SCADA.

This document defines the requirements for SCADA. The requirements in scope for this document include:

- TDSP input data (including breaker status, switch status, dynamic ratings, Block Load Transfers data)

- QSE input data (including resource status)

- ERCOT data override capability

- Outputs to QSEs (inputs from LFC)

- Alarming

- Stale data detection

- Quality code processing (all input and output data shall have quality code)

- Database structure modifications

- Inputs from WGR entities (data written to SCADA database)

- SCADA calculations (including hourly meteorological data, dynamic schedules, resource status)

## Business processes impacted

- Operations Support Engineering

- Operations Planning

- System Operations

## As Is and To Be Processes

### As Is SCADA

An “As Is” Sub process map for Process and Monitor Telemetry was not available.

### To Be SCADA

### Differences between the As Is and To Be

There is very little change in the SCADA processing but there are changes in the types and amount of data. There is the addition of alarm processing on specific data elements coming from QSE and TDSP participants.

### Standard SCADA functionality

SCADA’s primary functionality is to scan from and send to QSE and TDSP entities real-time and operational data via RTU and ICCP data links. It is the primary link between the EMS’s front end interface to outside entities and the EMS database. It does not transmit or process XML data or messages.

The SCADA application will receive both status and analog data from both ICCP and RTU services, external processes, State Estimator, and manually entered data.  For the purposes of this document, communication services are considered as part of “SCADA”.  When an analog measurement is received; SCADA will check data against reasonability limits, check time receipt for identification of stale data, perform conversion to engineering units if needed, assigns quality codes, checks measurements against alarm limits, alarms operators, and saves data into the SCADA database for use by other applications.  When a status measurement is received, SCADA will check the new status against the last status of this measurement, assigns quality code, and alarms operators if a status change is noted; SCADA will also support basic calculations.

## Assumptions and Dependencies

- Planned Outage information for Resources and Transmission equipment, as described in the TAC Approved Telemetry Standards Document, will not be transmitted to ERCOT via SCADA.

- Network transmission model and constraints data, as described in the TAC Approved Telemetry Standards Document, will not be transmitted to ERCOT via SCADA.

- Assume that generator frequency bias is not a telemetered value from the QSE.

- Supporting communication of data between ERCOT and Market Participants through ICCP and or RTU is still under study and this requirements document assumes that it is possible to communicate through both ICCP and RTU.

- ERCOT understands that the items indicated in Section(s) 6.5.7.1.13 (1)  includes telemetered data as well as modeling and calculated data. Normal status is modeling data and the MVA is calculated value within SCADA.

.

# Definitions and Acronyms

## Definitions

Area Control Error (ACE) - A calculation of the MW correction needed to control the actual system frequency to the scheduled system frequency.

Base Point - The MW output level for a Resource produced by the SCED process.

Combined-Cycle Configuration - Any combination in which a combined-cycle power block can be operated as a separate Resource. Each possible configuration operated as a separate Resource has a distinct set of operating parameters, physical constraints, and Energy Offer Curve.

Combined-Cycle Configuration Number – Specifies the operating configuration of the steam and gas units of a combined-cycle generator.

Current Operating Plan (COP) - A plan by a QSE reflecting anticipated operating conditions for each of the Resources that it represents for each hour in the next seven Operating Days, including Resource operational data, Resource Status, and Ancillary Service Schedule.

DSR Loads - A Load that a QSE designates to be followed by a Dynamically Scheduled Resource.

Dynamically Scheduled Resource (DSR) - A Resource that has been designated by the QSE, and approved by ERCOT, as a DSR status-type and follows a DSR Load.

Electric Reliability Council of Texas, Inc. (ERCOT) - A Texas nonprofit corporation that has been certified by the PUCT as the Independent Organization, as defined in §39.151 of PURA, for the ERCOT Region.

Flexible Alternating Current Transmission (FACT) Devices – A category of transmission devices consisting of:

- Static Var Compensator

- Static Synchronous Compensator

- Static Synchronous Generator

- Static Synchronous Series Controller

- Unified Power Flow Controller

- Interface Power Controller

- Thyristor Controlled Series Capacitor

- Battery Energy Storage System

Generation Resource (See Resource)

Generator breaker status – The status of a generator’s breaker used to determine its on-line status

Generator DRS block – The status of the inhibit of a generator’s ability to provide down regulation

Generator DRS participation factor The percentage of a QSE’s down regulation allocated to a specific generator as assigned by the QSE.

Generator emergency ramp rate - The maximum rate of change in MW per minute of a Resource to provide Responsive Reserve that is deployed by ERCOT and that is provided to ERCOT in up to ten segments, each represented by a single MW per minute value (across the capacity of the Resource), which describes the available rate of change in output for the given range (between HSL and LSL) of the output of a Resource.

Generator Gross (with auxiliary) or net real power – The current output of the generator in MW

Generator High Emergency Limit – Limit established by the QSE describing the maximum temporary unsustainable energy production capability of the Resource. This limit must be achievable for a time stated by the QSE, but not less than 30 minutes.

Generator High Sustained Limit- Limit established by the QSE, continuously updated in Real Time, that describes the maximum sustained energy production capability of the Resource.

Generator Low Emergency Limit– Limit established by the QSE describing the minimum temporary unsustainable energy production capability of the Resource. This limit must be achievable for a period of time indicated by the QSE but not less than 30 minutes.

Generator Low Sustained Limit- Limit established by the QSE, continuously updated in Real-Time, that describes the minimum sustained energy production capability of the Resource.

Generator Non-Spin designation/schedule – An indication of whether a generator is to provide non-spin reserve and its associated schedule

Generator normal ramp rate - The rate of change in megawatts (MW) per minute of a Resource, which is specified by the QSE to ERCOT by up to ten segments; each segment represents a single MW per minute value (across the capacity of the Resource) that describe the available rate of change in output for the given range (between HSL and LSL) of output of a Resource.

Generator Reg-Down designation/schedule – An indication of whether a generator is to provide downward regulation and its associated schedule

Generator Reg-Up designation/schedule – An indication of whether a generator is to provide upward regulation and its associated schedule

Generator Responsive Reserve designation/schedule – An indication of whether a generator is to provide responsive reserve and its associated schedule

Generator RRS participation factor – The percentage of a QSE’s responsive reserve allocated to a specific generator as assigned by the QSE

Generator URS block – The status of the inhibit of a generator’s ability to provide up regulation

Generator URS participation factor – The percentage of a QSE’s up regulation allocated to a specific generator as assigned by the QSE

High Ancillary Service Limit (HASL) - A dynamically calculated MW upper limit on a Resource to reserve the part of the Resource’s capacity committed for Ancillary Service, calculated as described in Section 6.5.7.2, Resource Limit Calculator.

High Emergency Limit (HEL) - Limit established by the QSE describing the maximum temporary unsustainable energy production capability of the Resource. This limit must be achievable for a time stated by the QSE, but not less than 30 minutes.

High Sustained Limit (HSL for a Generation Resource) - Limit established by the QSE, continuously updated in Real Time, that describes the maximum sustained energy production capability of the Resource.

High Sustained Limit (HSL for a Load Resource) - Limit calculated by ERCOT, using the QSE-established Low Power Consumption.

JOU – Jointly owned unit (Physical generating unit represented by multiple QSEs).

LAAR breaker status – A status indicating whether a LAAR is connected to the grid

LAAR DRS participation factor – The percentage of a QSE’s down regulation allocated to a specific generator as assigned by the QSE

LAAR LPC - Limit established by the QSE, continuously updated in Real-Time that describes the minimum sustained power consumption of the Load Resource.

LAAR MPC - Limit established by the QSE, continuously updated in Real-Time that describes the maximum sustained power consumption of the Load Resource.

LAAR MW – The current load at a Load Acting As A Resource (LAAR)

LAAR Non-Spin designation/schedule – An indication of whether a LAAR is to provide non-spin reserve and its associated schedule

LAAR Reg-Down designation/schedule - An indication of whether a LAAR is to provide down regulation and its associated schedule

LAAR Reg-Up designation/schedule – An indication of whether a LAAR is to provide up regulation and its associated schedule

LAAR relay status – The status of a Load Acting As A Resource (LAAR) breaker used to determine its on-line status

LAAR Responsive Reserve designation/schedule - An indication of whether a LAAR is to provide responsive reserve and its associated schedule

LAAR RRS participation factor – The percentage of a QSE’s responsive reserve allocated to a specific LAAR as assigned by the QSE

LAAR URS participation factor - – The percentage of a QSE’s up regulation allocated to a specific LAAR as assigned by the QSE

Load - The amount of energy in MWh delivered at any specified point or points on a system.

Load Frequency Control (LFC) - Deployment of those Generation Resources that are providing Regulation Service to ensure that system frequency is maintained within predetermined limits and deployment of those Generation Resources that are providing Responsive Reserve Service when necessary as backup regulation.

Load Resource (See Resource)

Load Serving Entity - An Entity that sells energy to Customers or Wholesale Customers and that has registered as an LSE with ERCOT. Load Serving Entities include Competitive Retailers (which includes Retail Electric Providers) and Non-Opt-In Entities that serve Load.

Locational Marginal Price (LMP) - The offer-based marginal cost of serving the next increment of Load at an Electrical Bus, which marginal cost is produced by the DAM process or by the SCED process.

Low Ancillary Service Limit (LASL) - A dynamically calculated MW lower limit on a Resource to maintain the ability of the Resource to provide committed Ancillary Service.

Low Emergency Limit (LEL) - Limit established by the QSE describing the minimum temporary unsustainable energy production capability of the Resource. This limit must be achievable for a period of time indicated by the QSE but not less than 30 minutes.

Low Power Consumption (LPC for a Load Resource) - Limit established by the QSE, continuously updated in Real-Time, that describes the minimum sustained power consumption of the Load Resource.

Low Sustained Limit (LSL for a Load Resource) - Limit calculated by ERCOT, using the QSE-established Maximum Power Consumption.

Low Sustained Limit (LSL for a Generation Resource) - Limit established by the QSE, continuously updateable in Real-Time, that describes the minimum sustained energy production capability of the Resource.

Maximum Power Consumption (MPC for a Load Resource) - Limit established by the QSE, continuously updated in Real-Time, that describes the maximum sustained power consumption of the Load Resource.

Non-Spinning Reserve (Non-Spin) - An Ancillary Service that is provided through use of the part of Off-Line Generation Resources that can be synchronized and ramped to a specified output level within 30 minutes (or Load Resources that can be interrupted within 30 minutes) and that can operate (or Load Resources that can be interrupted) at a specified output level for at least one hour. Non-Spinning Reserve Service (Non-Spin) may also be provided from unloaded On-Line capacity that meets the 30-minute response requirements and that is reserved exclusively for use for this service.

Off-Line - The status of a Resource that is not synchronously interconnected to the ERCOT System.

On-Line - The status of a Resource that is synchronously interconnected to the ERCOT System.

Qualified Scheduling Entity (QSE) - A Market Participant that is qualified by ERCOT in accordance with Section 16, Registration and Qualification of Market Participants, for communication with ERCOT for Resource Entities and Load Serving Entities and for settling payments and charges with ERCOT.

Real-Time - The current instant in time.

Regulation Down Service (Reg-Down) - An Ancillary Service that provides capacity that can respond to signals from ERCOT within three to five seconds to respond to changes in system frequency.  Such capacity is the amount available below any Base Point but above the Low Sustained Limit of a Generation Resource and may be called on to change output as necessary throughout the range of capacity available to maintain proper system frequency. A Load Resource providing Reg-Down must be able to increase and decrease Load as deployed within its Ancillary Service Schedule for Reg-Down below the Load Resource’s Maximum Power Consumption limit.

Regulation Service - Consists of Regulation Up Service and Regulation Down Service.

Regulation Up Service (Reg-Up) - An Ancillary Service that provides capacity that can respond to signals from ERCOT within three to five seconds to respond to changes in system frequency.  Such capacity is the amount available above any Base Point but below the High Sustained Limit of a Generation Resource and may be called on to change output as necessary throughout the range of capacity available to maintain proper system frequency.  A Load Resource providing Reg-Up must be able to increase and decrease Load as deployed within its Ancillary Service Schedule for Reg-Up above the Low Power Consumption limit.

Reliability Must-Run (RMR) Service - An Ancillary Service provided from a Reliability Must-Run Unit under an Agreement with ERCOT.

Reliability Must-Run (RMR) Unit - A Generation Resource operated under the terms of an Agreement with ERCOT that would not otherwise be operated except that it is necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria where market solutions do not exist.

Resource

A term used to refer to both a Generation Resource and a Load Resource. “Resource” used by itself in these Protocols does not include a Non-Modeled Generator.

All-Inclusive Generation Resource

A term used to refer to both a Generation Resource and a Non-Modeled Generator.

All-Inclusive Resource

A term used to refer to a Generation Resource, Load Resource and a Non-Modeled Generator.

Generation Resource

A generator that is capable of providing energy or Ancillary Service to the ERCOT System and is registered with ERCOT as a Generation Resource. “Generation Resource” used by itself in these Protocols does not include a Non-Modeled Generator.

Load Resource

A load that is capable of providing Ancillary Service to the ERCOT System and is registered with ERCOT as a Load Resource.

Non-Modeled Generator

A generator that is:

(1)	Capable of providing net output of energy to the ERCOT System;

- 10 MW or less in size; and

- Registered with ERCOT as a Non-Modeled Generator, which means that the generator may not participate in the Ancillary Service or energy markets, RUC, or SCED.

Resource Status – The status of a generator or LAAR reported by the QSE

Generation Resource - A generator that is capable of providing energy or Ancillary Service to the ERCOT System and is registered with ERCOT as a Generation Resource. “Generation Resource” used by itself in these Protocols does not include a Non-Modeled Generator.

Load Resource - A load that is capable of providing Ancillary Service to the ERCOT System and is registered with ERCOT as a Load Resource.

Resource Status - The operational state of a Resource as provided in Section 3.9, Current Operating Plan (COP).

Responsive Reserve - An Ancillary Service that provides operating reserves that is intended to:

Arrest frequency decay within the first few seconds of a significant frequency deviation on the ERCOT Transmission Grid using governor response and interruptible Load;

After the first few seconds of a significant frequency deviation, help restore frequency to its scheduled value to return the system to normal;

Provide energy or continued Load interruption during the implementation of the Emergency Electric Curtailment Plan (EECP); and

Provide backup regulation.

SCADA – In this document, SCADA consists of both the RTU interface and the ICCP interface (in the protocols, SCADA only refers to the RTU interface).

Transmission and/or Distribution Service Provider (TDSP) - An Entity that is either a Transmission Service Provider or a Distribution Service Provider.

Transmission Service Provider (TSP) - An Entity under the jurisdiction of the PUCT that owns or operates Transmission Facilities used for the transmission of electricity and provides Transmission Service in the ERCOT Transmission Grid.

## Acronyms and Abbreviations

ERCOT	Electric Reliability Council of Texas, Inc.

FACT	Flexible Alternating Current Transmission devices

HASL	High Ancillary Service Limit

ICCP	Inter-Control Center Communications Protocol (TASE.2 Standard)

IDA	Integration and Design Authority

LAAR	Load acting as a Resource

LFC	Load Frequency Control

LPC	Low Power Consumption

MPC	Maximum Power Consumption

MW	Megawatt

NERC	North American Electric Reliability Council

Non-Spin	Non-Spinning Reserve

QSE	Qualified Scheduling Entity

Reg-Down	Regulation Down

Reg-Up	Regulation Up

RRS	Responsive Reserve

RTU	Remote Terminal Unit

SCADA	Supervisory Control and Data Acquisition

SCED	Security-Constrained Economic Dispatch

SME	Subject matter expert

TAC	Technical Advisory Committee

TDSP	Transmission and/or Distribution Service Provider

TSP	Transmission Service Provider

WGR	Wind Generation Resource

# Functional Requirements

## Inputs to SCADA

| Requirement ID | SCD-FR1 |
| --- | --- |
| Requirement Name | Telemetry |
| Protocol Reference | Section(s) 6.5.7.1.1 |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | COPS.P02.I-2 and I-1 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA telemetry shall receive the actual Real-Time status and output of Resources and the status of observable Transmission Elements of the Network Operations Model. |  |

| Requirement ID | SCD-FR7 |
| --- | --- |
| Requirement Name | Input data from TDSPs |
| Protocol Reference | Section(s) 6.5.7.1.13 (1), 3.10.7.4 (1); TAC Approved Telemetry Standards Document |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-2 and I-1 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive available telemetry for use by Network Applications: ## Transmission Electrical Bus voltages ## MW and MVAR pairs for all lines and transformers ## Actual breaker and switch status for all modeled devices ## Tap position for autotransformers - MVAR for capacitor banks, reactors, and FACT devices |  |

| Requirement ID | SCD-FR3 |
| --- | --- |
| Requirement Name | Input Data from QSEs |
| Protocol Reference | Section(s) 6.5.7.2 (1); 6.5.5.2, 6.4.5 (2), 6.5.7.3 (1), 3.15.3 (4); TAC Approved Telemetry Standards Document |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-2 and I-1 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive generator-specific telemetry from QSEs: - Net real power (in MW); - Gross real power (in MW); - Net Reactive Power (in MVar); - Gross Reactive Power (in MVar); - Power to standby transformers serving Plant auxiliary Load; - Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid; - Generation Resource breaker and switch status; - High Sustained Limit; - High Emergency Limit; - Low Emergency Limit; - Low Sustained Limit; - Ancillary Service Schedule for each quantity of Reg-Up, Reg-Down, Responsive Reserve and Non-Spin; and - Reg-Up, Reg-Down and Responsive Reserve Services participation factors that represent how a QSE is deploying the Ancillary Service energy on a percentage basis to specific qualified Resource. - Normal ramp rate - Emergency ramp rate - Block Reg-Up status - Block Reg-Down status - Combined-cycle configuration number - Resource Status SCADA shall receive LAAR-specific telemetry from QSEs: - Ancillary Service Schedule for each quantity of Reg-Up, Reg-Down, Responsive Reserve and Non-Spin - Net real power (in MW) - Relay status - Breaker status - LPC - MPC - Reg-Up, Reg-Down and Responsive Reserve Services participation factors SCADA shall also receive the following QSE data: - System frequency - Dynamic resource schedules by load area - Dynamic load schedules by load area |  |

| Requirement ID | SCD-FR5 |
| --- | --- |
| Requirement Name | Frequency Inputs |
| Protocol Reference | Section(s) 6.5.7.6.1 (3) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1, I-2, and P-1 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive frequency measurements from real time telemetry as well as from Time receivers located at Austin and Taylor sites. |  |

| Requirement ID | SCD-FR8 |
| --- | --- |
| Requirement Name | Dynamic Ratings |
| Protocol Reference | Section(s) 3.10.8 (2) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1, P-3, and P-2 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall accept Dynamic Ratings received from other EMS applications and telemetry into limit analogs consisting of Normal Rating, Emergency Rating and 15-Minute Ratings. |  |

| Requirement ID | SCD-FR12 |
| --- | --- |
| Requirement Name | BLT Inputs |
| Protocol Reference | Section(s): 6.5.9.5 (i) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | COPS.P02.I-1 and I-2 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive telemetry on switching devices at Block Load Transfers’ points. |  |

| Requirement ID | SCD-FR17 |
| --- | --- |
| Requirement Name | WGR Meteorological Telemetry |
| Protocol Reference | Section(s): 3.13 (1) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1 and I-2 |
| Sub-Process Element Coverage | Partial |
| Description: The SCADA function shall receive telemetered meteorological information (wind speed and direction) from WGR Entities. SCADA shall also calculate hourly average meteorological data for the wind speed and direction for each WGR based on the telemetered meteorological data from WGR. |  |

3.2 Output Data to QSEs

| Requirement ID | SCD-FR4 |
| --- | --- |
| Requirement Name | Base Point Outputs to QSEs |
| Protocol Reference | Section(s) 6.5.7.4 (1), 6.3.2 (2) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-5 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall pass Base Point information to the QSE representing each Resource that includes the following information (data received from LFC): Resource identifier that is the subject of the Dispatch Instruction; Status indicator providing notice of Responsive Reserve Deployment requesting dispatch above the Resource’s HASL; Time of the Dispatch Instruction Base Point MW; Status indicator providing notice of pseudo unit dispatch above the Resource’s HASL; SCADA shall pass Emergency Base Point information to the QSE representing each Resource that includes the following information (data received from LFC): Resource identifier that is the subject of the Dispatch Instruction; Time of the Dispatch Instruction Base Point MW; Duration The Base Point information shall be transmitted to the QSE via the ICCP interface as a single data packet. Also, the Emergency Base Point information shall be transmitted to the QSE via the ICCP interface as a single data packet. All Emergency Base Point and Base Point data is sent to SCADA from LFC. |  |

| Requirement ID | SCD-FR9 |
| --- | --- |
| Requirement Name | Sending LMPs to QSEs |
| Protocol Reference | Section(s) 6.5.9.2 (2) and 6.5.9.4.2 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P07.I-5 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall send all resource node LMPs to all QSEs after they are received from LFC. |  |

| Requirement ID | SCD-FR6 |
| --- | --- |
| Requirement Name | Reg and RRS Outputs to QSEs |
| Protocol Reference | Section(s) 6.5.7.6.1 (4); 6.5.7.6.2.2 (11), 6.5.7.6.2.1 (8) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-5 |
| Sub-Process Element Coverage | Partial |
| Description: Regulation and Responsive Reserve control signals shall be sent by SCADA to the QSE Those Dispatch Instructions shall contain the MWs output requested. The Dispatch Instructions shall contain the change in MW output requested of the QSE assuming all Resources are at their last Base Point issued by SCED. |  |

3.3 Other Functionality

| Requirement ID | SCD-FR25 |
| --- | --- |
| Requirement Name | Data Availability Statistics |
| Protocol Reference | Sections 3.10.7.4, 8.1 (3) and 8.3 (1) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1, I-2, and P-1 |
| Sub-Process Element Coverage | Partial |
| Description SCADA shall provide availability statistics on a point by point basis and on an aggregated basis. EMS displays shall be provided to show hourly, daily, monthly, and quarterly availability statistics on a point by point basis and on an aggregated basis. Each of these displays shall have sorting and filtering tabs Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR24 |
| --- | --- |
| Requirement Name | Summary Displays and Tables |
| Protocol Reference | Section 3.10.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide a summary display for each of the following: - suspect status points - suspect analog points - stale points - disabled points - Manual override points Each of these displays shall have sorting and filtering tabs. All summary tables shall be archived. |  |

| Requirement ID | SCD-FR23 |
| --- | --- |
| Requirement Name | ICCP Link Availability Statistics |
| Protocol Reference | Section(s) 3.10.7.4, 8.1 (3) and 8.3 (4) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1 and P-1 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide ICCP link availability statistics. EMS displays shall be provided to show hourly, daily, and monthly availability statistics for each ICCP link. Availability statistics shall exclude planned outages. Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR22 |
| --- | --- |
| Requirement Name | Critical Data Availability Statistics |
| Protocol Reference | Sections 3.10.7.4, 8.1 (3) and 8.3 (1) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1, I-2, and P-1 |
| Sub-Process Element Coverage | Partial |
| Description SCADA shall uniquely identify critical data points and provide separate availability statistics on a point by point basis. EMS displays shall be provided to show hourly, daily, monthly, and quarterly availability statistics on a point by point basis and on an aggregated basis. Each of these displays shall have sorting and filtering tabs. Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR21 |
| --- | --- |
| Requirement Name | NERC Monitoring Requirements |
| Protocol Reference | Sections 6.5.2, 6.5.1.1, 6.5.1.2 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-3 and I-6 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall include necessary displays and alarming capability to support monitoring needs to meet NERC Reliability Standards. |  |

| Requirement ID | SCD-FR20 |
| --- | --- |
| Requirement Name | Interface to ERCOT Custom Applications |
| Protocol Reference | Section 3.1.2 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall interface to existing ERCOT custom applications (such as RTMONI) in the new system. Please note that our current load forecast is dependent upon RTMONI calculations to support the weather zone calculations. |  |

| Requirement ID | SCD-FR13 |
| --- | --- |
| Requirement Name | Standard SCADA functionality |
| Protocol Reference | Section 3.10.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.I-1 to I-6, and P-1 to P-3 |
| Sub-Process Element Coverage | Partial |
| Description: EMS Vendor shall assure all the standard SCADA functionality exising in their current EMP2.2 platform shall be included in the new system. |  |

| Requirement ID | SCD-FR18 |
| --- | --- |
| Requirement Name | Temporary Override Flag |
| Protocol Reference | Section 3.10.7.4.1 (4) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: For each SCADA status point that has a tag, an operator enterable flag shall be available, that when set shall automatically remove a manual override if the associated data quality flag returns to a valid condition code. Once the telemetry returns to valid, the tag shall be removed and the operator enterable flag shall be reset. |  |

| Requirement ID | SCD-FR10 |
| --- | --- |
| Requirement Name | Stale Data Processing |
| Protocol Reference | Section(s): 6.5.7.1.13(a) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | COPS.P02.P-1 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall indicate that real-Time input data is stale if that data value has not been updated for more than 20 seconds. Note: ERCOT intends that the vendor assess the impact of this requirement on the processing requirements including any conflicts with reporting by exception. |  |

| Requirement ID | SCD-FR2 |
| --- | --- |
| Requirement Name | Manual Override |
| Protocol Reference | Section(s) 6.5.7.1.5 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: There shall be the capability for the ERCOT operators to override SCADA telemetry from one-line diagrams and station tabular displays to correct erroneous breaker and switch status before that information is processed by the Network Security Analysis for the next SCED interval. |  |

| Requirement ID | SCD-FR11 |
| --- | --- |
| Requirement Name | Automatic tagging of Override Points |
| Protocol Reference | Section 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: When an operator overrides a telemetered SCADA point, a tag shall be automatically created if no tag exists for that telemetered point. Provision shall be made to require the operator to enter the reason for the change and the operator name. The system shall automatically enter the console name on the tag. The system shall create an entry in the tag summary upon completion of a tag entry. All tags shall be archived. |  |

| Requirement ID | SCD-FR14 |
| --- | --- |
| Requirement Name | ICCP Quality code processing |
| Protocol Reference | Section(s): 3.10.7.4 (3); 3.10.7.4 (1) & (3) and TAC Approved Telemetry Standards Document |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-1 |
| Sub-Process Element Coverage | Partial |
| Description: Per the TAC approved Telemetry Standards Document, SCADA shall process the following quality codes associated with ICCP status and analog data: - Valid – represents analog or status the market participant considers valid - Manual – represents a analog or status entered manually at the market participant (not received from the field electronically) - Suspect - Represents a analog or status in which the market participant is unsure of the validity - Invalid – Represents an analog or status, which the market participant has identified as out of reasonability limits. - Communication failure – informs ERCOT that due to communications failure, the analog or status provided ERCOT is not current SCADA shall produce an alarm when a point goes from a valid to an invalid state. SCADA shall produce an alarm when a point goes from an invalid to a valid state. SCADA shall convert data condition codes from each TDSP and QSE in a consistent manner for all applicable ERCOT applications. |  |

| Requirement ID | SCD-FR15 |
| --- | --- |
| Requirement Name | Database structure modification |
| Protocol Reference | Section(s): 3.10.7.4 (1) and TAC Approved Telemetry Standards Document |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: The SCADA function shall provide on-line editing tools and screens to allow an EMS Analysts to add, remove, and edit data points telemetered from QSEs and TDSPs. |  |

| Requirement ID | SCD-FR16 |
| --- | --- |
| Requirement Name | SCADA ICCP scan rate |
| Protocol Reference | Section(s): 3.10.8.1 (1) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | COPS.P02.I-1 and I-2 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive the following TSP dynamic ratings data via ICCP every 10 seconds: - Normal - Emergency - 15-Minute SCADA shall receive all status and analog inputs from QSEs every 2 seconds SCADA shall receive all status and remaining analog inputs from TSPs every 10 seconds SCADA shall send all outputs to QSEs every 4 seconds. |  |

| Requirement ID | SCD-FR19 |
| --- | --- |
| Requirement Name | Data for study State Estimator |
| Protocol Reference | Section(s): 3.10.4 (3) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P02.P-2 |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall make available all Real-Time ICCP and SCADA data to the production study State Estimator function. |  |

# Supplementary Requirements

| Requirement ID | SCD-SR1 |
| --- | --- |
| Requirement Name | SCADA Processing |
| Requirement Type | Performance |
| Description: SCADA shall perform all data processing within 1 second. Processing shall include the time from a limit change to the time the limit processing is completed and if a violation occurs, the violation is posted to the alarm/event system. |  |

| Requirement ID | SCD-SR2 |
| --- | --- |
| Requirement Name | Data Availability |
| Requirement Type | System and Communication |
| Description: SCADA shall monitor the availability of ICCP links. The cumulative availability in percentage shall be calculated for each hour, day and month. SCADA shall alarm if the availability falls below the pre-set monthly threshold. Availability thresholds shall be configurable by ERCOT Analysts. Initially these thresholds shall be configured as follows: - TDSP ICCP links shall achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages. - QSE ICCP links shall achieve a monthly availability of ninety-nine point ninety-nine (99.99%) percent, excluding approved planned outages. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data. A link will be considered as available when at least the predefined percent (configurable by an ERCOT Analyst and initially set to eighty-five (85%)) of the data defined on that link is successfully transferred to ERCOT with a valid or manual quality code. The current and previous month’s availability data shall be stored in EMS database and shall be viewable through EMS user interface. |  |

| Requirement ID | SCD-SR3 |
| --- | --- |
| Requirement Name | Process Redundant Links |
| Protocol Reference | System and Communication |
| Description: SCADA shall process fully redundant data communication links (ICCP or RTU) between the EMS and TSPs and QSEs. |  |

| Requirement ID | SCD-SR4 |
| --- | --- |
| Requirement Name | No degradation in performance |
| Requirement Type | Performance |
| Description: There shall be no degradation in the performance of ERCOT systems as a result of the SCADA functions execution under full volume processing. |  |

| Requirement ID | SCD-SR6 |
| --- | --- |
| Requirement Name | Online User Documentation and Help System Requirements |
| Requirement Type | Training and Documentation |
| Description: The delivered software shall support exception handling, error detection and diagnostic tools sufficient to support the functional requirements of this document to ERCOT’s satisfaction. User and operator software messages shall be formatted in plain English and generated at the application level (for each and every application) and not at the OEM software level (ORACLE, UNIX, etc.) |  |

| Requirement ID | SCD-SR7 |
| --- | --- |
| Requirement Name | Software User guides |
| Requirement Type | Training and Documentation |
| Description: The SCADA supplier shall provide Software Reference Design Guides documents including the following information: - In-code documentation and annotations: - ERCOT will identify all the customs implemented internally as ERCOT_XXXXXX. There will be a comment in the comments section of each subroutine that is changed for this purpose. - Everywhere code is modified changes are identified with ERCOT_XXXXXX (begin) / ERCOT_XXXXXX (end). - Single line changes will have inline comments noted as with ERCOT_XXXXXX ERCOT requires that SUPPLIER follows the same standard and use the note SUPPLIER_XXXXX instead of ERCOT_XXXXX. - Custom code description documents: - ERCOT requires an additional document that describes each of the customs done by SUPPLIER that includes the following information: - Custom Name / Developer's name /Date Implemented - Brief design description or definition of the custom - List of files affected by this custom (code set name and file name) - List of displays affected by this custom (DDL name and picture name) - List of database fields added (Table name and field name) There will be one document for each EMS subsystem (SCADA, RTCA etc.). These documents shall be provided in addition to supplier standard documentation. |  |

| Requirement ID | SCD-SR9 |
| --- | --- |
| Requirement Name | Provision for maintenance |
| Requirement Type | Maintenance |
| Description: Provision for maintenance, tagging, information display, communication management, logging, and calibration to ERCOT’s satisfaction shall be required. |  |

| Requirement ID | SCD-SR10 |
| --- | --- |
| Requirement Name | Database Sizing |
| Requirement Type | System and Communication |
| Description: The SCADA application shall be sized to process 60,000 status points and 35000 analog points per second”. |  |

| Requirement ID | SCD-SR11 |
| --- | --- |
| Requirement Name | Performance |
| Requirement Type | System and Communication |
| Description: SCADA failover time shall not exceed five minutes. |  |

# Protocol Coverage

| Protocol Sub-Section # (To the lowest level of granularity as possible) | Section title | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| 3.10.4 (3) | ERCOT Responsibilities | Partial |
| 3.10.7.4 (1) | Telemetry Criteria | Partial |
| 3.10.8 (2) | Dynamic Ratings | Partial |
| 3.10.8.1 (1) | Dynamic Ratings Delivered via ICCP | Full |
| 3.10.8.1 (2) | Dynamic Ratings Delivered via ICCP | Partial |
| 3.13 (1) | Renewable Production Potential Forecasts | Partial |
| 4.2.2 (3) | Wind-Powered Generation Resource Production Potential | Partial |
| 6.3.2 (2) | QSE Output | Partial |
| 6.5.5.2 | Operational Data Requirements | Partial |
| 6.5.5.2 (2) | QSE Inputs | Partial |
| 6.5.7.1.1 | Telemetry | Partial |
| 6.5.7.1.13(a) | Stale Data | Full |
| 6.5.7.1.5 | Override | Partial |
| 6.5.7.2 (1) | Operational Data Requirements | Partial |
| 6.5.7.3 (1) | Security Constrained Economic Dispatch | Partial |
| 6.5.7.4 (1) | QSE Output | Partial |
| 6.5.7.6.1 (3) | LFC Output | Partial |
| 6.5.7.6.1 (4) | Reg and RRS | Partial |
| 6.5.7.6.2.1 (8) | Regulation | Partial |
| 6.5.7.6.2.2 (11) | RRS Deployment | Partial |
| 6.5.9.5 (i) | BLT Inputs | Full |

# Sub-Process Coverage

| Sub-Process ID | Sub-Process Name | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| I-1 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |
| I-2 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |
| I-3 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |
| I-4 | COPS.P02ProcessMonitorTelemetry_V1 |  |
| I-5 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |
| I-6 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |
| P-1 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |
| P-2 | COPS.P02ProcessMonitorTelemetry_V1 |  |
| P-3 | COPS.P02ProcessMonitorTelemetry_V1 | Partial |