DWG Report to ROS, October 2006

- The last DWG meeting was October 3-4, 2006.

- DWG asks ROS approval of DWG Procedural Manual, Rev 4.  A clean and redline version of the manual will be forwarded to the ROS.  Changes include:

  - Rearranging sections of the manual so that compliance sections of the manual are separated from the ‘how to’ sections of the manual and clearly identifying the ‘how-to’ sections as guidelines not requirements.

  - Added a section specifically listing Wind Modeling Requirements as was presented to and approved by the ROS at the August meeting.  Some changes were made to the draft section that was sent to ROS in August.

  - Made additions or edits to the manual to address ERCOT compliance with NERC Standards (MOD-013-0, PRC-020-0, and PRC-021-0) as requested by ERCOT Compliance and the ROS.

- Earlier this year, the ROS assigned the DWG to review the four newly published NERC Field Test Standards.  I have forwarded the files “PRC-019_Draft 3 DWG Evaluation.doc” and “PRC-024_Draft 3 DWG Evaluation.doc”.  These documents summarize the DWG evaluation of the NERC Field Test requirements and whether the ERCOT Protocols and Operating Guides already address these.

The four standards are:

PRC-019: Coordination of Generator Voltage Regulator Controls with Unit Capabilities and Protection.  The DWG was asked to address only R1, the requirement to establish and maintain criteria for exemptions.  A 10 MW exemption already exists in the Operating Guides.

PRC-024: Generator Performance During Frequency and Voltage Excursions.  The DWG concluded that the majority of the requirements already exist in the Operating Guides.  It appeared to us that requirement R2 is already met by the Operating Guides; however, requirement R2.2 should be addressed more thoroughly by the SPWG.  For requirement R3, no exemption criteria is specifically stated in Op Guide 2.9.2, but one assumes the same 10 MW limit as in Section 3.1.4.  For requirement R4, the requirement calls for a procedure to handle variances from the requirements in R1 and R2.  Our thoughts are contained in the word document, but we generally thought that the Operating Guide Revision Request procedure would be the avenue a generator would take to request a variance from any of these requirements.  R6 requires ERCOT to review and update, if necessary, these requirements every five years.  Operating Guide revisions occur on an ongoing basis, so this seems to naturally be met; however, there did not appear to be any statement in the Operating Guides addressing this.

MOD-026: Verification of Models and Data for Generator Excitation System Functions.  The DWG concluded that the requirements in MOD-026 are not currently addressed in the ERCOT Protocols or Operating Guides.  Op Guide 2.2.4 discusses testing AVR’s and PSS’s every 5 years and gives a limited list of data to report.  The information determined in this test is not sufficient to verify the dynamic models of the excitation system.

MOD-027: Verification of Generator Unit Frequency Response.  The DWG concluded that the requirements in MOD-027 are not currently addressed in the ERCOT Protocols and Operating Guides.  Op Guide 2.2. states that generator governor performance tests must be conducted every two years.  Example test reports for “Turbine Governor Speed Regulation Tests” are located in Op Guide 6.2.1.  The information determined in this test is not sufficient to verify dynamic models of the governor.

- The next DWG meeting is currently planned for the week of November 27-December 1, 2006.

DWG Tasks, 2006

| Task | Status |
| --- | --- |
| Flat start 2006 case | Complete |
| Flat start 2008 case | Complete |
| Incorporate load as responsive reserve models into dynamics database. | Complete |
| Flat start 2006 case with wind models. | Complete |
| Publish flat start book. | Fall Activity |
| Make annual determination of the number and location of dynamic monitoring devices. | Complete |
| Assist Black Start Task Force in evaluating ERCOT-wide black start plan | Working |
| Dynamic Voltage Recovery criteria | Working |
| Review recently approved NERC Standards with respect to ERCOT Op Guides and Protocols | Working |
| Review current ERCOT criteria for proposed NERC Standards (PRC-019,PRC-024,MOD-026-1,MOD-027-1) | Complete |
| Participate in ROS Ad Hoc Task Force regarding Power System Stabilizers | Working |
| Annual Procedural Manual review/update. | Complete |
| Begin 2007 flat start activities. | Fall Activity |