ERCOT Nodal Operating Guides

Section 2: System Operations

DRAFT – [Month, Day, Year]

(Effective Upon Texas Nodal Market Implementation)

2.	System Operations	3

2.1	Operational Duties	3

2.2	System Monitoring and Control	5

2.2.1	Overview	5

2.2.2	Security Criteria	7

2.2.3	Automatic Generation Control Systems	7

2.2.4	Automatic Voltage Regulators And Power System Stabilizers	Error! Bookmark not defined.

2.2.5	Turbine Speed Governors	9

2.2.6	Performance/Disturbance/Compliance Analysis	9

2.2.7	Time Error And Time Synchronization	9

2.3	Dispatch Duties	Error! Bookmark not defined.

2.3.1	Control Area Operator Authority	Error! Bookmark not defined.

2.3.2	Dispatch Instruction Procedures	Error! Bookmark not defined.

2.4	Scheduling	Error! Bookmark not defined.

2.4.1	Day Ahead Scheduling	Error! Bookmark not defined.

2.4.2	Adjustment Period Scheduling Process	Error! Bookmark not defined.

2.4.3	Direct Current Tie Interconnection Day Ahead Scheduling Process	Error! Bookmark not defined.

2.4.4	Temporary Deviations from Scheduling Procedures	Error! Bookmark not defined.

2.4.5	Real-Time Schedules	Error! Bookmark not defined.

2.5	Ancillary Services	11

2.5.1	ERCOT Responsibilities	Error! Bookmark not defined.

2.5.2	Responsive Reserve	12

2.5.3	Non-Spinning Reserve Service (NSRS)	15

2.5.4	Replacement Reserve Service (RPRS)	Error! Bookmark not defined.

2.5.5	Balancing Energy Service	Error! Bookmark not defined.

2.6	Changes in System Status	Error! Bookmark not defined.

2.6.1	Changes in Resource Status	Error! Bookmark not defined.

2.6.2	Changes in Transmission Facility Status	Error! Bookmark not defined.

2.7	Outage Coordination	17

2.7.1	ERCOT Control Area Authority Responsibilities	17

2.7.2	Forced Outages	17

2.7.3	Scheduled Outages	18

2.8	Congestion Management	19

2.8.1	Overview of ERCOT Coordinated Congestion Management	20

2.9	Requirements for Under-Frequency Relaying	21

2.9.1	Automatic Firm Load Shedding	21

2.9.2	Generators	22

2.10	System Voltage Profile	23

2.10.1	Introduction	23

2.10.2	Maintaining Voltage Profile	23

2.10.3	Special Consideration for Nuclear Power Plants	24

2.10.4	Reactive Considerations for Gas and Steam Turbine Power Plants	25

2.11	External Control Area Inter-Ties	28

2.11.1	Control Area Operations	28

2.11.2	Operation of DC Ties	28

2.12	Document Control	Error! Bookmark not defined.

# 2	System Operations

2.1	Operational Duties

The duties of ERCOT are described in relevant sections of the Protocols and NERC Standards.  These Operating Guides assume that all actions taken will be on components of, or related to, the ERCOT Bulk Electric System unless otherwise specified.  The primary operational duties of ERCOT are to ensure the reliability of the Bulk Electric System.  In doing this ERCOT shall:

(1)	Perform Operational Planning:

(a)	Commit additional resources as needed to maintain reliability;

(b)	Perform operational transmission grid reliability studies, including those related to generation and load interconnection responsibilities;

(c)	Review outages of generating units and major transmission lines or components to identify constraints that may affect transfers;

(d)	Perform load flows and security analyses of Outages submitted by Qualified Scheduling Entities (QSEs) or Transmission Service Providers (TSPs) as a basis for approval or rejection;

(e)	Withdraw approval of a scheduled Outage if unable to meet the applicable reliability standards after all other reasonable options are exercised;

(f)	Serve as the point of contact for initiation of generation interconnection to the transmission grid;

(g)	Coordinate all Planned and Maintenance Outages of generation and transmission system facilities;

(h)	Forecast load and resources for the next seven days for reliability planning; and

(i)	Ensure that sufficient resources and required Ancillary Services have been committed for all expected load and power flow transactions within the Region on a Day-Ahead and Real-Time basis.

(2)	Operate energy and Ancillary Service markets:

(a)	Administer a Congestion Revenue Rights (CRR) financial market ;

(b)	Administer a Day-Ahead Market (DAM) and Ancillary Service market ;

(c)	Administer a Supplemental Ancillary Service Market (SASM); and

(d)	Administer a Real-Time energy market using Security-Constrained Economic Dispatch (SCED)

(3)	Supervise Grid Operations:

(a)	Evaluate transmission grid conditions on a continuous basis;

(b)	Oversee operation of the transmission grid and act as the ERCOT Reliability Coordinator;

(c)	Dispatch generation to control frequency and congestion;

(d)	Provide access to the transmission grid on a nondiscriminatory basis;

(e)	Approve schedules of interchange transactions across the DC Ties;

(f)	Adjust resources as needed to maintain safety and reliability within the Bulk Electric System, meet NERC frequency control performance requirements; and

(g)	Operate within rules established by governing agencies, Protocols, and these Guides.

(4)	Collect and Disseminate Information:

(a)	Provide appropriate operational information to individual QSEs and Transmission Operators (TOs);

(b)	Provide relevant operational information to Market Participants (MPs) over the Market Information System (MIS);

(c)	Collect and maintain operational data required by the PUCT, NERC or Protocols;

(d)	Receive reports from TOs and QSEs and forward them to the Department of Energy (DOE) and/or NERC as required;

(e)	Submit reports to DOE and/or NERC as required; and

(f)	Record and report accumulated time error.

2.2	System Monitoring and Control

2.2.1	Overview

(1)	ERCOT will maintain continuous surveillance of the status of operating conditions within the Region and act as a central information collection and dissemination point for Market Participants.

(2)	ERCOT is designated to receive information required to continually monitor the operating conditions of the Bulk Electric System and to order individual QSEs and/or TOs make changes to assure ongoing security and reliability of the Region.

(3)	ERCOT shall maintain, monitor and/or direct the following consistent with the Protocols:

(a)	Generation

(i)	Monitor unit status and capability;

(ii)	Monitor Automatic Voltage Regulator (AVR) status;

(iii)	Monitor unit commitment;

(iv)	Balance system generation and loads;

(v)	Monitor operating reserves;

(vi)	Monitor Forced Outages and capability limitations;

(vii)	Maintain net capability test results;

(viii)	Maintain Load Resource test results;

(ix)	Compile Ancillary Services Plans;

(x)	Perform Ancillary Services deployment;

(xi)	Collect data for Ancillary Services accounting;

(xii)	Monitor maintenance schedules;

(xiii)	Monitor Power System Stabilizer (PSS) status; and

(xiv)	Commit capacity as needed to maintain reliable operations.

(b)	Bulk-Electric System

(i)	Monitor line loading and power transfers;

(ii)	Coordinate Planned Outages;

(iii)	Monitor and detect Forced Outages;

(iv)	Perform contingency analyses and direct redispatch to maintain reliable operations;

(v)	Maintain maintenance and construction schedules;

(vi)	Monitor and control voltage levels; and

(vii)	Monitor Reactive Power flows.

(d)		System Operation

(i)	Monitor power transfers and interchange;

(ii)	Maintain and monitor Ancillary Services plans and delivery;

(iii)	Maintain and document compliance with transmission security criteria;

(iv)	Monitor performance of providers of Ancillary Services;

(v)	Manage inadvertent energy account balances;

(vi)	Direct time error correction;

(vii)	Issue and direct Operating Condition Notices, Advisories, Alerts and Emergency Notices;

(viii)	Direct short supply operations;

(ix)	Direct implementation of the Emergency Electric Curtailment Plan (EECP); and

(x)	Direct coordination of the black start plan.

(e)	Information Management

(i)	Monitor and coordinate information for daily planning, hourly reporting and minute-by-minute operation;

(ii)	Verify the accuracy of the Real-Time data;

(iii)	Operate a MIS, an  Energy Management System (EMS) and a Market Management System (MMS) to disseminate real-time, hourly accounting, and operations plan data between ERCOT and each QSE and TO; and

(iv)	Establish the requirements for each TO and QSE to report relevant Bulk System information to ERCOT.

2.2.2	Security Criteria

(1)	Technical limits established for the operation of transmission equipment shall be applied consistently in (Total Transfer Capability (TTC) calculations, engineering studies, real-time security analyses, and operator actions.

(2)	Unless an Emergency Condition has been declared by ERCOT, the ERCOT System shall be operated in such a manner that the occurrence of a creditable single contingency will not cause any of the following conditions:

(a)	Uncontrolled breakup of the transmission system;

(b)	Loading of Transmission Facilities above defined emergency ratings that can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures;

(c)	Transmission voltage levels outside system design limits that can not be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs; or

(d)	Customer outages, except for high set interruptible and radially served loads.

2.2.3	Response to Transient Voltage Disturbance

[To be inserted later.]

2.2.4	Load  Frequency Control

(1)	ERCOT shall operate the load frequency control system to maintain the scheduled frequency at 60 Hz (correcting periodically for time error) and to minimize the use of energy from Resources providing Regulation Service.

(2)	The ERCOT load frequency control system shall deploy Regulation and Responsive Reserve energy as necessary in accordance with Protocol Section 6.5.7.6, Load Frequency Control, to meet NERC Standards. ERCOT shall purchase sufficient Regulation resources to provide satisfactory frequency control performance for the Region.  ERCOT shall determine the satisfactory amount of Regulation Service, required by statistical analysis of possible unit outages and load forecast error, to expect operation of 95% of hours without deploying Responsive Reserve Service.

(3)	QSEs shall use Automatic Generation Control (AGC) to direct the output of generation facilities within the response times described in Operating Guides Section 8, Telemetry and Communication, and the Protocols.

2.2.4.1	Maintenance and Verification

Each provider of Regulation and/or Responsive Reserve Services will properly maintain Automatic Generation Control equipment.  ERCOT will initiate a regulation survey to evaluate the performance of all Automatic Generation Control equipment in the Region.

2.2.4.2	Regulation Provider Loss of AGC (Generator Loses Pulse Signal)

If a QSE providing Regulation Services or Responsive Reserve Services loses its Automatic Generation Control for any reason, it will notify ERCOT as soon as practicable of the reason for and estimated duration of the loss.  ERCOT will assess whether additional action should be taken to maintain system frequency.  Possible ERCOT actions include:

(1)	Placing a QSE on constant frequency control; and/or

(2)	Opening a Supplemental Ancillary Service Market (SASM) per Protocol Section 6.4.8.2, Supplemental Ancillary Service Market, for the period of anticipated loss.

2.2.4.3	Loss of Automatic Control

ERCOT is obligated to have back-up facilities in place for loss of control systems.  In the event that these backup facilities also fail to perform, ERCOT shall direct a QSE providing frequency control to implement Constant Frequency Control (CFC) for the duration of the control loss and will define ERCOT’s bias.  If a QSE on CFC develops a problem with regulating room, ERCOT will order additional regulation energy from another QSE to create regulation room.

2.2.4.4	Changes in Control Mode

All QSEs shall demonstrate to ERCOT that they have the ability to switch control modes as necessary in accordance with paragraph (2) of Protocol Section 8.1.2.2.2, Regulation Service.  A QSE shall notify ERCOT (via telephone) and obtain approval from ERCOT prior to changing control modes.  Valid QSE control modes are Normal (Ancillary Services control), Constant Frequency and Off.

2.2.5	Automatic Voltage Regulators and Power System Stabilizers

(1)	Generator Automatic Voltage Regulators (AVR) and Power System Stabilizers (PSS) will be kept in service whenever possible.  Generation Entities shall notify their QSEs, who in turn will promptly notify ERCOT by telephone of the circumstances, when a voltage regulator or stabilizer is unavailable due to maintenance or failure and when it is returned to normal operation.  ERCOT is responsible for notifying the appropriate TO of such AVR and PSS status changes.  QSEs shall supply AVR and PSS status logs to ERCOT upon request as per Protocol Section 6.5.5.1, Changes in Resource Status.

(2)	Performance tests shall be conducted on AVRs every five years per Protocol Section 8.1.2.2.5(5) or if equipment characteristics are knowingly modified.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

(3)	Excitation systems, including power system stabilizers, shall also be tested every five years.

(4)	Unit AVR and PSS modeling information required in the ERCOT Planning Criteria shall be determined from actual unit testing described in the Operating Guides.  Within 30 days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the TSP.

2.2.6	Turbine Speed Governors

(1)	All governors must be placed in-service for all generation resources (except nuclear and wind) as soon as power is above the minimum operating limit, as per Protocol Section 8.5.1.1, Governor in Service.

(2)	Governor performance tests shall be conducted at least every two years unless a written exception is obtained from ERCOT.   A sample of such tests may be found in Operating Guides Section 6.2.1.2, Example of a Turbine Governor Speed Regulation Test for Mechanical Hydraulic Governor.  Maintenance and tests on governors shall demonstrate calibration for operation with a five percent (5%) droop characteristic and dead band no greater than +/- 0.0.36 Hz.

(3)	There are other elements that can contribute to poor governor response.  These include:

(a)	Governor dead band greater than the maximum intentional dead band is +/- 0.036 Hz.);

(b)	Valve position limits;

(c)	Blocked governor operation;

(d)	Control mode;

(e)	Adjustable rates or limits;

(f)	Boiler/turbine coordinated control or set point control action; and

(g)	Automated “reset” or similar control action of the turbine’s MW set point.

(4)	Every attempt should be made to minimize the effects of these elements on the governor operation for the duration of all frequency deviations.  Each QSE should monitor its units to verify that these elements do not contribute to a governor droop characteristic greater than five percent (5%).

2.2.7	Performance/Disturbance/Compliance Analysis

(1)	Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance to published control criteria of ERCOT {{the Region??}}.  Control performance of a resource providing Responsive Reserve Service (RRS) can be found in Protocol Section 8.1.2.4.2, Responsive Reserve Service Energy Deployment Criteria.

(2)	ERCOT shall make a regular report on selected system disturbances, documenting the response of individual QSEs, together with a summary.  In addition, PGCs, QSEs, and individual members of the ERCOT Performance Disturbance Compliance Working Group (PDCWG) are encouraged to work within their respective companies to enhance the performance of individual generating resources control systems through application of the results of the PDCWG studies.

(3)	ERCOT Compliance shall communicate with the Market Participants having less than the current specified performancev to ensure compliance and improve performance.

(4)	As necessary, a Contingency Reserve Adjustment (CRA) as defined by NERC Standards, will be calculated by the PDCWG and submitted to the Reliability and Operations Subcommittee (ROS) for review and approval.  ERCOT will include the CRA in the daily Ancillary Service plan.

2.2.8	Time Error and Time Synchronization

2.2.8.1	Time Error

Sustained frequency deviations from scheduled frequency result in time error.  Time error will be monitored and controlled in ERCOT as follows:

(1)	Time Error Monitoring - ERCOT will monitor accumulated time error and initiate time corrections.  The instantaneous time error is available to all ERCOT QSEs on the ERCOT website.  When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction.  The correction may end when the error is less than ±0.5 seconds, or when system events mandate termination.  The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction; however, at no time should the accumulated time error be allowed to exceed five seconds.

(2)	Time Error Correction - When a time correction is necessary, ERCOT will adjust scheduled frequency by arranging for more or less resources by implementing a frequency offset. Information will be communicated via hotline call to all QSEs, which will include the frequency offset (-.02 Hz for fast and +.02 Hz for slow) and the start time. A time correction may be terminated after five hours, or after any hour without a 0.5 second error reduction.  ERCOT will provide adequate notice of the ending of a time correction to all QSEs in the Region.

2.2.8.2	Time Synchronization

To promote accurate data reporting during EECP and other system events, and to ensure transaction schedules are simultaneous, all QSEs and TOs, and ERCOT will maintain their control system time within +/-3 seconds of the National Bureau of Standards (NBS) time signal.  The NBS time signal shall set the time standard for ERCOT.  ERCOT, QSEs and TOs are required to employ clocks, voice and data recording systems that synchronize automatically with the NBS on at least a weekly basis.

2.3	Ancillary Services

The types of Ancillary Services required by ERCOT are described below:

| ANCILLARY SERVICE TYPE | DEFINITION | ERCOT CONTROL AREA AUTHORITY ACTION |
| --- | --- | --- |
| Regulation Down Service (Reg-Down) and Regulation Up Service (Reg-Up) Reference: Protocol Section 3.17.1, Regulation Service | Generation Resource capacity provided by a QSE to control frequency within the system which is controlled minute by minute (normally by an AGC System). | - Reg-Down power is deployed in response to a change in system frequency above the target system frequency. - Reg-Up power is deployed in response to a change in system frequency below the target system frequency. |
| Responsive Reserve Service Reference: Protocol Section 3.17.2, Responsive Reserve Service | Operating reserves maintained by ERCOT to restore the frequency of the system within the first few minutes of an event that causes a significant deviation from the standard frequency. Responsive Reserve can also be used as a backup regulation service and energy during an EECP event. | Normally None – Responsive Reserve deploys automatically through governor action. or Deployed for the under-frequency events on the ERCOT System. |
| Non-Spinning Reserve Service Reference: Protocol Section 3.17.3, Non-Spinning Reserve Service | - Off-line Generation Resource capacity, or reserved capacity from On-line Generation Resources, capable of being ramped to a specified output level within 30 minutes, and running at a specified output for at least one hour - Load Resource that are capable of being interrupted within 30 minutes and remaining interrupted for at least one hour. | Deployed in response to loss-of-Resource contingencies, load forecasting error, or other contingency events on the system. |
|  |  | . |
| Voltage Support Reference: Protocol Section 3.15, Voltage Support | Reactive capability of a Generation Resource that is required to maintain transmission and distribution voltages on the ERCOT Transmission Grid within acceptable limits All Generation Resources with a gross generating unit rating greater than 20 MVA shall provide Voltage Support Service. | Direct the scheduling of Voltage Support Service by providing Voltage Profiles at the high voltage side of generator busses. The Generation Resource is obligated to maintain the published voltage profile. |
| Black Start Service Reference: Protocol Section 3.14.2, Black Start | The provision of Generation Resources under a Black Start Agreement, which are capable of self-starting without support from within ERCOT in the event of a blackout. | Provide emergency Dispatch Instructions to begin restoration to a secure operating state after a total or partial blackout. |
| Reliability Must-Run Service Reference: Protocol Section 3.14.1, Reliability Must Run | The provision of Generation Resource capacity and/or energy Resources under a Reliability Must-Run (RMR) Agreement. | Enter into contractual agreements to retain units required for reliable operations. Direct the operation of those units that otherwise would not operate and that are necessary to provide reliable operations. |

ERCOT shall procure and deploy Ancillary Services on behalf of QSEs.

2.3.1	Supplemental Ancillary Services Market

If ERCOT determines in the Adjustment Period that more Ancillary Services are needed for one or more Operating Hours than were provided in the Day Ahead Ancillary Services Plan; ERCOT may procure more Ancillary Services through a SASM, as per Protocol Section 6.4.8.2, Supplemental Ancillary Service Market.

2.3.2	Responsive Reserve

2.3.2.1	Obligation

ERCOT operating reserve requirements are more restrictive than NERC Standards.  The ERCOT Responsive Reserve Obligation is 2300 MW.

2.3.2.2	Allocation of Obligation

The daily Responsive Reserve Obligations will be available on the ERCOT MIS. The allocation of the Responsive Reserve Obligation (RRO) between Load Entities will be based on Protocol Section 4.2.1.2, Ancillary Service Obligation Assignment and Notice.

2.3.2.3	Types of Responsive Reserve

(1)	Responsive Reserve (RRS) service may be provided per Protocol Section 8.1.2.2.3, Responsive Reserve Service, by:

(a)	Unloaded Generation Resources that are On-line,

(b)	Load Resources controlled by high-set under-frequency relays,

(c)	Hydro Responsive Reserves,

(d)	DC Tie response that stops frequency decay,

(e)	Load Resources capable of controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action).

(2)	ERCOT shall specify the minimum amount of RRS provided by Generation Resources.   QSE’s Generation Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.

(3)	Responsive reserves provided by a QSE shall meet the following requirements as defined in paragraph (5) of Protocol Section 3.18, Resource Limits in Providing Ancillary Service:

(a)	In no case shall more than 20% of the net dependable capability for any non-combined cycle thermal unit be used as Responsive Reserve.

(b)	In no case shall more than 20% of the combined net dependable capability for any combined cycle block with one or more CTs or GTs coupled to a steam turbine, with their net maximum capability aggregated together, be used as Responsive Reserve.

(c)	In no case shall more than 20% of the net dependable capability for any hydro unit with a 5% droop setting operating as a generator be used as Responsive Reserve.

(d)	In no case shall capacity from any wind unit be used as Responsive Reserve.

(4)	Telemetered Interruptible Load controlled by under-frequency relays for automatic interruption may be eligible to participate as a responsive reserve Resource as specified in Protocol Section 8.1.2.2.3, Responsive Reserve Service.  To become a provider of RRS, the Interruptible Load shall complete the following requirements:

(a)	Register as a Resource with ERCOT;

(b)	Complete asset registration of LaaR;

(c)	Provide ERCOT the appropriate under-frequency relay Load affidavit;

(d)	Provide ERCOT with a simplified one-line diagram between relay and operating device;

(e)	Provide ERCOT with under-frequency relays set point calibration documentation including: the relay used to shed Load at low frequency, the relay set point, the relay operating time, and the typical loads to be shed;

(f)	Test to verify appropriate voice communications are in place for Verbal Dispatch Instructions by ERCOT;

(g)	Be capable of interruption by automatic operation of the under-frequency relay(s) set to initiate the interruption whenever system frequency reaches a specific value.  The initiation setting of the relay shall not be any lower than 59.7 Hz.;

(h)	Have frequency measuring relays with a time delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles).  Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times.

(i)	Be capable of interruption within ten minutes of receipt of a Verbal Dispatch Instruction (VDI) from ERCOT;

(j)	Be telemetered through the QSE to ERCOT with a real-time signal of total interruptible Load on high-set under-frequency relays, breaker status, the status of the high set under-frequency relay, and signals representing the Load Resource’s MW response to instruction; and,

(k)	Be able to remain interrupted during actual event until replaced by other net dependable capability.  In no case may interrupted Load be restored to service without the approval of the ERCOT operator.

(5)	To become and remain fully qualified as a provider of RRS, the Load shall complete the requirements above and the following:

(a)	Pass simulated or actual testing according to ERCOT Procedure; and,

(b)	Perform verification testing as described in Section 6, Reports and Forms.

(6)	A DC tie may be used as Responsive Spinning Reserve up to 30 MW subject to the following constraints:

(a)	The tie shall respond with increased deliveries to ERCOT or decreased deliveries from ERCOT at a frequency of 59.9 Hz;

(b)	The response rate will not be less than 30 MW per minute;

(c)	The response delay will not exceed four seconds;

(d)	The response will be retained until frequency has recovered to a level at or above 60.0 Hz or as directed by ERCOT;

(e)	A QSE claiming DC Tie Responsive Reserve Service must demonstrate the existence of contracts agreeing to provide the required response with the DC Tie operator; and

(f)	A QSE claiming DC Tie Responsive Reserve Service must have an agreement with the Balancing Authority on the opposite side of the DC Tie involved approving the amount and conditions.

(7)	Hydro Unit(s) operating in the synchronous condenser fast response mode may be designated as Hydro Responsive Reserve per Protocol Section 3.18 (5), Resource Limits in Providing Ancillary Service, provided that:

(a)	Only the amount of a hydro powered resource's demonstrated 20 second response may be used as Responsive Reserve;

(b)	For any hydro powered resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 20% of the HSL;

(c)	Automatic controls using the "fast response" mode must be in operation to initiate a move to the generating mode.  The initiation setting of the automatic controls shall not be any lower than 59.9 Hz and the unit must be generating within four seconds of the set relay operation; and

(d)	A Real Time signal of the MW output of hydro units being operated in the synchronous condenser fast response mode is telemetered to ERCOT.

2.3.3	Non-Spinning Reserve Service (NSRS)

*****

2.3.3.1	Types of Non-Spin Reserve Service

(1)	NSRS Generating Resource providers must be capable of being synchronized and ramped to a specified output level within 30 minutes of notification of deployment and run at a specified output level for at least one hour, as specified in paragraph (1)(a) of Protocol Section 3.17.3, Non-Spinning Reserve Service.

(2)	Each Generating Resource providing NSRS must meet the additional technical requirements specified in Protocol Section 8.1.2.2.1, Ancillary Service Technical Requirements and Qualification Criteria and Test Methods.

(3)	NSRS Load Resource providers must be capable of unloading within 30 minutes and remaining unloaded for at least one hour, as specified in paragraph (1)(b) of Protocol Section 3.17.3, Non-Spinning Reserve Service.  Load Resources must not be fulfilling any other commitment from the capacity, including participation in ERCOT markets, self-generation, or other energy transactions.

(4)	Loads providing NSRS must provide telemetered output signals, including breaker status.

(5)	QSEs using dispatchable Loads to provide NSRS must be capable of responding to ERCOT Dispatch Instructions in a similar manner to QSEs using Generation Resource to provide NSRS, as specified in Protocol Section 8.1.2.2.4, Non-Spinning Reserve.

(6)	To become provisionally qualified as a provider of NSRS, a Load shall complete the following requirements:

(a)	Register as a Resource with ERCOT;

(b)	Complete asset registration of the Load Resource;

(c)	Provide ERCOT the appropriate Non-Spinning Load affidavit;

(d)	Test to verify appropriate voice communications are in place for VDIs by ERCOT;

(e)	Be telemetered through the QSE to ERCOT with the Load MW of each Load breaker, breaker status, and signals representing the Load Resource’s MW response to instruction; and,

(f)	Be able to remain interrupted during an ERCOT deployment for a minimum of one hour up to a maximum of the hours of service awarded.

(7)	To become and remain fully qualified as a provider of NSRS, the Load shall complete all the requirements for provisional qualification identified above and the following:

(a)	Respond successfully to an actual ERCOT deployment; or pass simulated or actual testing according to ERCOT’s Procedure; and,

(b)	Perform verification testing as described in Section 6, Reports and Forms.

## 2.4	Outage Coordination

### 2.4.1	ERCOT Responsibilities

The following table outlines the action to be taken by ERCOT as a result of various Outage events, as defined in Protocol Section 3.1.1, Role of ERCOT:

| EVENT | ERCOT ACTION |
| --- | --- |
| Submission of schedules for Planned Outages and Maintenance Outages of Transmission Facilities. | Evaluation of all Planned Outages and Maintenance Outages to ensure the Outage does not result in a violation of the security criteria. |
| Submission of Planned Outages and Maintenance Outages of Reliability Must Run (RMR) Units. Reference: Protocol Section 3.1.4.3, Reporting for Planned Outages and Maintenance Outages of Resource and Transmission Facilities. | Evaluation of all Planned Outages and Maintenance Outages to ensure the Outage does not result in a violation of the security criteria. |
| Submission of Black Start Unit Outages. Reference: Protocol Section 3.1.4.3, Reporting for Planned Outages and Maintenance Outages of Resource and Transmission Facilities. | Evaluation of all requested Planned Black Start Outages to ensure that unavailability may not cause a violation of the security criteria and that a valid methodology of restoring ERCOT from black start conditions without the requested unit exists (Subject to the terms of the applicable Black Start Agreement). |
| Transmission Facility Forced Outages and resultant maintenance on related facilities. Reference: Protocol Section 3.1.4.5, Management of Resource or Transmission Forced Outages or Maintenance Outages. | Evaluate the impact of Forced Outage on the Transmission Grid, perform constraint analysis and implement changes to generation or transmission to restore or maintain secure operating conditions. Previously approved transmission outages may be adjusted or withdrawn if necessary. |
| Receipt of schedules of Planned Outages for Resources. Reference: paragraph (2) of Protocol Section 3.2.3, System Adequacy Report. | Weekly – prepare an assessment of Load vs. Available capacity. The information shall include projected Load, available capacity and deficiency, if any, projected to occur during each week of the rolling 12-month period. ERCOT shall post the report on the MIS Secure Area. |

#### 2.4.2   Forced Outages

#### 2.4.2.1	Generation

A QSE with Generation Resources shall advise ERCOT via telemetry of all Forced Outages of any Resource with a capability greater than 10 MW within one minute as described in Protocol Section 3.1.4.5, Management of Resource or Transmission Forced Outages or Maintenance Outages.  If the forced outage remains on Outage for longer than two hours, it must be entered into the Outage Scheduler, per paragraph (2) of Protocol Section 3.1.4.6, Notice of Forced Outage or Unavoidable Extension of Planned or Maintenance Outage Due to Unforeseen Events.

#### 2.4.2.2	Transmission

(1)	Forced Outages of all transmission lines (>60 kV) shall be reported to ERCOT {{by whom?? The QSE, the TSP??}} immediately per Protocol Section 3.1.4.5, Management of Resource or Transmission Forced Outages or Maintenance Outages.  If the Forced Outage remains on Outage for longer than two hours, it must be entered into the Outage Scheduler, per paragraph (2) of Protocol Section 3.1.4.6, Notice of Forced Outage or Unavoidable Extension of Planned or Maintenance Outage Due to Unforeseen Events.

(2)	Forced Outages of other transmission equipment that affect power flows or transfer capacity will be reported immediately to ERCOT{{by whom?? The QSE, the TSP??}}.

(3)	When a Forced Outage affects the overall security or capacity, ERCOT shall take remedial steps immediately to insure that other facilities are not loaded beyond capacity limits.

(4)	An Outage initiated by protective relay, or manually in response to an observation by field personnel or the TSP System Operator that equipment poses a threat to personnel or equipment. The TSP may remove such equipment from service immediately and notify ERCOT of its action.

2.4.3	Scheduled Outages

2.4.3.1	Generation

(1)	ERCOT will record and monitor each Resource Entity’s annual maintenance schedule for all generating resources owned or operated by the Resource Entity that are within the ERCOT Region, as specified in Protocol Section 3.1.3.2, Resources.

(2)	ERCOT shall have the option of approving or rejecting a Planned Outage or a Maintenance Outage, prior to the removal from service of a Reliability Must-Run (RMR) or Black Start Resource, per Protocol Section 3.1.4.3, Reporting for Planned Outages and Maintenance Outages of Resource and Transmission Facilities.

(3)	ERCOT shall accept all other resource outages submitted more than eight days in advance of the Planned Outage date.  If necessary, ERCOT may withdraw approval of previously approved Transmission Outages to allow this approval per Protocol Section 3.1.6.4, Approval of Changes to a Resource Outage Plan.

(4)	Resource outages submitted eight days or less prior to the outage date (short-noticed resource outage),  and which cannot be accommodated by modifying existing outage schedules, may be rejected as per Protocol Section 3.16.5, Evaluation of Proposed Short-Noticed Resource Outage.

2.4.3.2	Transmission

(1)	ERCOT shall coordinate all proposed planned or maintenance outages of lines or equipment that affects power flows or transfer capacity.  TSPs shall communicate the information to the Distribution Service Providers connected to that TSP.

(2)	ERCOT jointly with TSPs shall attempt to minimize the effect of simultaneous Outages of lines on the reliability of the Region.  ERCOT will establish priorities, when necessary, in accordance with the following to provide adequate time for required Planned or Maintenance Outages.

(3)	When a request for removal of transmission equipment from service is received, ERCOT should conduct studies prior to approval to demonstrate that:

(a)	The capacity of remaining Transmission Elements and associated equipment shall not be exceeded.

(b)	ERCOT shall remain single contingency secure.  Remedial Action Plans (RAPs) may be depended upon to recover from overloads under some contingency conditions.

(c)	ERCOT may limit the loading on generating units to a value that can be delivered by remaining transmission lines.

2.5	Reliability Unit Commitment

2.5.1	Overview of Reliability Unit Commitment (RUC)

(1)	Transmission security analysis and Reliability Unit Commitment (RUC) are used to ensure transmission system reliability and to ensure that enough Resource capacity, in addition to Ancillary Service capacity, is committed in the right locations to reliably serve the forecasted Load on the ERCOT Transmission Grid, as stated in paragraph (1) of Protocol Section 5.1, Introduction.

(2)	RUC considers capacity requirements for each hour of the RUC Study Period with the objective of minimizing costs based on Three-Part Supply Offers.  The calculated Resource commitments arising from each RUC process must be reviewed by ERCOT before issuing Dispatch Instructions to QSEs to commit, extend, or decommit Resources.

(3)	The security sequence is a set of prerequisite processes for RUC that describes the key system components and inputs that are required to support the RUC process, the RUC process itself, and the ERCOT review of the Resource commitment recommendations made by the RUC process.

(4)	Below is the criterion by which ERCOT may remove contingencies from the RUC analysis as described in paragraph (5) of Protocol Section 5.5.1, Security Sequence.

2.5.2	Criteria for Removing Contingencies from the RUC Analysis

(1)	Contingency is known to produce post-contingency results that are incorrect;

(2)	Contingency has been producing in real-time contingency results which cannot be corrected by generation adjustment. (submit to operations engineers for RAP/MP proposal); and

(3)	Contingency is known to produce a non-convergent contingency result which may fail the RUC process. (Must create a generic constraint if non-convergent case represents a voltage collapse).

2.6	Requirements for Under-Frequency Relaying

2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.  The under-frequency relays shall be set to provide load relief as follows:

| Frequency Threshold | Load Relief |
| --- | --- |
| 59.3 Hz | 5% of the ERCOT System Load (Total 5%) |
| 58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%) |
| 58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%) |

(2)	ERCOT will, prior to the peak each year, survey each TSP’s compliance with the automatic load shedding steps above, and report its findings to the ERCOT Technical Advisory Committee (TAC).  For minimum compliance, TSPs are obligated to meet the prescribed percent values at all times.  It is not permitted to use rounding to meet the minimum.  ERCOT will direct a review of the automatic firm load shedding program whenever warranted by conditions.  At a minimum, this review will follow the ROS directed dynamic simulations of automatic firm load shedding conducted at five-year intervals beginning in the summer of 2001.

(3)	Under-frequency relays may be installed on transmission facilities with the approval ERCOT provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay.  A TSP may by mutual agreement, with the approval of the TAC, arrange to have all or part of its automatic load shedding obligation carried by another TSP.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

(4)	TSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the Region to minimize the impact of load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  TSPs shall ensure that the under-frequency relays connected to each load will operate with a fixed time delay of no more than 30 cycles. Total time from the time when frequency first reaches one of the values specified above to the time load is interrupted should be no more than 40 cycles, including all relay and breaker operating times. If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(5)	If a loss of load occurs due to the operation of under-frequency relays, a TO may rotate the physical load interrupted to minimize the duration of interruption experienced by individual customers or to restore the availability of under-frequency load-shedding capability.  In no event shall the initial total amount of load without service be decreased by a TO without the approval of ERCOT.  TOs  shall make every reasonable attempt to restore load, either by automatic or manual means, to preserve system integrity.  TSPs shall exercise extreme caution in restoring load so that the capability limits of generating units and transmission lines are not exceeded.

(6)	Whenever possible, TSPs shall not manually drop load connected to under-frequency relays during the implementation of Step 4 of the Emergency Electric Curtailment Plan.

2.6.2	Generators

(1)	If under-frequency relays are installed, these relays shall be set such that the automatic removal of individual generating units from the Bulk Electric System meets the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (Continuous operation) |
| Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

(2)	No prearranged instruction that conflicts with the above limits will be given for the manual removal of an otherwise operable generating unit.  This Operating Guide is not intended to conflict with the plant operator's responsibility to protect generating units from potentially damaging operating conditions.  While this Operating Guide does not address the removal of generating units for frequency deviations above 60 Hz, it is realized that the generating unit operating restrictions below 60 Hz apply equally to operation of a generating unit above 60 Hz.

2.7	System Voltage Profile

2.7.1	Introduction

(1)	The system voltage profile is a predetermined distribution of desired nominal voltage set points across the ERCOT Region.

(2)	ERCOT shall coordinate and conduct studies with the TSPs to determine the normally desired voltage profile for all Generation Resource busses in the Region as specified in paragraph (1) of Protocol Section 3.15, Voltage Support.

(3)	ERCOT shall establish and update voltage profiles at points of interconnection of Generation Resources to maintain system voltages within established limits.

2.7.2	Maintaining Voltage Profile

ERCOT has the responsibility for monitoring and controlling the voltage profile and should use the following:

(1)	Operations Engineering

(a)	All voltage limits must be based on sound engineering studies that use the appropriate Network Operations Model.  TSP study results should be made available to ERCOT.

(b)	Transfer limits shall reflect voltage and/or reactive restrictions.

(2)	Coordination

(a)	Entities must coordinate high voltage limits in order to guarantee that the Maximum Continuous OverVoltage {{one word??}} (MCOV) of equipment is not exceeded.  TSPs shall notify ERCOT of normal operating voltage limits and post-contingency voltage limits for each bus.

(b)	Low voltage limits must be coordinated in order to prevent one Entity from being a burden to another.

(c)	Voltage limits shall not be violated during all normal and first contingency conditions.

(d)	The operation of all Reactive Power devices under the control of a TO or a QSE will be coordinated under the direction of ERCOT to maintain transmission voltage levels within normal limits and post-contingency voltages within post contingency limits.  Static reactive devices will be managed to ensure that adequate dynamic Reactive Reserves are maintained at all times.

(3)	Notification

(a)	Generation Resources with voltage problems shall notify the TSP to whom they are directly connected.  TSPs shall notify other affected TSPs and ERCOT.

(b)	ERCOT will monitor events and may direct actions to solve the problem.

(4)	Response

(a)	When the voltage levels deviate from established limits, ERCOT shall take immediate steps to relieve the condition using all available reactive resources.

(5)	Monitoring

(a)	TSPs shall provide telemetry to ERCOT on all major transmission bus voltages.  A routine schedule shall be maintained by the TSP to calibrate the telemetry.

(6)	Controls

(a)	ERCOT must be aware of the locations of available reactive capability.

(b)	ERCOT shall maintain displays to monitor voltage profiles and reactive flows.

(c)	Controls to maintain voltage profiles may include capacitor switching, reactor switching, autotransformer tap changing, generator reactive Dispatch, transmission line switching, and Load shedding.

(7)	Documentation

(a)	Each TSP must maintain a voltage/reactive plan for normal and Emergency Conditions.  This document shall be provided to adjacent TSPs as well as ERCOT.

(8)	Emergency or Abnormal Conditions

(a)	Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions.

(b)	Major transmission lines shall be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded.

(c)	Voltage reduction should not be done on the transmission system unless coordinated with adjacent TSPs.

2.7.3	Special Consideration for Nuclear Power Plants

In all planning studies and Real-Time operations, ERCOT and TSPs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission.  ERCOT shall notify the QSE representing a nuclear power plant of the result of any studies where the voltage at the plant switchyard cannot be adequately maintained.  The TSP shall monitor the voltage in Real-Time and provide notice to the QSE representing the nuclear power plant of any voltage inadequacy at the plant switchyard that cannot be corrected within 30 minutes.  High and low limits on switchyard voltage at each nuclear power plant necessary to meet these requirements shall be specified in ERCOT Procedures.

2.7.4	Reactive Considerations for Generation Resources

### 2.7.4.1	 Maintaining System Voltage

(1)	Each generator whose installations initially began operations on or after September 1, 1999, must have and maintain a Unit Reactive Limit (URL) which has an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the generating unit’s maximum net power to be supplied to the transmission grid and both measured at the point of interconnection to the TSP as specific in paragraph (4) of Protocol Section 3.15, Voltage Support.

(2)	The TSP, to which the generator is connected, shall monitor and direct, by communicating with the Generation Resource (at the discretion of the Generation Resource) or the QSE responsible for operation of the Generation Resource, the reactive output of the machines having direct effect on the local system voltage.  Under TSP declared emergency conditions, TSPs may directly dispatch the reactive output of the Generation Resource and follow up with notification of the QSE.  The TSP will, using Good Utility Practices, equalize the reactive output of the generators based on size (net dependable MW capability), reactive capability, reactive limits and system voltage impact.

(3)	Qualified Renewable Generation Resources in operation before February 17, 2004, and all other Generation Resources that were in operation prior to September 1, 1999, whose current design does not allow them to meet the URL as stated above, must maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as per paragraph (5) of Protocol Section 3.15, Voltage Support.  The URL for these generation resources will be determined by the results of the Corrected Unit Reactive Limits (CURL) test mentioned in Section 3 of these Guides.

(4)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and /or equipment procurement decisions were made prior to February 17, 2004, whose design does not allow them to meet the URL as stated above, must maintain a URL that is limited to the capability (MW) as per paragraph (6) of Protocol Section 3.15, Voltage Support.  The URL for these generation Resources will be determined by the results of the Corrected Unit Reactive Limits (CURL) test mentioned in Section 3 of these Guides.

2.7.4.2	 Parameters for Standard Reactor and Capacitor Switching Plan

(1)	TSPs shall provide switching plans for reactors, capacitors, and other reactive controlled sources to ERCOT.  The plans shall be posted on the MIS Secure Area and must be provided in accordance with the NOMCR or other ERCOT prescribed process. The parameters to be provided in the standard reactor and capacitor switching plan as required by Protocol Section 3.10.7.1.5, Reactors, Capacitors, and other Reactive Controlled Sources are as follows:

Device Attributes

(a)	Transmission Element name per Protocol Section 3.10.7.1

(b)	Substation Name

(c)	Associated switching device or controlling device name (Transmission Element name per Protocol Section 3.10.7.1)

(d)	Electrical Bus name and location

(e)	Voltage Level of Transmission Element

(f)	Installed capacity or range of device in MVARs (Nominal MVAR)

(g)	Limits of device (in normal and emergency situations)

(h)	Device output limitations (such as capacity and duration in normal and emergency situations)

(i)	Planned regulating voltage and control point location

(j)	Local reactive device dependencies or interactions

(k)	Voltage or time determined for operation of device (both in and out of service)

(l)	SCADA availability (Status and MVAR flow)

(m)	Schedules of device

(i)	Time-based

(ii)	Voltage-based

(iii)	Load-based

(iv)	Contingency-based

(v)	Normal Operation

(vi)	Emergency Operation

(vii)	Seasonal

(viii)	Others as required by technology

(2)	From a modeling perspective, ERCOT shall work with the Market Participants to ensure that the advanced application tool(s) voltage/reactive control methodology reflects actual field operation to the extent practicable.

2.7.4.3	Unit Dispatch Beyond the Unit Reactive Limit (URL)

Each generator shall respond to ERCOT instructed voltage control, including exceeding its URL, as specified in Protocol Section 6.5.7.7, Voltage Support Service.  For multi-generator busses, ERCOT shall not instruct any single generator to operate beyond its URL until all generators on-line and interconnected at the same transmission bus, have been instructed to their respective URLs.

2.8	External Inter-Ties

2.8.1	Balancing Authority Operations

(1)	Balancing Authority Area schedules between ERCOT and interconnected non-ERCOT Balancing Authority Area(s), through the use of schedules over DC Tie(s), will be implemented in accordance with Protocol Section 4.4.4, DC Tie Schedules and NERC Standards. Scheduling must also be in accordance with any applicable FERC tariffs.

(2)	ERCOT will perform schedule confirmation with the applicable interconnected non-ERCOT Balancing Authority Area(s) and will coordinate the approval process for the NERC tags as both the ERCOT Balancing Authority and on behalf of ERCOT TSPs.

2.8.2	Operation of DC Ties

(1)	ERCOT will confirm interconnected non-ERCOT Balancing Authority schedule profiles with the DC Tie operator, who will control the tie to the schedules agreed to by both the designated Security Coordinator for the interconnected non-ERCOT Balancing Authority  and ERCOT.

(2)	Exports from ERCOT via DC Ties will be treated as a Load connected at transmission voltage.

(3)	Imports into ERCOT via DC Ties will be treated as generation injection located at the DC tie point.

(4)	Any changes in the interconnected non-ERCOT Balancing Authority schedules due to a de-rating of the tie or other change within the NERC Standards will be communicated to ERCOT by the DC Tie Operator or designated security coordinator for the interconnected non-ERCOT Balancing Authority.

(5)	ERCOT Balancing Authority will coordinate operation of the DC Tie(s) with the DC Tie Operator such that the Inadvertent Energy Account is maintained as close to zero as possible.

2.8.3	Inadvertent Interchange Management

The only Inadvertent Energy will be between ERCOT and the Southwest Power Pool (SPP and/or Comision Federal de Electricidad (CFE).  ERCOT shall track any differences between the net of deemed meter readings at each DC Tie and the actual metered value at that DC Tie in an “Inadvertent Energy Account” between ERCOT and each interconnected non-ERCOT Balancing Authority as per Protocol Section 6.5.4, Inadvertent Energy Account.  Accounting / payback will be handled according to NERC Standards.  The hourly difference between a Balancing Authority’s actual net interchange and a Balancing Authority’s scheduled net interchange is classified as “Inadvertent Energy”.  All Inadvertent Energy is placed in an Inadvertent Payback Account to be paid back in kind.