## Slide 1: Texas Nodal ICCP Business Case By Jeyant Tamby, ERCOT

## Slide 2: Nodal Protocol Requirements
The Nodal Protocols require ERCOT to supply certain data via “SCADA or ICCP”. Some Examples:
  6.3.2(2) – “Communicate all Base Points, Dispatch Instructions and LMPs for energy and Ancillary Services using ICCP, SCADA, or Verbal Dispatch Instructions”
  6.5.7.6.1(4) – “Control signals are provided to the QSE using the ICCP data link or SCADA”
  6.5.7.6.2.2(11) – “ERCOT shall issue Responsive Reserve deployment Dispatch Instructions over SCADA or ICCP for Generation Resources and XML for Load Resources.”

## Slide 3: Current Communication Path

## Slide 4: RTU/DNP – Architectural Issues
Communication with the RTUs is accomplished using the DNP 3.0 protocol.
Nodal Model will increase DNP data exchange volume by more than 130%
The specific issues concerning the current architecture are:
  Communication capacity and performance limitations
  Lack of a consistent definition of data quality codes across all market participant systems
  Maintenance complexity
  Lack of support for a security environment

## Slide 5: ERCOT Recommendation for Texas Nodal

## Slide 6: Impact Assessment
The level of effort for a particular participant to convert to full ICCP data exchange depends on a number of factors such as:
  The total number of RTU points that must be mapped to the ICCP database
  The readiness of a system without ICCP to accept an ICCP upgrade
  For participants choosing an ICCP gateway, the native protocols available to connect the participant’s system to the gateway and the means by which physical connections can be established

## Slide 7: Conversion Options
Conversion Options | Relative Complexity | Comment
(1) No conversion required. | None | Participant is already exchanging all data via ICCP.
(2) Move RTU data to ICCP | Small | Involves adding all points presently on the RTUs to the ICCP database.
(3) Move RTU data to ICCP and configure a new ICCP association with ERCOT | Medium | Includes the effort of recommendation (2) plus testing new ICCP associations with ERCOT.
(4) Procure and implement ICCP via system upgrade or ICCP gateway | Large | Involves procuring an ICCP communication upgrade or adding an ICCP gateway.

## Slide 8: Conversion Prediction vs. Existing Capability
Number of Participants with the stated capabilities | Participant Type | Current Data Exchange Capabilities |  |  | Predicted Conversion Option
 |  | Real-time Data via RTU? | Real-time Data via ICCP? | ICCP Available? | 
12 | QSE | Yes | Yes | Yes | 2
2 | QSE | Yes | No | Yes | 3
7 | QSE | Yes | No | No (or unknown) | 4
4 | TDSP | Yes | No | No | 4
9 | TDSP | No | Yes | Yes | 1

## Slide 9: Rough Cost Estimates by Option
Project Phase | Project Tasks | Conversion Options |  |  |  |  | 
 |  | Option 2 - Move RTU data to ICCP | Option 2 - Hours | Option 3 - move RTU data to existing ICCP and configure a new ICCP association | Option 3 - Hours | Option 4 - Procure and implement ICCP from a supplier | Option 4 - Hours
Planning, Specification and Vendor Management | Define, select and issue PO. | NO | NO | NO | NO | $2,600 | 40
 | Vendor Management | NO | NO | NO | NO | $2,600 | 40
Vendor Deliverable | Hardware | NO | NO | NO | NO | $16,000 | 
 | Software | NO | NO | NO | NO | $48,000 | 
 | Field Setup and Living Expense | NO | NO | NO | NO | $15,000 | 231
ICCP Configuration/ Build DB | Training | NO | NO | NO | NO | $17,600 | 271
 | ICCP Configuration/ point definition | $22,707 | 349 | $11,873 | 183 | $7,540 | 116
 | DB Build/Load | $520 | 8 | $520 | 8 | $520 | 8
 | Setup Association | NO | NO | $2,080 | 32 | $2,080 | 32
ICCP Installation/Test | Installation | NO | NO | NO | NO | $7,280 | 112
Testing with ERCOT | Point to Point | $3,207 | 49 | $2,123 | 33 | $1,690 | 26
Production Installation | Cutover | $585 | 9 | $585 | 9 | $2,600 | 40
 | Operation Stability | $1,040 | 16 | $1,040 | 16 | $3,120 | 48
Total |  | $28,059 | 432 | $18,221 | 280 | $126,630 | 964

## Slide 10: Questions?
Questions?