Standard Development Roadmap

This section is maintained by the drafting team during the development of the standard and will be removed when the standard becomes effective.

This proposed standard is a translation of planning measure III.C.M8, which was not included in the approval Version 0 reliability standards because it required further work.

Development Steps Completed:

- A SAR was posted from December 2, 2004, through January 7, 2005.

- The SAC appointed a standard drafting team on January 13, 2005.

- The drafting team posted its response to SAR comments and all other historical comments on April 19, 2005.

- The drafting team posted Draft 1 of the standard on April 21, 2005.

- The drafting team posted Draft 2 of the standard on September 1, 2005.

Description of Current Draft:

This is the 3rd draft of the standard to be posted for industry review while the standard is field tested.

Future Development Plan:

| Anticipated Actions | Anticipated Date |
| --- | --- |
| - Review revised standard and results of field test for industry comment. | To be determined |
| - Consider comments submitted with 3rd posting; post consideration of comments | To be determined |
| - Post standards and implementation plan for 30-day pre-ballot review. | To be determined |
| - Conduct 1st ballot. | To be determined |
| - Consider comments submitted with 1st ballot; post consideration of comments | To be determined |
| - Conduct 2nd ballot. | To be determined |
| - Post standards and implementation plan for 30-day review by Board. | To be determined |
| - Board adoption. | To be determined |
| - Effective date. | To be determined |

Definitions of Terms Used in Standard

This section includes all newly defined or revised terms used in the proposed standard.  Terms already defined in the Reliability Standards Glossary of Terms are not repeated here.  New or revised definitions listed below become approved when the proposed standard is approved.  When the standard becomes effective, these defined terms will be removed from the individual standard and added to the Glossary.

No new definitions are proposed for this standard.

- Introduction

- Title:	Coordination of Generator Voltage Regulator Controls with Unit Capabilities and Protection

- Number:	PRC-019-1

- Purpose:	Ensure generator voltage regulator controls and limit functions are coordinated with the generator’s capabilities and protective relays.

- Applicability

  - Regional Reliability Organization.

  - Generator Owner.

- Proposed Effective Dates:	To be determined:

- One year beyond Board of Trustee adoption for Requirement 1

- Two years beyond Board of Trustee adoption 1st 20% compliant with Requirement 2 and Requirement 3

- Three years beyond Board of Trustee adoption 2nd 20% compliant with R2, R3

- Four years beyond Board of Trustee adoption 3rd 20% compliant with R2, R3

- Five years beyond Board of Trustee adoption 4th 20% compliant with R2, R3

- Six years beyond Board of Trustee adoption 5th 20% compliant with R2, R3

- Requirements

- The Regional Reliability Organization shall establish and maintain criteria for exemptions to any of the Generator Owner requirements in R2.

- ERCOT Operating Guides 3.1.4 states “This Section defines the minimum requirements for the integration of generation facilities greater than 10 MW into the ERCOT System.”

- Unless exempted by the Regional Reliability Organization in accordance with R1, the Generator Owner shall have study results that show it verified that its generator voltage regulator controls and limit functions are coordinated with the generator’s capabilities and protective relays.  This study shall include the following:

  - Plots, or data that could be plotted for the following:

    - Generator capability curve, including specification of nominal voltage, ambient air or cooling temperature, or hydrogen pressure.

    - Steady state over-excitation limiter and under-excitation limiter control characteristics.

    - MW limit of the prime mover.

    - Any other limit that could restrict the megawatt or megavar capability.

    - Loss of excitation / field protective relay characteristics.

    - Volts-per-hertz protection settings including volts-per-hertz limiters in the automatic voltage regulator.

- The Generator Owner shall have the information in R2.1.1 through R2.1.6 available to show to the Regional Reliability Organization upon request (within 30 calendar days).

- Measures

- The Regional Reliability Organization shall, within 30 calendar days of a request, provide to Generator Owners its exemption criteria defined in accordance with R1.

- The Generator Owner shall have evidence it showed the Regional Reliability Organization the information identified in R2.1 through R2.1.6 within 30 calendar days of a request.

- Compliance

- Compliance Monitoring Process

  - Compliance Monitoring Responsibility

NERC for the Regional Reliability Organization.

Regional Reliability Organization for Generator Owners.

  - Compliance Monitoring Period and Reset Timeframe

- The compliance reset period is one calendar year.

  - Data Retention

The Generator Owner shall retain all current information needed to show coordination. The Compliance Monitor shall retain any audit data for three years.

  - Additional Compliance Information

The Regional Reliability Organization and Generator Owner shall demonstrate compliance through self-certification or audit (periodic, as part of targeted monitoring or initiated by complaint or event), as determined by the Compliance Monitor.

- Levels of Non-Compliance

  - Level 1:  The Regional Reliability Organization did not provide the exemption criteria in accordance with R1.

  - Level 2: The Generator Owner information on coordination of the generator voltage regulator controls and limit functions does not address one of the requirements identified in accordance with R2.1.1 through R2.1.6.

  - Level 3: Not applicable.

  - Level 4: The Generator Owner information on coordination of the generator voltage regulator controls and limit functions does not address two or more of the requirements identified in accordance with R2.1.1 through R2.1.6.

- Regional Differences

- None identified.

#### Version History

| Version | Date | Action | Change Tracking |
| --- | --- | --- | --- |