| PRR Number | 682 | PRR Title | Emergency Electric Curtailment Plan (EECP) Event Realignment |
| --- | --- | --- | --- |
| Date |  | 10/9/06 |  |
| Submitter’s Information |  |  |  |
| Name |  | Ellis Rankin |  |
| E-mail Address |  | erankin@txued.com |  |
| Company |  | TXU Electric Delivery |  |
| Company Address |  | 2233-B Mountain Creek Pkwy Dallas, TX 75211 |  |
| Phone Number |  | 214-743-6825 |  |
| Fax Number |  | 972-263-6710 |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

| Assumptions | 1 | System changes would take place at ERCOT only. |  |
| --- | --- | --- | --- |
|  | 2 | Data will be used for communication purposes only. |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | None | None |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Early communication of reliability concerns by ERCOT | None |
| Additional Qualitative Information | 1 | Provide better information and data to market participants and concerned entities. |  |
|  | 2 | Conform with Operating Guide proposed revisions in OGRR186 |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |

Comments

My edits are as described below and for the indicated purposes

1. Correct the description of the calculation of PRC where RDF is applied.

2. Added “physical” where I thought it was needed within the PRC definition.

3. Clarified that it was “total” PRC that was being monitored and used for triggering notifications and EECP steps.

4. Re-worded the requirement that ERCOT submit its value for RDF to the ROS for approval.

5. Added some clarifying language to the sentence that describes ‘management’s discretion‘ to issue public appeal ‘at any time’.

6. Added language clarifying that the decision to declare Step 3 based upon frequency would be subject to responsible operator’s assessment of reliability risk.

7. Added clarification to the description of the assigned TDSP percentages of load shedding.

8. Added language that would have RMR units go to full load capability at “ERCOT’s direction”

9. Inserted “amount of” in front of “RRS MW”

10. Changed “beneficial” to “effective” where TDSP voltage reduction was described in Step 2.

11. Re-worded the description of public appeal in Step 2

12. Re-worded the description of TDSPs responsibility to protect safety, health, etc when shedding firm load in Step 3 (and also substituted “shed” for “drop”).

The above edits are intended to clarify and improve without making any fundamental change.

Proposed Protocol Language Revision

# 2	Definitions and Acronyms

2.1	Definitions

Physical Responsive Capability (PRC)

The Physical Responsive Capability is a representation of the amount of system wide online capability that has a high probability of being able to quickly respond to system disturbances.  The PRC shall be calculated by (i) determining each Resource meeting the requirements defined in the Operating Guides,  (ii) determining for each Resource the lesser quantity of the latest Net Dependable Capability, the Resource Plan HOL, or the telemetered real time capability, (iii) multiplying the lesser quantity of each Resource by 1 - RDF (Reserve Discount Factor), and (iv) using that result to determine the amount of physical responsive reserve capability then available on each Resource. The sum, for all Resources, of the physical responsive reserve capability as determined for each Resource yields the total PRC which shall be used by ERCOT to determine the appropriate Emergency Notification and EECP Steps.

Reserve Discount Factor (RDF)

The Reserve Discount Factor is a representation of the average amount of system wide capability that, for whatever reason, is historically undeliverable during periods of high system demand.  ERCOT will submit the RDF value to the ROS for approval.

5.6.6.1	Emergency Electric Curtailment Plan (EECP)

At times it may be necessary to reduce electrical demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing demand during such emergencies, ERCOT will initiate and coordinate the implementation of the Emergency Electric Curtailment Plan following the EECP Steps set forth  below in subsection 5.6.7, EECP Steps.

The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

ERCOT’s operating procedures shall meet the following goals while continuing to respect the confidentiality of market sensitive data:

(1)	Use of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT system;

(2)	Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(3)	Maximum use of ERCOT System capability;

(4)	Maintenance of station service for nuclear Generation Resource Facilities;

(5)	Securing of startup power for Generation Resources;

(6)	Operation of power Generation Resources during loss of communication with ERCOT;

(7)	Restoration of service to critical Loads in the manner defined in the Operating Guides; and

(8)	Restoration of service to all customers following major system disturbances, giving priority to the larger groups of customers.

ERCOT shall be responsible for coordinating with QSEs and TDSPs to monitor system conditions, initiating the EECP steps, notifying all QSEs, and coordinating the implementation of the EECP Steps while maintaining transmission security limits.

ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation when it is in the interest of maintaining acceptable reserve margin (PRC) needed to support grid reliability.

During the EECP, ERCOT has the authority to obtain energy over the DC Ties when transmission capacity is available across the DC Tie.  ERCOT will not supersede any market use of the DC Ties.

[PRR543: Replace the paragraph above with the following upon ERCOT Legal review of the Comision Federal de Electricidad contract:] During the EECP, ERCOT has the authority to obtain energy from BtB Ties or Block Load Transfers (BLTs) from non-ERCOT Control Areas when capacity is available.

Some of the EECP Steps will not be applicable if transmission security violations exist. There may be insufficient time to implement all Steps in sequence, but to the extent practicable, ERCOT will use Ancillary Services which bidders have made available in the market to maintain or restore reliability.

ERCOT may, subject to the on duty responsible operator’s assessment of reliability risk, immediately implement Step 3 of the EECP any time the steady-state system frequency is below 59.8 Hz and will immediately implement Step 3 any time the steady-state frequency is below 59.5 Hz.

Assigned TDSP percentages for Step 3 Load shedding will be based on previous year’s TDSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and published annually.

5.6.6.2 	General Procedures Prior to EECP Operations

- Prior to declaring EECP Step 1 detailed in Section 5.6.7, EECP Steps, ERCOT shall:

(1)	Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability as directed by ERCOT;

(2)	Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT required generating unit or Resource performance testing;

(3)	Utilize available resources providing Non-Spin Reserve Services that can be deployed to increase Responsive Reserves; and

(4)	ERCOT shall monitor total Physical Responsive Reserve (PRC) using the Reserve Discount Factor (RDF) to determine amount of PRC.  The amount of total PRC  will be used by ERCOT to determine the appropriate Emergency Notification and EECP Steps.

In addition, ERCOT may issue an appeal through the public news media for voluntary load reduction if authorized by the ERCOT Chief Executive Officer or its designee based on an evaluation of existing and expected system conditions.

5.6.7	EECP STEPS

Step 1 — Maintain ERCOT Total Physical Responsive Capability (PRC) on units plus amount of RRS MW provided from LaaR Equal to 2300 Mw.  ERCOT will:

(1)	Utilize available DC tie capability that is not already being used by the market;

(2)	 Notify the Southwest Power Pool Security Coordinator;

(3)	Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency; and

(	  Issue an appeal through public media for voluntary load reduction.

[PRR543: Add the following bullet upon ERCOT Legal review of the Comision Federal de Electricidad contract:] (5) Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers.

QSEs will:

(1)  	Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

Step 2 — Maintain ERCOT Total Physical Responsive Capability (PRC) on units plus amount of RRS MW Provided from LaaR Equal to 1750 MW.  In addition to measures associated with Step 1, ERCOT will:

(1)	Instruct TDSPs to reduce Customers load by using distribution voltage reduction measures, if deemed effective by the TDSP;

(2)	Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays); and

(3)	With the approval of the affected Non-ERCOT control area, may instruct TDSPs to implement BLTs, which transfer load from the ERCOT control area to Non-ERCOT control areas.  Use of a BLT will be defined in the ERCOT Operating Guides.

(4)	If one is not already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation.

Step 3 — Maintain system frequency at 59.8 Hz or greater

In addition to measures associated with Steps 1 and 2, ERCOT will direct all TDSPs and their agents to shed firm load, in 100 MW blocks, distributed using published percent allocations as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hz.

TDSPs will endeavor to protect the safety and health of the community including essential human needs while meeting ERCOT assigned firm load shed obligation.  Whenever possible, TDSPs shall not manually shed load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.

6.10.3.2	Responsive Reserve Qualification Testing Criteria

(1)	Testing using Generation Resource(s)

(a)	A test for RRS shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow, and not previously disclosed to the QSE, ERCOT shall send a signal to the QSE requesting it to provide an amount of RRS.  The QSE shall acknowledge the start of the test.

(d)	For the thirty (30) minute duration of the test, the QSE output shall be measured as clock-minute average outputs for:  (i) the clock-minute prior to the instructions being received from ERCOT; (ii) the clock-minute following receipt of instructions from ERCOT and continuing for ten (10) minutes; and (iii) for each of the subsequent nineteen (19) clock-minutes.  All measurements shall confirm the additional delivery of energy due to the deployment of Responsive Reserve Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred five percent (105%) of the amount requested by ERCOT.  Satisfactory performance shall be deemed acceptable if ninety percent (90%) of each clock-minute measurement ten (10) minutes after notice through the balance of the test period is equal to at least ninety-five percent (95%) and no more than one hundred five percent (105%) of the amount expected.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the QSE is capable of providing RRS and shall provide a copy of the certificate to the QSE.

(2)	Testing using Load(s) Acting as a Resource

(a)	A test for RRS shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow, and not previously disclosed to the QSE, ERCOT shall send a signal to the QSE requesting it to provide an amount of RRS.  The QSE shall acknowledge the start of the test.

(d)	Upon ERCOT issuing a verbal instruction to the QSE to deploy the LaaR, the QSE shall demonstrate that it has procedures in place to satisfy a satisfactory deployment of the LaaR(s) providing Responsive Reserve Service as required in Step 2 of an EECP,  Section 5.6.7, EECP Steps.  All measurements shall confirm the additional delivery of energy due to the deployment of Responsive Reserve Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred and fifty percent (150%) of the amount requested by ERCOT.  A deployment will be deemed acceptable when ERCOT confirms the interruption of the Load(s) within ten (10) minutes of issuance of the instruction by ERCOT.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the QSE is capable of providing RRS from LaaRs and shall provide a copy of the certificate to the QSE designating its qualification to provide RRS from LaaRs.