## Slide 1: NSRS in Nodal Proposal for Deployment & Recall Procedures
ERCOT ROS
10/12-13/2006
By:
S.Niemeyer
R.Jones
R.Wheeler
B.Green
J.Dumas
P.Breitzman

## Slide 2: ISSUE & Background
At the August 10-11ROS meeting the PDCWG reported on a TAC assignment to define the proper procedures in Nodal for the deployment and recall of resources providing NSRS,
At that meeting Chair formed a small task force to examine Protocols 6.5.7.6.2.3(1) and recommend a set of procedural steps,
The small task force met on 9/14 and considered two written proposals (J.Adams-ERCOT & B.Green-GP&L),
B.Green’s proposal was selected by the task force and finalized.

## Slide 3: What the Nodacols Say
6.5.7.6.2.3 Non-Spinning Reserve Service Deployment
(1)ERCOT shall deploy Non-Spinning Reserve Service using SCED for On-Line Generation Resources with Energy Offer Curves and by Operator Dispatch Instruction for Resources with Output Schedules, Off-Line Generation Resources and Load Resources. ERCOT shall develop a procedure approved by TAC to deploy Resources providing Non-Spinning Reserve Service. ERCOT operators shall implement the deployment procedure when a specified threshold(s) in MW of capability available to SCED to increase generation is reached. ERCOT Operators may implement the deployment procedure to recover deployed Responsive Reserve or when other Emergency Conditions exist.

## Slide 4: Conditions Leading to NSRS Deployment
#1) Detection of insufficient capacity for
energy dispatch for future operations,
#2) Disturbance Conditions: unit trip,
sustained freq decay, sustained low
freq ops.,
#3) SCED does not have enough energy
available to execute properly,
---ISO Operator makes final decision and initiates deployment.

## Slide 5: Deployment Under Condition #1 [Detection of insufficient capacity for future operations]
QSE gets a resource-specific instruction for off-line generation for NSRS with expected amount of capacity to be available and for how long, QSE must have resource on and ready for SCED base points asap, SCED will respond to changes in status via telemetry from QSE, resource must respond within 30 minutes, QSE will reduce NSRS A/S schedule to zero in COP and telemetry
Load resource will get instruction for MW level of energy deployed and duration of instruction, if bought by block then deployed by block, load must respond within 30 minutes
On-Line Generation w/energy offer curve will be notified of total capacity reserved for NSRS is being dispatched, ERCOT will auto calculate a new HASL for SCED by reducing the NSRS schedule to zero, QSE updates COP and telemetry parameters, resource must deliver in 30 minutes,

## Slide 6: Deployment Under Condition #1-cont’d [Detection of insufficient capacity for future operations]
On-Line Generation w/output schedule will get an instruction to deploy NSRS with energy amount and duration, DSR will adjust its output schedule in telemetry and COP, for non-DSR ERCOT will adjust the output schedule for operating period to show deployment amount.

## Slide 7: Deployment Under Condition #2 [Disturbance Conditions]
The procedure for deployment will be the same as in Condition #1,
Determination of need will be driven by the A/S Capacity Monitor program executing every 10 seconds,
EECP processes may govern

## Slide 8: Deployment Under Condition #3 [SCED has insufficient energy available to operate properly]
Same deployment procedure as Conditions #1 & #2,
Determination of need based on A/S Capacity Monitor, executing every 10 seconds,
SCED’s failure to converge initiates Emergency State, emergency processes will then govern deployment

## Slide 9: Recall of NSRS Deployments
Deployed for each clock hour until HRUC sees a sustained capacity margin >8% of forecasted load demand,
Previously off-line generation resource allowed to ramp down at normal rate and trip off,
Previously on-line generation (w/offer curve) will stay on and restore NSRS A/S schedule and ERCOT will update its HASL prior to next SCED,
Previously on-line generation (w/output schedule) will stay on and back out NSRS amount from schedule [can be done incrementally],
Load Resource will restore NSRS capability and energy w/in 3 hours from deployment expiration or restore it from another resource.

## Slide 10: Action Requested of ROS
Endorse the principles in the white paper and forward white paper to TAC for consideration as “homework completed”.