| PRR Number | 686 | PRR Title | Black Start Testing Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline (Normal or Urgent) | Normal | Action |  | Tabled |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 6.10.3.6, System Black Start Capability |  |  |
| Proposed Effective Date |  | TBD |  |  |
| Priority & Rank Assigned |  | N/A |  |  |
| Revision Description |  | This PRR specifies the requirements for starting the next start Resource and which tests are allowed to be run simultaneously. |  |  |
| Overall Market Benefit |  | This PRR documents ERCOT's practice of conducting next start Resource tests when new next start Resources are selected. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts: Has the Credit Workgroup reviewed the PRR? If so, are there credit impacts? (indicate Yes or No, and if Yes, include a summary of impact) |  | TBD |  |  |
| Procedural History |  | - On 08/23/06, PRR686 was posted. - On 08/30/06, ERCOT posted the Impact Analysis (IA). - On 09/19/006, ERCOT Comments were posted. - On 09/21/06, PRS considered this PRR. - On 10/19/06, PRS considered the Recommendation Report. |  |  |
| PRS Recommendation (indicate whether all segments were present for the vote, and the segment of parties that voted no or abstained) |  | On 09/21/06, the PRS unanimously voted to recommend approval of PRR686 as revised by ERCOT Comments. All Market Segments were present for the vote. On 10/19/06, the PRS unanimously voted to table PRR686 until the November PRS meeting. All Market Segments were present for the vote. |  |  |
| Summary of PRS discussion |  | On 09/21/06, PRS agreed to table the related NPRR019, Black Start Testing Requirements until completion of Transition Plan Task Force (TPTF) review. On 10/19/06, PRS agreed to table PRR686 until completion of TPTF’s review of the related NPRR019, Black Start Testing Requirements. |  |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

| Assumptions | 1 | NPRR documents current practices. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | None | None |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 |  |  |
| Additional Qualitative Information | 1 | Clearly defines Black Start testing practices |  |
|  | 2 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | David Wood on behalf of the Black Start Task Force |
| E-mail Address | david.wood @austinenergy.com |
| Company | Austin Energy |
| Segment |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| 091906 ERCOT | Clarify the Black Start testing process and provide more detail regarding disqualification and decertification of Black Start Resources. |

Revised Proposed Protocol Language

6.10.3.6	System Black Start Capability

(1)	Qualification will be provided to any Black Start Resource that has met the following requirements:

(a)	Verified control communication path performance;

(b)	Verified primary and alternate voice circuits for receipt of instructions;

(c)	Passed the “Basic Starting Test” as defined below;

(d)	Passed the “Line-Energizing Test ” as defined below;

(e)	Passed the “Load-Carrying Test” as defined below;

(f)	Passed the “Next Start Resource Test” as defined below;

(g)	If not starting itself, has an ERCOT approved firm standby power contract with deliverability under ERCOT blackout circumstances from another power pool that can be finalized upon selection as a Black Start Resource;

(h)	If not starting itself, has an ERCOT approved agreement with the necessary TDSPs for access to another power pool, for coordination of switching during a Black Start event, for coordination of maintenance through the ERCOT Outage scheduler for all non-redundant transmission startup feeds; and

(i)	If dependent upon non-ERCOT transmission Resources, agreements providing this Transmission Service have been provided in the proposal.

(2)	On successful demonstration of system Black Start Service capability, ERCOT shall qualify the Black Start Resource as being permitted to provide the system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource.  Qualification shall be valid for the time frames set forth below. Except under extenuating circumstances, as reasonably determined by ERCOT, all qualification testing for the next year of Black Start Service must be completed by December 1 of each year.  ERCOT shall revoke the qualification of a Black Start Resource and reduce the Black Start Resources’ Hourly Standby Fee (if under an existing Black Start Agreement) to zero during the time of disqualification if the Black Start Resource fails to perform successfully during a test describe herein, until the Black Start Resource is successfully retested.  ERCOT may limit the number of retests allowed. Retesting is only required for the aspect of system Black Start Service capability for which the Black Start Resource failed. If a Black Start Resource under an existing Black Start Agreement does not successfully re-qualify within two months of failing a test described herein, ERCOT shall decertify the Black Start Resource for the remainder of the calendar year as described in Section 7 of the “Standard Form Black Start Agreement.” The following tests are required for Black Start Service qualification:

(a)	Basic Starting Test:

(i)	The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another power pool, without support from the ERCOT System, is tested annually, either as a stand-alone test or with the other tests described below.  The test is run during a one-week period agreed on in advance by the Black Start Resource and ERCOT and must not cause Outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(ii)	ERCOT shall confirm the dates of the test with the Black Start Resource;

(iii)	At a time during a previously agreed test week window not previously disclosed to the Black Start Resource, ERCOT will initiate the test;

(iv)	The Black Start Resource, including all auxiliary Loads, will be isolated from the ERCOT power system, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of another power pool through a firm standby agreement will connect to the external grid, start-up, carry internal Load, disconnect from the external grid if not supplied through a black start capable DC Tie, and continue equivalently to what is required of other Black Start units;

(v)	The Black Start Resource will start without assistance from the ERCOT System, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract;

(vi)	The Black Start Resource must remain stable (in both frequency and voltage) in no Load condition or while supplying only its own auxiliary Loads or Loads in the immediate area for at least thirty (30) minutes; and

(vii)	The Black Start Resource must have verified that its Volts/Hz relay, over excitation limiter, and under excitation limiter are set properly and that no protection devices will trip the unit within the required reactive range.  Data to verify these settings will be provided to ERCOT.

(viii) 	Qualification under the Basic Starting Test is valid for one (1)  year.

(b)	Line-Energizing Test:

(i)	The ability of the Black Start Resource to energize transmission will be tested when conditions permit as determined by the TDSP but at least once every three years.  Tests will be conducted at a time agreed on by the Black Start Resource, TDSP, and ERCOT.

(ii)	Sufficient transmission will be de-energized such that when it is energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan calls for the Black Start Resource to supply.  ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource.

(iii)	The Resource Entity controlling the Black Start Resource shall coordinate with TDSPs to submit necessary transmission outages to ERCOT for approval thirty (30) days before the scheduled test date.

(iv)	The test shall commence with a Basic Starting Test.

(v)	ERCOT will direct the Black Start Resource to energize the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line.  Alternatively, if ERCOT agrees, the transmission line can be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed.

(vi)	The Black Start Resource must remain stable (in both frequency and voltage) in no Load condition or while supplying only its own auxiliary Loads or external Loads and controlling voltage for at least thirty (30) minutes.

(vii)	This test may be performed together with the Basic Starting Test in one thirty (30) minute interval.

(viii)	Qualification under the Line-Energizing Test is valid for three (3) years.

(c)	Load-Carrying Test:

(i)	The ability of the Black Start Resource to remain stable and to control voltage and frequency while supplying restoration power to the Load that ERCOT’s restoration plan calls for the Black Start Resource to supply shall be tested as conditions permit, but at least once (1) every six (6) years.

(ii)	The test shall commence with a Basic Starting Test followed by

a Line-Energizing Test.

(iii)	The TDSP operator will direct picking up sufficient Load to demonstrate the Black Start Resource’s capability to supply the required power identified in ERCOT’s restoration plan, while maintaining voltage and frequency for at least thirty (30) minutes.  In the event that there is no additional Load in the immediate vicinity of the plant (e.g., hydro plants), this test can be conducted with no Load.

(iv)	This test may be performed together with the Basic Starting Test and Line Energizing Test in one thirty (30) minute interval.

(v)	Qualification under the Load- Carrying Test is valid for six (6) years.

(d)	Next Start Resource Test:

(i)	The ability of a Black Start Resource to start up the next start unit’s largest required motor while continuing to remain stable and control voltage and frequency shall be tested.

(ii) 	To pass the test, (a) the potential Black Start Resource must start the next start unit (as determined by ERCOT), or start the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or (b) the Resource Entity shall demonstrate to the satisfaction of ERCOT staff through simulation studies conducted by the Resource Entity or a qualified third party, that the potential Black Start Resource is capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.  Potential Black Start Service bidders may request next start unit information from ERCOT prior to the selection process to satisfy this requirement.  ERCOT shall request this information from the designated next start unit as follows:  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate Black Start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource or the Generation Resource Entity to ERCOT within thirty (30) days. Such information shall be considered Protected Information by the requesting Resource Entity when provided to the Resource Entity.

(iii)	This test shall be repeated when a new next start unit is selected.

(ii)	If a physical test is performed, the test shall commence with a Basic Starting Test, followed by

a Line-Energizing Test and

a Load-Carrying Test as a stand-alone test or part of the Next Start Resource Test.

(iii)	If a physical test is performed, the Black Start Resource must remain stable (in both voltage and frequency) and controlling voltage for thirty (30) minutes.

(iv)	If a physical test is performed, this test may be performed together with the Basic Starting Test, Line-Energizing Test, and Load-Carrying Test in one thirty (30) minute interval.

(v)	Qualification under the Next Start Resource Test is valid until a new next start unit is selected.

- ERCOT shall decertify a Black Start Resource for the calendar year as described in Section 7 of the “Standard Form Black Start Agreement” if the Black Start Resource fails to perform successfully during an actual ERCOT System black out event and the Black Start Resource has been declared available, as defined in Section 9B(1) of the “Standard Form Black Start Agreement.”