## Sheet1
TRANSMISSION LOSS FACTORS for 2006 as of 12/20/05
Data from Seasonal SSWG Base Cases Updated with updates received by 9/09/05
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN NOIE INTERNAL TOTAL |  |  |  |  | CPS NOIE INTERNAL TOTAL |  |  |  |  | COG NOIE INTERNAL TOTAL |  |  |  |  | GEUS NOIE INTERNAL TOTAL |  |  |  |  | COD NOIE INTERNAL TOTAL |  |  |  |  | PUB NOIE INTERNAL TOTAL |  |  |  |  | BTU NOIE INTERNAL TOTAL |  |  |  |  | COCS NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 06SPG1 | 60523.5 | 59241.7 | 1188.8 | 1281.71 | 954 | 1953 | 36.32 | 38.25 | 1037.25 | 2912 | 3942.5 | 21.22 | 25.88 | 1056.38 | 197.5 | 405.2 | 5.05 | 5.05 | 212.75 | 87 | 74.3 | 0.34 | 0.76 | -11.94 | 0 | 261.1 | 1.09 | 1.09 | 262.19 | 57 | 230 | 0.41 | 0.41 | 173.41 | 103 | 250.2 | 2.24 | 2.33 | 149.53 | 0 | 120.8 | 0.07 | 0.07 | 120.87
Spring Off Peak | 06SPG2 | 38400.5 | 37822.9 | 529.19 | 577.5 | 268 | 1178 | 17.06 | 17.52 | 927.52 | 1024 | 2087.5 | 6.85 | 8.39 | 1071.89 | 33.5 | 135.1 | 0.94 | 0.94 | 102.54 | 87 | 30.7 | 0.09 | 0.51 | -55.79 | 0 | 80.8 | 0.26 | 0.26 | 81.06 | 77.8 | 150 | 0.28 | 0.27 | 72.47 | 48.3 | 206.2 | 1.77 | 1.86 | 159.76 | 0 | 58 | 0.06 | 0.06 | 58.06
Summer On Peak | 06SUM1 | 71652.6 | 70145.4 | 1388.38 | 1507.26 | 1316 | 2309 | 44.32 | 47.04 | 1040.04 | 3510 | 4499.7 | 27.93 | 33.78 | 1023.48 | 441.5 | 519.7 | 7.52 | 7.51 | 85.71 | 87 | 104.1 | 0.66 | 1.09 | 18.19 | 0 | 290.2 | 1.36 | 1.35 | 291.55 | 111.8 | 281 | 0.71 | 0.71 | 169.91 | 286.9 | 368.2 | 2.72 | 2.77 | 84.07 | 0 | 179.5 | 0.08 | 0.08 | 179.58
Summer Off Peak | 06SUM2 | 42524.6 | 41809.4 | 658.07 | 715.19 | 276 | 1300 | 15.92 | 16.41 | 1040.41 | 1265 | 2294.3 | 8.7 | 10.42 | 1039.72 | 73.2 | 174.1 | 2.25 | 2.25 | 103.15 | 87 | 31.4 | 0.09 | 0.52 | -55.08 | 0 | 147.9 | 0.39 | 0.39 | 148.29 | 87.7 | 173 | 0.33 | 0.34 | 85.64 | 48 | 191.4 | 1.39 | 1.46 | 144.86 | 0 | 84.7 | 0.05 | 0.05 | 84.75
Fall On Peak | 06FAL1 | 57643.7 | 56446.3 | 1110.62 | 1197.44 | 854 | 1804 | 29.58 | 31.09 | 981.09 | 3215 | 3719.8 | 22.47 | 27.59 | 532.39 | 182 | 389.5 | 3.95 | 3.95 | 211.45 | 87 | 89.2 | 0.48 | 0.91 | 3.11 | 0 | 234.4 | 0.82 | 0.82 | 235.22 | 56 | 236.8 | 0.47 | 0.47 | 181.27 | 103 | 353.5 | 3.35 | 3.44 | 253.94 | 0 | 157.1 | 0.15 | 0.15 | 157.25
Fall Off Peak | 06FAL2 | 36498.6 | 35942.1 | 503.94 | 556.43 | 139 | 1085 | 9.99 | 10.21 | 956.21 | 1555.4 | 2082.2 | 8.04 | 10.22 | 537.02 | 31.5 | 133 | 0.82 | 0.82 | 102.32 | 87 | 30.7 | 0.09 | 0.51 | -55.79 | 0 | 98.5 | 0.25 | 0.24 | 98.74 | 0 | 130 | 0.21 | 0.21 | 130.21 | 48 | 165.7 | 1.28 | 1.35 | 119.05 | 0 | 41.8 | 0.03 | 0.03 | 41.83
Winter On Peak | 07WIN1 | 56473.9 | 55257.1 | 1132.04 | 1216.78 | 656 | 1680 | 32.81 | 34.12 | 1058.12 | 1917 | 2944.4 | 19.18 | 22.46 | 1049.86 | 193.9 | 401.4 | 4.51 | 4.51 | 212.01 | 87 | 71.7 | 0.32 | 0.74 | -14.56 | 0 | 179.8 | 0.73 | 0.73 | 180.53 | 54 | 228 | 0.43 | 0.44 | 174.44 | 143 | 274 | 2.23 | 2.32 | 133.32 | 0 | 113.5 | 0.09 | 0.09 | 113.59
Winter Off Peak | 07WIN2 | 40381.7 | 39660.4 | 659.9 | 721.35 | 97 | 933 | 17.19 | 17.33 | 853.33 | 1052 | 2083.3 | 8.69 | 10.24 | 1041.54 | 36.2 | 142.2 | 0.93 | 0.93 | 106.93 | 87 | 38.9 | 0.12 | 0.54 | -47.56 | 0 | 91.8 | 0.28 | 0.28 | 92.08 | 0 | 155 | 0.32 | 0.32 | 155.32 | 53 | 103.3 | 1.23 | 1.3 | 51.6 | 0 | 76.2 | 0.04 | 0.04 | 76.24
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | PNM-TNMP Self Serve MW | BTU Self Serve MW | TXU ED Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 06SPG1 | 2839.5 | 1352.07 | 540 | 23 | 363.8 | 0 | 5118.37 |  | 7237.1 | 3000.44 | 4236.66 | 66.74 | 06SPG1
Spring Off Peak | 06SPG2 | 2839.5 | 1352.07 | 540 | 23 | 363.8 | 0 | 5118.37 |  | 3926.3 | 2417.51 | 1508.79 | 27.31 | 06SPG2
Summer On Peak | 06SUM1 | 2839.5 | 1352.07 | 540 | 18 | 363.8 | 25 | 5138.37 |  | 8551.4 | 2892.53 | 5658.87 | 85.3 | 06SUM1
Summer Off Peak | 06SUM2 | 2839.5 | 1352.07 | 540 | 18 | 363.8 | 0 | 5113.37 |  | 4396.8 | 2591.74 | 1805.06 | 29.12 | 06SUM2
Fall On Peak | 06FAL1 | 2839.5 | 1352.07 | 540 | 23 | 363.8 | 0 | 5118.37 |  | 6984.3 | 2555.72 | 4428.58 | 61.27 | 06FAL1
Fall Off Peak | 06FAL2 | 2839.5 | 1352.07 | 540 | 23 | 363.8 | 0 | 5118.37 |  | 3766.9 | 1929.59 | 1837.31 | 20.71 | 06FAL2
Winter On Peak | 07WIN1 | 2839.5 | 1352.07 | 540 | 23 | 363.8 | 0 | 5118.37 |  | 5892.8 | 2907.31 | 2985.49 | 60.3 | 07WIN1
Winter Off Peak | 07WIN2 | 2839.5 | 1352.07 | 540 | 15 | 363.8 | 0 | 5110.37 |  | 3623.7 | 2329.48 | 1294.22 | 28.8 | 07WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | PUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 55405.13 | 33282.13 | 2.146% | 1.59% |  | 1953 | 1178 | 1.826% | 1.428% |  | 3942.5 | 2087.5 | 0.5354% | 0.3271% |  | 405.2 | 135.1 | 1.231% | 0.691% |  | 74.3 | 30.7 | 0.4555% | 0.2923% |  | 261.1 | 80.8 | 0.4157% | 0.3208% |  | 230 | 150 | 0.1779% | 0.1863% |  | 250.2 | 206.2 | 0.8873% | 0.8511% |  | 120.8 | 58 | 0.05791% | 0.1033%
SUMMER | 66514.23 | 37411.23 | 2.087% | 1.759% |  | 2309 | 1300 | 1.883% | 1.21% |  | 4499.7 | 2294.3 | 0.6169% | 0.3778% |  | 519.7 | 174.1 | 1.426% | 1.276% |  | 104.1 | 31.4 | 0.63% | 0.2858% |  | 290.2 | 147.9 | 0.4665% | 0.263% |  | 281 | 173 | 0.252% | 0.1904% |  | 368.2 | 191.4 | 0.7333% | 0.721% |  | 179.5 | 84.7 | 0.04455% | 0.059%
FALL | 52525.33 | 31380.23 | 2.114% | 1.606% |  | 1804 | 1085 | 1.613% | 0.9123% |  | 3719.8 | 2082.2 | 0.6004% | 0.3846% |  | 389.5 | 133 | 1.004% | 0.6128% |  | 89.2 | 30.7 | 0.5352% | 0.2923% |  | 234.4 | 98.5 | 0.3486% | 0.2532% |  | 236.8 | 130 | 0.1981% | 0.1613% |  | 353.5 | 165.7 | 0.9388% | 0.7666% |  | 157.1 | 41.8 | 0.09539% | 0.07172%
WINTER | 51355.53 | 35271.33 | 2.204% | 1.871% |  | 1680 | 933 | 1.916% | 1.809% |  | 2944.4 | 2083.3 | 0.6472% | 0.4154% |  | 401.4 | 142.2 | 1.111% | 0.6498% |  | 71.7 | 38.9 | 0.4443% | 0.3075% |  | 179.8 | 91.8 | 0.4044% | 0.3041% |  | 228 | 155 | 0.1882% | 0.206% |  | 274 | 103.3 | 0.8073% | 1.177% |  | 113.5 | 76.2 | 0.07923% | 0.05247%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  | For Testing Only |  |  | AEN NOIE INTERNAL |  | For Testing Only |  |  | CPS NOIE INTERNAL |  | For Testing Only |  |  | COG NOIE INTERNAL |  | For Testing Only |  |  | GEUS NOIE INTERNAL |  | For Testing Only |  |  | COD NOIE INTERNAL |  | For Testing Only |  |  | PUB NOIE INTERNAL |  | For Testing Only |  |  | BTU NOIE INTERNAL |  | For Testing Only |  |  | COCS NOIE INTERNAL |  | For Testing Only
| SSC | SIC | 42555.9 |  |  | SSC | SIC | 2022.1 |  |  | SSC | SIC | 2920.1 |  |  | SSC | SIC | 381.1 |  |  | SSC | SIC | 77.1 |  |  | SSC | SIC | 252 |  |  | SSC | SIC | 204 |  |  | SSC | SIC | 279 |  |  | SSC | SIC | 108
SPRING | 2.5116e-05 | 0.7541 | 1.8229 |  |  | 0.00051381 | 0.82227 | 1.8613 |  |  | 0.00011228 | 0.092679 | 0.42056 |  |  | 0.0019992 | 0.42088 | 1.1828 |  |  | 0.0037435 | 0.17738 | 0.466 |  |  | 0.00052678 | 0.27819 | 0.41094 |  |  | -0.00010469 | 0.20202 | 0.18067 |  |  | 0.00082398 | 0.68118 | 0.91107 |  |  | -0.00072337 | 0.1453 | 0.067173
SUMMER | 1.1282e-05 | 1.337 | 1.8171 |  |  | 0.00066749 | 0.34206 | 1.6918 |  |  | 0.00010842 | 0.12902 | 0.44562 |  |  | 0.00043541 | 1.2001 | 1.366 |  |  | 0.0047346 | 0.13714 | 0.50218 |  |  | 0.0014298 | 0.051533 | 0.41184 |  |  | 0.00057078 | 0.091644 | 0.20808 |  |  | 6.9683e-05 | 0.70765 | 0.7271 |  |  | -0.00015241 | 0.071906 | 0.055446
FALL | 2.405e-05 | 0.85123 | 1.8747 |  |  | 0.00097483 | -0.14535 | 1.8258 |  |  | 0.00013177 | 0.11027 | 0.49506 |  |  | 0.0015251 | 0.40993 | 0.99113 |  |  | 0.0041527 | 0.16481 | 0.48499 |  |  | 0.00070232 | 0.18399 | 0.36097 |  |  | 0.00034465 | 0.11647 | 0.18678 |  |  | 0.00091699 | 0.61461 | 0.87045 |  |  | 0.0002053 | 0.063137 | 0.085309
WINTER | 2.0728e-05 | 1.1398 | 2.0219 |  |  | 0.00014251 | 1.6762 | 1.9643 |  |  | 0.00026919 | -0.1454 | 0.64065 |  |  | 0.0017798 | 0.39667 | 1.075 |  |  | 0.0041703 | 0.14531 | 0.46684 |  |  | 0.0011396 | 0.19947 | 0.48664 |  |  | -0.00024363 | 0.24379 | 0.19409 |  |  | -0.002164 | 1.4002 | 0.79648 |  |  | 0.0007176 | -0.0022151 | 0.075286