## Slide 1
CREZ Study Update
ERCOT TAC
11/2/2006

## Slide 2: 2005 Legislative Requirements
Section 39.904
(g) The (Public Utility) commission, after
consultation with each appropriate
independent organization, electric
reliability council, or regional
transmission organization:
(1) shall designate competitive renewable energy zones throughout this state in areas in which renewable energy resources and suitable land areas are sufficient to develop generating capacity from renewable energy technologies;
(2) shall develop a plan to construct transmission capacity necessary to deliver to electric customers, in a manner that is most beneficial and cost-effective to the customers, the electric output from renewable energy technologies in the competitive renewable energy zones

## Slide 3: ERCOT Study Process and Timeline
J | F | M | A | M | J | J | A | S | O | N | D
Reports/
Approvals
Transmission Studies
Wind Ancillary Services Study
CREZ Rule Development
CREZ Determination
ERCOT
PUCT
Stakeholder Input on CREZs
Wind Potential/Characteristics Study
1Q
2007

## Slide 4: Potential Wind Resource
10600
8300
12000
9600
7900
6900
6000
6200
4700
2900
4600
3000
2200
2700
ERCOT contracted with leading wind consultant AWS Truewind to identify areas with best wind resource potential
AWS identified highest CF 100MW sites and clustered into 25 areas
Identified 4000MW of highest CF sites in each area (shown on map)
  Approximate wind capacity potential(in MW) with >35% capacity factor in each area is shown

## Slide 5: Wind Data
AWS used complex meteorological and terrain model that provided localized prediction of wind patterns and resulting wind power output each site
Typical generation output for each site is provided as a time series of 8,784 hourly data points (one leap-year of data).

## Slide 6: Current Wind Development
2,508MW In Service
16,523MW In Interconnection Process
RPG initiated study of transmission upgrades needed if nearly 5000MW is in-service by EOY 2007
  ~3250MW existing and signed IAs
  ~1600MW proxy for additional IAs in 2007

## Slide 7: 5000MW Wind Upgrades
Developed plan to relieve most curtailment associated with ~5000MW wind assumption (based on steady state analysis)
  Includes opening lines, phase shifters, some line/auto upgrades, and a new 345kV station
  See Update #4 under 2007 5-Year Plan folder on Planning website for details
Dynamic study is underway, but not yet complete

## Slide 8: CREZ Analytical Process
Base Case is the 2009 Case from the 5-Year Plan
  Latest Validated Case when CREZ Analysis Process Began
  Contains 4,850 MW of Installed Wind Capacity
Overall Strategy – to develop incremental transmission solutions that are part of an overall design
  No large steps and no regrets
We evaluated constraints on 69 kV and 138 kV lines, but focused on 345 kV (in some cases 765 kV) solutions

## Slide 9: Other Considerations/Caveats
Transmission solutions presented here are the result of extensive what-if analyses, followed by iterations (and iterations) of economic modeling and power-flow studies
  Over 60 different configurations evaluated for the McCamey area alone
Due to responsive reserves on the system, we limited the flow on radial lines to a maximum of 1,500 MW
Transmission studies were conducted primarily using thermal (DC) analysis
Other system considerations that will need to be addressed
  Voltage Stability
  Dynamic Stability
  Ancillary Services

## Slide 10: Network Upgrades
From the perspective of network upgrade needs, there are generally three sets of CREZs
  Coastal (Area 24)
  Mc Camey Area (Areas 5&6)
  Abilene Area (Areas 9,10,12 &14)
  Panhandle (Areas 2 & 4)
Will show a few options from each area as examples

## Slide 11: Coastal Zone (CREZ 24): 1,000 MW Solution
Cost: $15M
System Fuel Savings: $140M

## Slide 12: Coastal Zone (CREZ 24): 3,000 MW Solution
Cost: $320M
System Fuel Savings: $390M

## Slide 13: McCamey Area (CREZ 5 and 6): Wind Resources

## Slide 14: McCamey Area (CREZ 5 and 6): 1,500 MW Solution
Cost: $365M
System Fuel Savings: $200M

## Slide 15: Wind Curtailment Analysis

## Slide 16: McCamey Area (CREZ 5 and 6): 4,000 MW Solution
Cost: $850M
System Fuel Savings: $520M

## Slide 17: Central Western Texas (CREZ 9, 10, 12, 14): 1400 MW
Total Capital Cost: $350M
Annual System Fuel Savings: $215M/yr

## Slide 18: Panhandle (CREZ 2 and 4): 1,800 MW
Total Capital Cost: $645M (Zone 2)
Annual System Fuel Savings: $260M/yr

## Slide 19: Next Steps
Presentations from 10/30 RPG meeting available under RPG Combined Interest folder at http://oldercot.ercot.com/tmaps/login.cfm
Comments due by noon 11/6
Some additional analysis will be performed based on RPG comments and to evaluate other combinations
Detailed report due to PUCT by 12/1