## ERCOT Operations Report

## ROS & OWG

## October 2006

Frequency control   59.9 > F > 60.1

| Disturbance Data |  |  |
| --- | --- | --- |
| Time | Frequency |  |
| 10/3/06 17:28 | 59.832 | Units trip. 1223MW lost |
| 10/10/06 0:19 | 59.832 | Unit trip. 600MW lost |
| 10/21/06 0:11 | 60.102 | Unit AGC problem |
| 10/23/06 22:09 | 60.105 | Two QSEs reported units responding with slow ramp rates. |
| 10/25/06 15:21 | 59.884 | Unit trip. 571MW lost |
| 10/27/06 0:32 | 59.894 | Unit trip. 376MW lost |
| 10/29/06 15:20 | 59.761 | Unit trip. 920MW lost |

Deployed Responsive (13) (Reported Above)

10/3/06 17:28

10/9/06 22:04

10/10/06 0:19

10/13/06 21:59

10/14/06 21:59

10/22/06 19:00

10/23/06 23:04

10/25/06 15:21

10/27/06 0:32

10/27/06 6:09

10/29/06 15:20

10/30/06 6:25

10/31/06 6:07

Day-Ahead RMR and OOMC Capacity Purchases

| Historical Totals | Oct-05 | Sep-06 | Oct-06 |
| --- | --- | --- | --- |
| Austin | 0 | 0 | 3 |
| Bryan Area | 54 | 14 | 8 |
| Corpus | 31 | 6 | 20 |
| DFW | 42 | 19 | 16 |
| E RIO | 115 | 5 | 10 |
| Houston | 41 | 2 | 0 |
| Laredo | 52 | 90 | 80 |
| North | 6 | 0 | 2 |
| Northeast | N/A | 0 | 13 |
| San Antonio | 8 | 0 | 0 |
| South | 14 | 0 | 0 |
| W RIO | 36 | 65 | 97 |
| Western | 7 | 8 | 6 |
| Total | 406 | 209 | 255 |

| Oct 06 Data in detail | RMR | OOMC | Total |
| --- | --- | --- | --- |
| Austin | 0 | 3 | 3 |
| Bryan Area | 8 | 0 | 8 |
| Corpus | 0 | 20 | 20 |
| DFW | 0 | 16 | 16 |
| E RIO | 0 | 10 | 10 |
| Houston | 0 | 0 | 0 |
| Laredo | 80 | 0 | 80 |
| North | 0 | 2 | 2 |
| Northeast | 0 | 13 | 13 |
| San Antonio | 0 | 0 | 0 |
| South | 0 | 0 | 0 |
| W RIO | 0 | 97 | 97 |
| Western | 0 | 6 | 6 |
| Total | 88 | 167 | 255 |

OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingencies | Overload Elements | Days |
| --- | --- | --- |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345kV | Lake Creek - Temple Pecan Creek 138kV | 18 |
| Marion - Zorn & - Clear Springs 345kV | Seguin - Seguin West 138kV | 13 |
| Trinidad - Stryker Creek & - Enterprise 345kV | Athens Tap - Elkton 138kV | 8 |
| Zorn - Lytton Spring & - Austrop 345kV | Canyon - Rohr 138kV | 7 |
| Hamilton Road - Sonora 138kV | Ft. Lancaster - Illinois 69kV | 6 |
| Odessa EHV 345/138kV Auto | Odessa EHV Switch 345/138kV Auto | 5 |
| Calaveras - Skyline & Walzem Road 138kV | Fern - Ball Park 138kV | 3 |
| Collin - Anna Switch 345kV | Anna Switch 345/138kV Auto | 3 |
| Menard - Gillespie 138kV | Menard 138/69kV Auto | 3 |
| STP - Skyline & - Whitepoint 345kV | Blessing - Lolita 138kV | 3 |
| Calaveras - Laredo Street 138kV | Calaveras - Ball Park 138kV | 2 |
| Hill Country - Marion & - STP 345kV | Marion - Skyline 345kV | 2 |
| Jack County - Reno 138kV | Rhome - decatur 138kV | 2 |
| Midland East - Odessa EHV Switch 345kV | Odessa Switch - Moss Switch 138kV | 2 |
| Monticello - Allen Sw & Sulphur Springs - Royse 345kV | Commerce Switch - Wolf City 138kV | 2 |
| Asherton - West Batesville 138kV | Derby - Pearsal 69kV | 1 |
| Denton Steam 138/68kV Auto | North Denton 138/69kV Auto | 1 |
| Double Gibbons Creek - Twin Oak 345kV | Robertson - Watson Chapel 138kV | 1 |
| Double Monticello - Farmersville 345kV | Monticello - Sulphur Springs Switch 345kV | 1 |
| Hill Country - Helotes 138kV | Medical Center - Hamilton Wolfe Station 138kV | 1 |
| Lon Hill - Coleto Creek 345kV | Kennedy Switch - Kennedy Sub 69kV | 1 |
| Marion - Hill Country & Skyline 345kV | Marion - San Miguel 345kV | 1 |
| Military Highway - La Palma 138kV | La Palma - Cavazos 69kV | 1 |
| Parkdale - Prairie Creek Switch 138kV | Prairie Creek - Prairie Creek Switch 138kV | 1 |
| Sandow - Temple Switch 138kV | Sandow 345/138kV Auto | 1 |
| South Channel - Jefferson 138kV | Jefferson - Crown 138kV | 1 |
| Temple Switch - Bell County 138kV | Seaton - Barclay 69kV | 1 |

Zonal OC1’s

| CSC | Days |
| --- | --- |
| North - Houston | 12 |
| South - Houston | 10 |
| South - North | 3 |
| Northeast - North | 3 |
| West - North | 1 |
| North - West | 0 |

New RAPs

- None

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 10/27/2006 | Transmission & Security Desk - V3R77 | 299 |
| 10/17/2006 | Frequency Control Desk - V3R34 | 298 |
| 10/12/2006 | Day Ahead Desk - V3R28 | 297 |
| 10/12/2006 | Transmission & Security Desk - V3R76 | 296 |
| 10/12/2006 | Frequency Control Desk - V3R43 | 295 |
| 10/06/2006 | Day Ahead Desk - V3R27 | 294 |

Blackout/Load Shed incidences

10/03/2006, Gibbons Creek substation was forced out. Generation units in this area also tripped with 1,223MW lost. 339 MW of load in Bryan/College Station area was also shed.

Major system voltage problems

None

Voltage Instructions

None

Major Computer Problems, Enhancements & Fixes

10/24/2006, 02:00 balancing energy deployments held for 02:15 due to computer problem.

Two database loads.

Communication

None.

ERCOT peak (Unofficial)

10/02/2006	15:57	52088MW

Other

None.

OCN, Advisory, Alerts, and Emergency Notices

| Date | Start | End | Subject | Details |
| --- | --- | --- | --- | --- |
| 10/1/2006 | 19:24 | 21:00 |  | Controlling to real time contingency analysis studies on the North to Houston Zonal OC1. |
| 10/3/2006 | 17:28 | 24:00 |  | There were several forced outages at the College Station area. |
| 10/5/2006 | 13:01 | 18:00 | OCN | Adjusted Responsive Reserve less than 3300mw. |
| 10/5/2006 | 16:14 | 18:00 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000mw. |
| 10/6/2006 | 13:00 | 18:23 | OCN | Adjusted Responsive Reserve less than 3300mw. |
| 10/6/2006 | 14:15 | 18:23 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000mw. |
| 10/7/2006 | 15:00 | 16:00 | Alert | Loss of Sandow - Temple Switch 138 kV line overloads Sandow 345/138 kV Autotransformer above first contingency limits. |
| 10/8/2006 | 15:00 | 19:00 | OCN | Adjusted Responsive Reserve less than 3300MW but greater than 3000MW. |
| 10/8/2006 | 15:55 | 18:30 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000MW but greater than 2500MW. |
| 10/9/2006 | 10:10 | 20:30 | OCN | Adjusted Responsive Reserve below 3300MW. |
| 10/9/2006 | 16:00 | 18:05 | Alert | Loss of Pawnee to San Miguel 345kV overloads Pleasanton 138/69 kV Auto. |
| 10/9/2006 | 16:20 | 20:30 | Advisory | Advisory - Adjusted Responsive Reserve below 3000MW. |
| 10/9/2006 | 22:04 | 22:07 |  | Deployed 267 MW of Responsive Reserve Service on Frequency less than 59.91, large amount of schedule changes, slow responding units. |
| 10/10/2006 | 0:19 | 0:22 |  | ERCOT Frequency down to 59.832 Hz, XXXX tripped while importing 600 MW, Deployed 594 MW of Responsive Reserve Service ERCOT load 30,750. |
| 10/10/2006 | 1:05 | 04:30 | OCN | Adjusted Responsive Reserve below 3300 MW. |
| 10/10/2006 | 8:50 | 17:07 | Alert | Loss of San Miguel "B" 345/138 kV Autotransformer overloads Pleasanton 138/69 kV Autotransformer. |
| 10/10/2006 | 9:45 | 12:45 | OCN | Adjusted Responsive Reserve below 3300 MW. |
| 10/10/2006 | 10:50 | 17:42 | Alert | Loss of San Miguel 138/69 kV Autotransformer overloads Derby - Pearsall 69 kV. |
| 10/10/2006 | 12:00 | 16:45 | OCN | Wet weather across the state. |
| 10/10/2006 | 15:04 | 23:45 | Transmission mergency | Forced outages XXXX. Voltage Collapse. |
| 10/11/2006 | 16:58 | 18:00 | OCN | Adjusted Responsive Reserve less than 3300mw. |
| 10/12/2006 | 17:30 | 20:40 | Alert | Loss of Hill Country - Marion & STP 345kV overloads Marion -Skyline 345kV above first contingency limits. |
| 10/12/2006 | 19:25 | 21:05 | Alert | Loss of Dilley Switch - North Laredo 138kV overloads North Laredo - Asherton 138kV above first contingency limits. |
| 10/13/2006 | 06::45 | 8:05 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 10/13/2006 | 6:58 | 7:40 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 10/13/2006 | 7:15 | 7:40 | Alert | Adjusted Responsive Reserve less than 2500 MW |
| 10/13/2006 | 10:15 | 10:52 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 10/13/2006 | 21:59 | 22:02 |  | Frequency spiked to 59.917Hz due to the 22:15 interval generation change. 270 MW of Responsive Reserve Service deployed, ERCOT load 30,540. |
| 10/14/2006 | 22:00 | 22:03 |  | Frequency spiked to 59.903Hz due to 22:15 interval generation change. 278MW of Responsive Reserve Service deployed, ERCOT load 31,745. |
| 10/15/2006 | 15:10 | 24:00 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 10/15/2006 | 17:30 | 21:00 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 10/16/2006 | 0:15 | 0:45 | OCN | Adjusted Responsive Reserve less than 3300 MW (continuance from Sunday 10/15/06) |
| 10/16/2006 | 7:05 | 10:35 | Alert | Adjusted Responsive Reserve less than 2500 MW |
| 10/16/2006 | 6:30 | 11:00 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 10/16/2006 | 6:35 | 10:35 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 10/16/2006 | 16:30 | 21:45 | Alert | Contingency loss of Menard - Gillespie 138kV overloads Menard 138/69kV autotransformer beyond first contingency limits. |
| 10/16/2006 | 16:30 | 21:45 | Alert | Loss of Temple Pecan Creek - Tradinghouse and Temple Switch - Lake Creek 345KV overloads Temple Pecan Creek - Lake Creek 138kV beyond first contingency limits. |
| 10/16/2006 | 16:30 | 21:45 | Alert | Loss of the Marion - Zorn and Marion - Clear Springs 345KV overloads the Seguin - Seguin West 138kV beyond first contingency limits. |
| 10/17/2006 | 7:29 | 22:30 | Transmission Emergency | Loss of the Asherton to Escondido overloading the Uvalde to Hamilton. |
| 10/17/2006 | 13:17 | 18:30 | OCN | Adjusted Responsive Reserve less than 3300 |
| 10/17/2006 | 13:17 | 17:00 | OCN | Capacity shortage for hours ending 1700 and 1800. |
| 10/17/2006 | 13:24 | 17:45 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 10/17/2006 | 13:24 | 17:00 | OCN | Balancing energy bid shortage for hours ending 1600 through 2000. |
| 10/17/2006 | 14:02 | 24:00 | Transmission Emergency | Post contingency voltage collapse in the Valley with the loss of the Lon Hill - North Edinburg 345KV line. |
| 10/18/2006 | 0:15 | 24:00 | Transmission Emergency | Post contingency voltage collapse in the Valley with the loss of the Lon Hill - North Edinburg 345KV line. |
| 10/18/2006 | 6:45 | 23:20 | Transmission Emergency | Loss of the Asherton to Escondido overloading the Uvalde to Asphalt Mines. |
| 10/18/2006 | 0:15 | 24:00 | Transmission Emergency | Base case overload of Barney Davis-Nelson Sharpe 138kV line and Kennedy Switch-Kennedy 69kV line due to loss of Lon Hill-Nelson Sharpe 345kV line. |
| 10/18/2006 | 12:18 | 16:00 | OCN | Shortage of up balancing bids for hours ending 1500 through 1800. |
| 10/18/2006 | 14:30 | 22:00 | Alert | Post contingency overload on the Evant - Adamsville 138KV line of 123% of the 95MVA rating with the loss of the Temple Pecan Creek - Tradinghouse and Temple Switch - Lake Creek 345KV lines. |
| 10/18/2006 | 14:00 | 17:40 | Alert | Post contingency loss of 345kV double Circuit Marion-Zorn and Marion-Clear Springs overloads the Seguin-Seguin West 138kV line to 102% of 220MVA rating. |
| 10/18/2006 | 7:20 | 23:20 | Alert | Post contingency overload on the South McAllen - Las Milpas 138KV line with the loss of the North Edinburg - Rio Hondo 345KV line. |
| 10/18/2006 | 13:22 | 18:15 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 10/18/2006 | 14:00 | 23:20 | Alert | Post contingency overload of Menard 138/69KV Auto-transformer with loss of Menard-Gillespie 138kV line. |
| 10/18/2006 | 14:00 | 17:40 | Alert | Post contingency overload of Marion-San Miguel 345kV line with loss of 345kV double Circuit Marion-Skyline and Marion-Hill Country. |
| 10/19/2006 | 0:15 | 17:20 | Transmission Emergency | Post contingency voltage collapse in the Valley with the loss of the Lon Hill - North Edinburg 345KV line. |
| 10/19/2006 | 0:15 | 17:20 | Transmission Emergency | Base case overload of Barney Davis-Nelson Sharpe 138kV line and Kennedy Switch-Kennedy 69kV line due to loss of Lon Hill-Nelson Sharpe 345kV line. |
| 10/19/2006 | 7:00 | 24:00 | Transmission Emergency | Transmission outage causing the post contingency loss XXXX - Escondido 138KV line overloads the Uvalde - Asphalt 138KV line |
| 10/19/2006 | 7:00 | 17:20 | Alert | Post contingency overload on the South McAllen - Las Milpas 138KV line with the loss of the North Edinburg - Rio Hondo 345KV line. |
| 10/19/2006 | 10:00 | 24:00 | Emergency request | 30 MW schedule from CFE on DC_EGPS to ERCOT due to outage in the Hamilton Rd to Cauthorn 138KV line. |
| 10/20/2006 | 6:45 | 23:00 | Transmission Emergency | Loss of Lon Hill - North Edinburg may cause voltage collapse in the Rio Grande Valley. |
| 10/20/2006 | 7:30 | 23:00 | Transmission Emergency | Loss of Asherton - Escondido 138kV overloads Uvalde - Asphalt Mines beyond first contingency limits. |
| 10/20/2006 | 8:00 | 12:16 | Alert | Loss of Lytton Springs - Zorn and Austrop - Zorn 345kV overloads Canyon - Rohr 138kV beyond first contingency limits. |
| 10/21/2006 | 6:45 | 16:30 | Alert | Loss of Lon Hill - North Edinburg may cause voltage collapse in the Rio Grande Valley. |
| 10/21/2006 | 6:45 | 11:10 | Transmission Emergency | Loss of Asherton - Escondido 138kV overloads Uvalde - Asphalt Mines 138kV beyond first contingency limits. |
| 10/21/2006 | 13:20 | 15:15 | Alert | Loss of North Edinburg - Rio Hondo 345kV overloads South McAllen - Las Milpas 138kV beyond first contingency limits. |
| 10/24/2006 | 2:00 | 2:15 |  | 02:00 Balancing energy deployments held for 02:15 due to computer problem. |
| 10/25/2006 | 4:00 | 4:45 | Alert | Adjustment Period Replacement Reserve Market opened for hours 08:00 to 24:00. |
| 10/25/2006 | 12:45 | 23:55 | Transmission Emergency | Loss of Lon Hill - North Edinburg may cause voltage collapse in the Rio Grande Valley. |
| 10/25/2006 | 15:21 | 15:27 |  | Frequency spiked to 59.884Hz, XXXX tripped with 571MW. ERCOT load 33,686. 325 MW of Responsive Reserve deployed. |
| 10/25/2006 | 19:03 | 21:00 | Advisory | Advisory - Adjusted Responsive Reserve below 3000MW. |
| 10/26/2006 | 6:43 | 12:03 | Advisory | Advisory - Adjusted Responsive Reserve below 3000MW. |
| 10/26/2006 | 7:07 | 12:03 | Alert | Adjusted Responsive Reserve below 2500MW. |
| 10/26/2006 | 9:43 | 12:52 | Alert | Loss of North Edinburg – Rio Hondo 345kV overloads South McAllen - Las Milpas 138kV past first contingency limits. |
| 10/26/2006 | 10:27 | 22:00 | Transmission Emergency | Loss of Asherton - West Conoco 138kV overloads Sonora - Cauthorn 138kV beyond first contingency limits. |
| 10/26/2006 | 11:04 | 12:49 | Transmission Emergency | Loss of Lon Hill - North Edinburg may cause voltage collapse in the Rio Grande Valley. |
| 10/26/2006 | 14:02 | 20:15 | Advisory | Advisory - Adjusted Responsive Reserve below 3000MW. |
| 10/27/2006 | 0:32 | 0:36 |  | Frequency spiked to 59.894Hz, XXXX tripped with 376MW. ERCOT load 28774. 316MW of Responsive Reserve deployed. |
| 10/29/2006 | 200 | 200 |  | Daylight Saving Time Ends |
| 10/29/2006 | 15:20 | 15:30 |  | Frequency spiked to 59.761Hz due to XXXX tripping with 920MW. ERCOT load 30035. Deployed 729MW of Responsive Reserve Service. |
| 10/29/2006 | 18:00 | 20:00 | Advisory | Advisory - Adjusted Responsive Reserve below 3000 mw. |
| 10/30/2006 | 6:25 |  |  | Deployed 239 MW of Responsive Reserve Service due to low frequency. Frequency low due to Load Pickup, Non Conforming load and slow unit response. |
| 10/31/2006 | 4:00 | 6:30 | Advisory | Advisory - Adjusted Responsive Reserve below 3000 mw. |
| 10/31/2006 | 6:07 |  |  | Deployed 262 MW of Responsive Reserve Service due to low frequency. Frequency low due to Load Pickup and slow unit response. |
| 10/31/2006 | 14:00 | 21:00 | Transmission Emergency | Del Rio Area. Planned Transmission Outage requires a South DC tie Schedule from CFE. |
| 10/31/2006 | 14:00 | 19:36 | Advisory | Advisory - Adjusted Responsive Reserve below 3000 mw. |
| 10/31/2006 | 14:30 | 16:00 | Alert | Forced outage XXXX - the contingency of Perminan Basin-Wink 138 KV line overloads the Perminan Basin 138/69 KV Transformer #2 122% of 72 MVA rating with no market solution. |