## ERCOT Operations Report

## ROS & OWG

## September 2006

Frequency control   59.9 > F > 60.1

| Disturbance Data |  |  |
| --- | --- | --- |
| Time | Frequency |  |
| 9/7/06 23:28 | 59.895 | Unit trip. 200MW lost |
| 9/10/06 13:38 | 59.889 | Unit trip. 335MW lost |
| 9/10/06 17:57 | 59.854 | Unit trip. 630MW lost |
| 9/11/06 10:55 | 59.891 | Unit trip. 330MW lost |
| 9/14/06 19:43 | 59.866 | Unit trip. 640MW lost |
| 9/14/06 21:04 | 60.102 | QSE had large positive SCE |
| 9/28/06 15:08 | 59.732 | Unit trip. 1206MW lost |

Deployed Responsive (13) (Reported Above)

9/1/06 0:02

9/7/06 23:28

9/8/06 21:59

9/10/06 13:38

9/10/06 17:57

9/11/06 10:55

9/14/06 9:07

9/14/06 19:43

9/17/06 22:05

9/20/06 13:24

9/21/06 22:04

9/28/06 15:08

9/28/06 18:35

Day-Ahead RMR and OOMC Capacity Purchases

| Historical Totals | Sep-05 | Aug-06 | Sep-06 |
| --- | --- | --- | --- |
| Austin | 1 | 0 | 0 |
| Bryan Area | 91 | 86 | 14 |
| Corpus | 33 | 0 | 6 |
| DFW | 69 | 4 | 19 |
| E RIO | 96 | 12 | 5 |
| Houston | 2 | 0 | 2 |
| Laredo | 90 | 93 | 90 |
| North | 4 | 0 | 0 |
| Northeast | 2 | 0 | 0 |
| San Antonio | 5 | 0 | 0 |
| South | n/a | 0 | 0 |
| W RIO | 39 | 19 | 65 |
| Western | 4 | 17 | 8 |
| Total | 436 | 231 | 209 |

| Sep 06 Data in detail | RMR | OOMC | Total |
| --- | --- | --- | --- |
| Austin | 0 | 0 | 0 |
| Bryan Area | 12 | 2 | 14 |
| Corpus | 0 | 6 | 6 |
| DFW | 0 | 19 | 19 |
| E RIO | 0 | 5 | 5 |
| Houston | 0 | 2 | 2 |
| Laredo | 90 | 0 | 90 |
| North | 0 | 0 | 0 |
| Northeast | 0 | 0 | 0 |
| San Antonio | 0 | 0 | 0 |
| South | 0 | 0 | 0 |
| W RIO | 0 | 65 | 65 |
| Western | 0 | 8 | 8 |
| Total | 102 | 107 | 209 |

OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| contingency | overload | Days |
| --- | --- | --- |
| Marion - Zorn & - Clear Springs 345kV | Seguin - Seguin West 138kV | 29 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345kV | Lake Creek - Temple Pecan Creek 138kV | 12 |
| STP - Skyline & - Whitepoint 345kV | Blessing - Lolita 138kV | 9 |
| Menard - Gillespie 138kV | Menard 138/69kV Auto | 9 |
| North Edinburg - Rio Hondo 345kV | S. McAllen - Las Milpas 138kV | 8 |
| Odessa EHV 345/138 Auto | Odessa EHV Switch 345/138kV Auto | 8 |
| Enterprise - Stryker Creek 345kV | Nacogdoches 345/138kV Auto | 7 |
| Trinidad - Stryker Creek & - Enterprise 345kV | Athens Tap - Elkton 138kV | 7 |
| Skyline - Marion & - STP 345kV | Marion - Hill Country 345kV | 6 |
| Pawnee - Lon Hill 345kV | Kennedy Switch - Kennedy 69kV | 5 |
| Hill Country - Marion & - STP 345kV | Marion - Skyline 345kV | 5 |
| Zorn - Lytton Spring & - Austrop 345kV | Canyon - Rohr 138kV | 3 |
| Oklaunion - Bowman & - Fisher Road 345kV | Venon - Grayback 69kV | 3 |
| Military Highway 138/69 Auto | Military Hwy - Laredo Road 69kV | 3 |
| STP - Hill country & - Skyline 345kV | Marion - Hill Country 345kV | 3 |
| Airport PUB 138/69 Auto | Loma Alta 138/69 kV Auto | 2 |
| Temple - Bell County 138kV | Seaton - Poage 69kV | 2 |
| Comanche Peak Unit 1 & 2 | Uvalde - Asphalt Mines 138kV | 2 |
| Comanche Peak - De-Cordova & Wolfe Hollow to Rock Creek 345kV | Concord 345/138kV Auto | 2 |
| Austrop - Sandow 345kV | Killeen Clark Road - Copperas Cove 138kV | 2 |
| Sargent Road - Watermill 345kV | Prairie Creek Switch - Prairie Creek 138kV | 2 |
| Garrott - Midtown 138kV (Base Case) |  | 1 |
| Hamilton - Balcones 138kV | Mag. Plant - Northland 138kV | 1 |
| Duke - SE Edinburg 138kV | N. Edinburg - N. McAllen 138kV | 1 |
| Lon Hill - Coleto Creek 345kV | Victoria - Warburton 138kV | 1 |
| Duke - Pharr 138kV | N. Edinburg - MV W. Edinburg 138kV | 1 |
| Dilley Switch - San Miguel 138kV | Derby - Pearsall 69kV | 1 |
| Parkdale - Prairie Creek 138kV | Parkdale - Scyene Road 138kV | 1 |
| San Miguel 138kV Auto | Kennedy - Kennedy Switch 69kV | 1 |
| STP - Hill Country & - Holman 345kV | Blessing - Lolita 138kV | 1 |
| STP Unit 1 & 2 | Big Brown - Jewett 345kV | 1 |
| Watermill - Tricorner & - Trinidad 345kV | Kleberg Tap - Seagoville 138kV | 1 |
| Wolf Hollow - Red Creek 345kV | Concord 345/138kV Auto | 1 |

Zonal OC1’s

| CSC | Days |
| --- | --- |
| North - Houston | 10 |
| South - Houston | 7 |
| North - West | 3 |
| South - North | 2 |
| West - North | 2 |
| Northeast - North | 1 |

New RAPs

- None

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 09/29/2006 | Day Ahead Desk - V3R26 | 293 |
| 09/29/2006 | Frequency Control Desk - V3R42 | 292 |
| 09/29/2006 | Transmission & Security Desk - V3R75 | 291 |
| 09/29/2006 | Operating Period Desk - V2R19 | 290 |
| 09/27/2006 | Operating Period Desk - V2R18 | 289 |
| 09/28/2006 | Frequency Control Desk - VDI-JOU | 288 |
| 09/28/2006 | Transmission & Security Desk - VDI-JOU | 287 |
| 09/28/2006 | Transmission & Security Desk - Western Area Action Plan | 286 |
| 09/13/2006 | Transmission & Security Desk - V3R74 | 285 |
| 09/12/2006 | Transmission & Security Desk V3R73 | 284 |
| 09/12/2006 | Operating Period Desk - V2R17 | 283 |
| 09/12/2006 | Transmission & Security Desk V3R72 | 282 |
| 09/12/2006 | Frequency Control Desk - V3R40 | 281 |

Blackout/Load Shed incidences

None

Major system voltage problems

None

Voltage Instructions

None

Major Computer Problems, Enhancements & Fixes

Three lost intervals

Communication

None.

ERCOT peak (Unofficial)

9/1/2006	16:38 	57674MW

Other

None.

OCN, Advisory, Alerts, and Emergency Notices

| Date | Start | End | Subject | Details |
| --- | --- | --- | --- | --- |
| 9/1/06 | 2:00 | 3:10 | Alert | Adjustment Period Replacement market opened for 09/01/06. |
| 9/1/06 | 12:30 | 17:00 | OCN | Capacity deficit HE 16 and 17 |
| 9/1/06 | 13:40 | 18:00 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 9/1/06 | 14:15 | 17:45 | Advisory | Adjusted Responsive Reserve less than 3000 MW |
| 9/1/06 | 15:20 | 17:45 | Alert | Alert issued due to Adjusted Responsive Reserve is less than 2500 MW |
| 9/6/06 | 14:17 | 18:40 | OCN | OCN - Adjusted Responsive Reserve less than 3300 MW |
| 9/6/06 | 16:06 | 18:40 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 9/6/06 | 20:10 | 20:55 |  | ERCOT Texas Market Link, TML, down. Being investigated |
| 9/7/06 | 9:42 | 9:58 |  | Held Interval Ending 09:45 until 10:15 due to Market Database Load. |
| 9/7/06 | 13:20 | 18:30 | OCN | OCN - Adjusted Responsive Reserve less than 3300 MW |
| 9/7/06 | 13:30 | 16:00 | OCN | OCN Balancing Bid insufficient for Hours Ending 16 and 17 |
| 9/7/06 | 14:40 | 18:30 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000 MW |
| 9/8/06 | 10:30 | 13:09 | OCN | OCN - Capacity shortage for hours 16:00, 17:00 and 18:00 |
| 9/8/06 | 11:00 | 11:45 | Alert | Alert - Adjustment period replacement reserve market opened |
| 9/8/06 | 11:30 | 13:09 | OCN | OCN - shortage of UBES bids for 14:00 and 15:00 |
| 9/8/06 | 13:10 | 14:00 | OCN | OCN - shortage of UBES bids for 16:00 and 17:00 |
| 9/9/06 | 14:49 | 18:40 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300Mw's but greater than 3000Mw's. |
| 9/10/06 | 11:43 | 19:25 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300Mw's but greater than 3000Mw's. |
| 9/10/06 | 12:40 | 19:25 | Advisory | Advisory issued due to Adjusted Responsive Reserve less than 3000Mw's but greater than 2500Mw's. |
| 9/10/06 | 12:53 | 19:25 | OCN | OCN issued due to actual load running 1800 Mw's above forecast. QSE's were requested to review and update resource plans. |
| 9/10/06 | 13:55 | 19:25 | Alert | Alert issued due to Adjusted Responsive Reserve less than 2500Mw's. |
| 9/10/06 | 13:38 | 13:40 |  | Frequency spiked to 59.89hz, XXXX tripped with 335Mw's. ERCOT load 46113. |
| 9/10/06 | 17:57 | 18:00 |  | XXXX tripped with 511mw Freq. went to 59.86hz back to 60hz in 3 min. |
| 9/11/06 | 10:10 | 16:00 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300Mw's but greater than 3000Mw's. |
| 9/11/06 | 11:11 | 16:00 | OCN | OCN issued for a shortage of UBES bids for hours 14:00 thru 18:00. |
| 9/11/06 | 12:00 | 13:30 | OCN | OCN issued for a capacity shortage for hours 16:00 and 17:00. |
| 9/11/06 | 16:25 | 23:39 | Alert | Transmission Alert for loss of Asherton to Escondido overloads Uvalde to Asphalt Mines. |
| 9/12/06 | 13:35 | 18:00 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300 Mw's but greater than 3000 Mw's. |
| 9/12/06 | 14:25 | 18:00 | Advisory | Advisory issued due to Adjusted Responsive Reserve less than 3000 Mw's but greater than 2500 Mw's. |
| 9/13/06 | 15:45 | 18:50 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300 Mw's but greater than 3000 Mw's. |
| 9/13/06 | 16:00 | 16:45 |  | Controlling to real time contingency analysis studies on the South to Houston Zonal OC1. |
| 9/13/06 | 16:10 | 18:50 | Advisory | Advisory issued due to Adjusted Responsive Reserve less than 3000 Mw's but greater than 2500 Mw's. |
| 9/14/06 | 14:50 | 21:30 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300 Mw's but greater than 3000 Mw's. |
| 9/14/06 | 16:00 | 21:30 | Advisory | Advisory issued due to Adjusted Responsive Reserve less than 3000 Mw's but greater than 2500 Mw's. |
| 9/14/06 | 19:43 | 19:45 |  | Frequency spiked to 59.872hz, XXXX tripped with 640 Mw's. ERCOT load 47130. |
| 9/15/06 | 13:08 | 18:00 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300 Mw's but greater than 3000 Mw's. |
| 9/15/06 | 15:09 | 18:00 | Advisory | Advisory issued due to Adjusted Responsive Reserve less than 3000 Mw's but greater than 2500 Mw's. |
| 9/16/06 | 0:25 | 01:25 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300 Mw's but greater than 3000 Mw's. |
| 9/16/06 | 10:32 | 19:30 | OCN | OCN issued due to Adjusted Responsive Reserve less than 3300 Mw's but greater than 3000 Mw's. |
| 9/16/06 | 16:35 | 19:30 | Advisory | Advisory issued due to Adjusted Responsive Reserve less than 3000 Mw's but greater than 2500 Mw's. |
| 9/18/06 | 0:30 | 13:30 | OCN | Weather OCN issued for heavy rains and possible flooding in the Houston area. MIS#18092006003955. |
| 9/19/06 | 14:15 | 14:45 |  | Held IE 1415, resumed with 14:45, SPD loader failed, under investigation |
| 9/19/06 | 15:45 | 18:55 | OCN | OCN issued due to Adjusted Responsive below 3300mw. |
| 9/19/06 | 16:30 | 18:55 | Advisory | Advisory issued due to Adjusted Responsive below 3000mw. |
| 9/22/06 | 11:30 | 12:00 |  | Held interval 11:30 due to MOI failed to send out deployments for 11:45. Resumed at 12:00. Cause under investigation. |
| 9/22/06 | 12:50 | 19:00 | OCN | OCN issued due to Adjusted Responsive Reserve is below 3300 mw. |
| 9/22/06 | 13:30 | 16:30 | Advisory | Advisory issued due to Adjusted Responsive Reserve is below 3000 mw. |
| 9/23/06 | 16:00 | 18:22 | OCN | OCN issued due to Adjusted Responsive Reserve is below 3300 mw. |
| 9/23/06 | 16:00 | 17:15 | Alert | Transmission Alert issued for loss of San Miguel 69kv - San Miguel 138kv overloads Derby - Pearsall 69kv line. |
| 9/26/06 | 15:00 | 19:15 | OCN | OCN issued due to Adjusted Responsive Reserve below 3300 mw. |
| 9/26/06 | 15:05 | 19:15 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 9/27/06 | 9:20 | 10:30 |  | ERCOT performed a local data base load |
| 9/27/06 | 15:15 | 18:45 | OCN | OCN issued due to Adjusted Responsive Reserve below 3300 mw's but greater than 3000 mw's. |
| 9/27/06 | 15:45 | 18:45 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000 mw's but greater than 2500 mw's. |
| 9/27/06 | 14:46 | 14:56 |  | ERCOT performed an emergency local data base load |
| 9/27/06 | 18:00 | 24:00 |  | ERCOT is unable to clear the Replacement Reserve Market by 18:00 for 9-28-06 due to system issues. |
| 9/28/06 | 0:15 | 17:15 |  | ERCOT Replacement Reserve Service Market unavailable due to software issues. |
| 9/28/06 | 15:08 | 15:17 |  | Frequency spiked to 59.732hz, XXXX tripped with 1206mw's. ERCOT load 43317. Responsive Reserve deployed at 59.91 hz. |
| 9/28/06 | 18:36 | 18:46 |  | Responsive Reserve deployed at 59.91 hz due to regulation up depleted. |
| 9/28/06 | 15:32 | 18:15 | Alert | Transmission Alert for loss of San Miguel 69kv - San Miguel 138kv overloads Derby - Pearsall 69 kv. |
| 9/28/06 | 18:30 | 24:00 |  | Northeast - North Zonal limit changed to 1150 mw per ERCOT Engineering. |
| 9/28/06 | 1415 | 18:00 | OCN | OCN issued due to Adjusted Responsive Reserve below 3300 mw's but greater than 3000 mw's. |
| 9/28/06 | 15:30 | 18:00 |  | Advisory issued due to Adjusted Responsive Reserve below 3000 mw's but greater than 2500 mw's. |
| 9/29/06 | 16:20 | 20:00 | OCN | OCN issued due to Adjusted Responsive Reserve below 3300 mw's but greater than 3000 mw's. |
| 9/30/06 | 14:36 | 21:30 | OCN | OCN issued due to ERCOT load running approximately 2000 MW ahead of the current load forecast. |