## ERCOT Operations Report

## ROS & OWG

## August 2006

Frequency control   59.9 > F > 60.1

| Disturbance Data |  |  |
| --- | --- | --- |
| Time | Frequency |  |
| 8/6/2006 16:09 | 59.896 | Unit trip. 510MW lost |
| 8/11/2006 4:43 | 59.815 | Unit trip. 840MW lost |
| 8/11/2006 8:47 | 59.891 | Unit trip. 565MW lost |
| 8/14/2006 22:28 | 59.899 | Unit trip. 450MW lost |
| 8/19/2006 15:27 | 59.849 | Unit trip. 791MW lost |
| 8/24/2006 5:59 | 59.891 | Unit trip. 310MW lost |
| 8/28/2006 0:58 | 59.889 | Unit trip. 500MW lost |
| 8/28/2006 7:57 | 59.889 | Unit trip. 450MW lost |

Deployed Responsive (12) (Reported Above)

08/06/2006 16:09

08/08/2006 06:43

08/11/2006 04:43

08/11/2006 08:47

08/13/2006 18:29

08/14/2006 22:28

08/19/2006 14:01

08/19/2006 15:27

08/24/2006 05:59

08/28/2006 00:58

08/28/2006 07:57

08/31/2006 10:51

Day-Ahead RMR and OOMC Capacity Purchases

| Historical Totals | Aug-05 | Jul-06 | Aug-06 |
| --- | --- | --- | --- |
| Austin | 0 | 0 | 0 |
| Bryan Area | 93 | 80 | 86 |
| Corpus | 33 | 3 | 0 |
| DFW | 75 | 15 | 4 |
| E RIO | 101 | 13 | 12 |
| Houston | 9 | 0 | 0 |
| Laredo | 93 | 93 | 93 |
| North | 8 | 1 | 0 |
| Northeast | 18 | 9 | 0 |
| San Antonio | n/a | 0 | 0 |
| South | n/a | 0 | 0 |
| W RIO | 28 | 32 | 19 |
| Western | 21 | 1 | 17 |
| Total | 479 | 247 | 231 |

| Aug 06 Data in detail | RMR | OOMC | Total |
| --- | --- | --- | --- |
| Austin | 0 | 0 | 0 |
| Bryan Area | 80 | 6 | 86 |
| Corpus | 0 | 0 | 0 |
| DFW | 0 | 4 | 4 |
| E RIO | 0 | 12 | 12 |
| Houston | 0 | 0 | 0 |
| Laredo | 93 | 0 | 93 |
| North | 0 | 0 | 0 |
| Northeast | 0 | 0 | 0 |
| San Antonio | 0 | 0 | 0 |
| South | 0 | 0 | 0 |
| W RIO | 0 | 19 | 19 |
| Western | 0 | 17 | 17 |
| Total | 173 | 58 | 231 |

OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| contingency | overload | Days |
| --- | --- | --- |
| Gibbons Creek - Green Prairie - East 138kV | Watson Chapel - Robertson 138kV | 16 |
| Duke - SE Edinburg 138 kV | North Edinburg - MVEC NW Edinburg 138 kV | 10 |
| Morgan Creek 345/138 kv Auto | Morgan Creek 345/138 kv Auto | 8 |
| ODEHV T2 345/138 kV | ODEHV T1 345/138 kV | 8 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345kV | Nacogdoches 345/138kV auto | 6 |
| Marion - Zorn and Clear Springs 345 kV | Seguin - West Seguin 138 kV | 6 |
| Comanche Peak - DeCordova and Wolf Hollow - Rocky Creek 345kV | Concord 345/138 auto | 5 |
| Lon Hill - Nelson Sharpe 345 kV | Barney Davis - Alazan 138 KV | 5 |
| Lytton Spring - Zorn & Austrop - Zorn 345 kv | Canyon - Rohr 138 kv | 4 |
| Roanoke Sw - Parker Sw & Roanoke Sw - Eagle Mountain SES 345kV | Rhome - Chisolm 138kV | 4 |
| Temple Pecan Creek - Trading House and Temple Switch - Lake Creek 345 kV | Goldthwaite 138/69 kV Auto | 4 |
| Austrop 345/138 kV Auto | Austrop 345/138 kV Auto | 3 |
| Comanche Peak Units 1 and 2 | Uvalde - Asphalt Mines 138 kV | 3 |
| Gibbons Creek - Greens Prairie and East 138 kV | Dansby - Atkins 138 kV | 2 |
| Marion-Clear Springs-Zorn 345kV | Seguin to Seguin West 138kv | 2 |
| Marion-Zorn and Marion-Clear Springs 345kV | Seguin-Geronimo 138kV | 2 |
| Military Highway 138/69 kV Auto | Brownsville - Brownsville Switch 69 kV | 2 |
| Norwood Sw - Cedar Hill Sw - Liggett 345 KV | Norwood Sw - East Levee 138 KV | 2 |
| Sargeant Road - Watermill 345kV | Cedar Hill SW 345/138kV auto | 2 |
| Temple Switch - Bell County Sw 138 Kv | Seaton - Poage 69kV | 2 |
| Cagnon - Calaveras and VH Braunig 345 Kv | Medical Center - Hamilton Wolfe Station 138 kV | 2 |
| Trinidad - Enterprise and Martin Lake - Stryker Creek 345 kV | Herty North Switch - Nacogdoches SE | 2 |
| Asherton - Escondido 138kV | Uvalde - Hamilton 138kV | 1 |
| Brenham - Salem LCRA 138kV | Mill Creek - Gay Hill 138kV | 1 |
| Calaveras - Skyline & Walzem Road 138kV | Westside - Five Points 138kV | 1 |
| Collin 345/138kv Auto | Allen Sw - Custer Rd 138kv | 1 |
| Marion -Zorn & Clear Springs 345kV | Seguin - Seguin West 138 kV | 1 |
| Friend Ranch - Fort Lancaster 138 kv | Fort Lancaster - Illinois 69 kv. | 1 |
| Lake Pauline 138/69 kV Auto | Munday to Benjamin 69 kV | 1 |
| Menard - Gillespie 138KV | Menard 138/69KV Auto | 1 |
| Royse Switch 345/138 kV Auto | Forney Switch - Forney West 138 kV | 1 |
| Sandow unit #4 | Sandow 345/138 kV Auto | 1 |
| STP - Skyline - White -Point 345kV | Blessing - Lolita 138kv | 1 |
| Jefferson to S.Channel 138kv | Jefferson to Crown 138kv | 1 |
| Watermill - Sargent Road 345kV | Watermill 345/138kV Auto | 1 |
| Hill Country 345/138 kV Auto | Medical Center - Hamilton Wolfe Station 138 kV | 1 |
| Morgan Creek 345/138 kV Auto | Morgan Creek 345/138 kV Auto | 1 |
| North Edinburg - Rio Hondo 345 kV | South McAllen - Las Milpas 138 kV | 1 |

Zonal OC1’s

| CSC | Days |
| --- | --- |
| South - Houston | 11 |
| North - West | 10 |
| South - North | 6 |
| North - Houston | 2 |
| West - North | 2 |

New RAPs

- None

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 08/31/2006 | Frequency Control Desk - V3R40 | 280 |
| 08/29/2006 | Operating Period Desk - V2R16 | 279 |
| 08/28/2006 | Shift Supervisor Procedure - V3R29 | 278 |
| 08/14/2006 | Shift Supervisor Desk - V3R28 | 277 |
| 08/08/2006 | FC Desk - Fast Start Emergency Schedules to SPP | 272 |
| 08/02/2006 | Frequency Control Desk - Provide Advance Notice of Diminishing Responsive Reserve | 276 |
| 08/01/2006 | Shift Supervisor - PUC Daily Report | 275 |

Blackout/Load Shed incidences

None

Major system voltage problems

None

Voltage Instructions

None

Major Computer Problems, Enhancements & Fixes

None.

Communication

None.

ERCOT peak (Unofficial)

8/17/	16:43	63,246MW

Other

None.

OCN, Advisory, Alerts, and Emergency Notices

| Date | Start | End | Subject | Details |
| --- | --- | --- | --- | --- |
| 8/1/06 | 14:20 | 22:45 | Alert | Loss of Duke - SE Edinburg 138 kV overloads North Edinburg - MVEC (NW Edinburg) 138 kV. |
| 8/2/06 | 6:20 | 11:00 | Alert | Loss of Sonora - Friend Ranch 138 kV overloads San Angelo Concho - San Angelo Lake Nasworthy 69 kV. |
| 8/2/06 | 12:10 | 22:00 | Alert | Loss of Duke - SE Edinburg 138 kV overloads North Edinburg - MVEC (NW Edinburg) 138 kV. |
| 8/2/06 | 23:00 | 23:30 | Alert | Adjustment Period Replacement market opened for 8/03/06. |
| 8/3/06 | 9:00 | 9:30 | Alert | Adjustment Period Replacement market opened for 8/03/06. |
| 8/4/06 | 14:30 | 17:15 | OCN | Adjusted Responsive Reserve below 3300MW. |
| 8/4/06 | 14:50 | 17:15 | Advisory | Adjusted Responsive Reserve below 3000MW. |
| 8/6/06 | 13:50 | 14:05 | OCN | Adjusted Responsive Reserve is less than 3300MW but greater than 3000MW. |
| 8/6/06 | 14:05 | 16:40 | Advisory | Adjusted Responsive Reserve is less than 3000MW but greater than 2500MW. |
| 8/8/06 | 12:21 | 12:45 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 8/8/06 | 12:45 | 19:00 | Advisory | Advisory - Adjusted Responsive reserve less than 3000 MW |
| 8/9/06 | 12:19 | 15:15 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 8/9/06 | 12:45 | 19:20 | Advisory | Advisory - Adjusted Responsive reserve less than 3000 MW |
| 8/10/06 | 15:28 | 19:00 | OCN | Adjusted Responsive Reserve less than 3300 MW |
| 8/11/06 | 3:56 | 0:00 | Alert | A second market for 8-11-06 for hrs 1200-2400 would be opened |
| 8/11/06 | 15:00 | 17:00 | OCN | Physical Responsive Reserve less than 3300 MW. |
| 8/12/06 | 14:15 | 17:50 | OCN | Physical Responsive Reserve less than 3300 MW. |
| 8/12/06 | 15:25 | 17:50 | Advisory | Advisory - Physical Responsive Reserve less than 3000 MW. |
| 8/13/06 | 15:00 | 16:10 | OCN | Physical Responsive Reserve less than 3300 MW. |
| 8/13/06 | 16:10 | 18:20 | Advisory | Advisory - Physical Responsive Reserve less than 3000 MW. |
| 8/14/06 | 14:35 | 17:15 | OCN | Physical Responsive Reserve less than 3300MW but greater than 3000MW. |
| 8/14/06 | 15:00 | 17:30 | Alert | Loss of La Palma to Rio Hondo 345kV or theLoss of La Palma 345/138kV autotransformer overloads South McAllen to Las Milpas 138kV. |
| 8/15/06 | 9:00 | 9:30 | Alert | Adjustment Period Replacement Market opened for hours 13:00 to 24:00. |
| 8/15/06 | 11:08 | 12:11 | OCN | A shortage of UBES bids for hours 14:00 and 15:00. |
| 8/15/06 | 13:08 | 14:55 | OCN | A shortage of UBES bids for hours 16:00 and 17:00. |
| 8/15/06 | 13:15 | 19:00 | OCN | Physical Responsive Reserve less than 3300MW but greater than 3000MW. |
| 8/15/06 | 15:23 | 19:00 | Advisory | Physical Responsive Reserve less than 3000MW but greater than 2500MW. |
| 8/15/06 | 15:40 | 20:00 | Alert | Loss of Pleasanton - Moore 138kV overloads Dilley2 - Pearsall 69kV. |
| 8/15/06 | 15:44 | 19:45 | Alert | Loss of Lon Hill 138/69kV autotransformer #1 overloads Lon Hill 138/69kV autotransformer #2 or theLoss Lon Hill 138/69kV autotransformer #2 overloads Lon Hill 138/69kV autotransformer #1. |
| 8/15/06 | 15:45 | 19:45 | Alert | Loss San Miguel 69KV to San Miguel 138KV overloads the Derby to Pearsall at 128% of the 40MVA rating. |
| 8/16/06 | 11:00 | 13:02 | OCN | A shortage of UBES bids for hours 14:00 and 15:00. |
| 8/16/06 | 11:52 | 13:30 | OCN | OCN issued capacity shortage for hours 17:00 and 18:00. |
| 8/16/06 | 12:00 | 12:30 | Alert | Adjustment Period Replacement Market opened for hours 16:00 to 24:00. |
| 8/16/06 | 13:00 | 19:00 | Alert | Loss San Miguel 69KV to San Miguel 138KV overloads the Derby to Pearsall. |
| 8/16/06 | 13:04 | 15:00 | OCN | A shortage of UBES bids for hours 16:00 and 17:00. |
| 8/16/06 | 13:05 | 21:00 | Alert | Loss of Pleasanton - Moore 138kV overloads Dilley2 - Pearsall 69kV. |
| 8/16/06 | 13:37 | 21:00 | Alert | Loss of Lon Hill 138/69kV autotransformer #1 overloads Lon Hill 138/69kV autotransformer #2 or theLoss Lon Hill 138/69kV autotransformer #2 overloads Lon Hill 138/69kV autotransformer #1. |
| 8/16/06 | 14:57 | 18:45 | OCN | Physical Responsive Reserve less than 3300MW but greater than 3000MW. |
| 8/16/06 | 15:06 | 18:45 | Advisory | Physical Responsive Reserve less than 3000MW but greater than 2500MW. |
| 8/16/06 | 16:15 | 21:00 | Alert | Transmission Alert issued for theLoss of Hamilton - Sonora 138 kv indicates voltage collapse in area. |
| 8/17/06 | 6:30 | 24:00 | OCN | High pressure will continue to dominate much of Texas weather. A heat advisory remains in effect for Thursday August 17, 2006 from North Central to South Central Texas. This situation could threaten ERCOT System reliability and has a reasonable expectation of leading ERCOT into record breaking demand. |
| 8/17/06 | 9:00 | 9:30 | Alert | Adjustment Period Replacement Market opened for hours 13:00 to 24:00. |
| 8/17/06 | 12:58 | 21:30 | Alert | Loss of Lon Hill 138/69kV autotransformer #1 overloads Lon Hill 138/69kV autotransformer #2 or Loss of Lon Hill 138/69kV autotransformer #2 overloads Lon Hill 138/69kV autotransformer #1. |
| 8/17/06 | 13:15 | 19:00 | Alert | Loss of Pleasanton - Moore 138kV overloads Dilley2 - Pearsall 69kV. |
| 8/17/06 | 13:57 | 21:30 | Alert | Loss San Miguel 69KV to San Miguel 138KV overloads the Derby to Pearsall. |
| 8/17/06 | 14:31 | 14:57 |  | Loss of La Palma to Rio Hondo 345kV or theLoss of La Palma 345/138kV autotransformer overloads South McAllen to Las Milpas 138kV. |
| 8/17/06 | 15:16 | 19:00 | OCN | Physical Responsive Reserve less than 3300MW but greater than 3000MW. |
| 8/17/06 | 15:26 | 19:00 | Advisory | Advisory issued due to Physical Responsive Reserve less than 3000MW but greater than 2500MW. |
| 8/18/06 | 9:52 | 18:00 | OCN | load running approximately 600 MW ahead of yesterday's peak. |
| 8/18/06 | 11:00 | 15:15 | OCN | A shortage of UBES bids for hours 14 thru 20. |
| 8/18/06 | 15:10 | 18:00 | OCN | Physical Responsive Reserve less than 3300 MW but greater than 3000 MW. |
| 8/19/06 | 15:15 | 18:45 | OCN | Physical Responsive Reserve below 3300. |
| 8/19/06 | 15:40 | 18:45 | Advisory | Physical Responsive Reserve below 3000 |
| 8/20/06 | 13:00 | 19:15 | OCN | Physical Responsive Reserve below 3300 |
| 8/20/06 | 14:00 | 19:15 | Advisory | Physical Responsive Reserve below 3000 |
| 8/20/06 | 14:00 | 19:15 | OCN | A shortage of UBES bids for hours 15 thru 19. |
| 8/21/06 | 7:39 | 17:30 | OCN | A capacity shortage at 17:00 and a shortage of UBES bids for hours 14:00 thru 19:00. |
| 8/21/06 | 11:54 | 13:00 | Alert | Adjustment Period Replacement Market opened for hours 15:00 to 24:00. |
| 8/21/06 | 12:41 | 19:00 | OCN | Physical Responsive Reserve below 3300 |
| 8/21/06 | 13:10 | 19:00 | Advisory | Physical Responsive Reserve below 3000 |
| 8/21/06 | 14:47 | 17:00 | Alert | Physical Responsive Reserve below 2500 |
| 8/21/06 | 19:00 | 24:00 | Alert | Loss of Kingsville - Alice 138 kV overloads Orange Grove - San Diego Sub 69 kV. |
| 8/22/06 | 13:38 | 18:00 | OCN | Physical Responsive Reserve below 3300 |
| 8/22/06 | 14:09 | 18:00 | Advisory | Physical Responsive Reserve below 3000 |
| 8/22/06 | 15:00 | 16:30 | Alert | Physical Responsive Reserve below 2500 |
| 8/23/06 | 13:10 | 18:02 |  | Physical Responsive Reserve below 3300MW |
| 8/23/06 | 14:16 | 22:00 | Alert | Loss of the 138kv line Asherton to Escondido overloads 138kv line Uvalde to Asphalt Mines. |
| 8/23/06 | 14:20 | 22:00 | Alert | Loss San Miguel Auto overloads 69kv line Derby to Pearsall. |
| 8/23/06 | 14:21 | 22:25 | Alert | Loss of the Asherton Auto overloads Uvalde Auto. |
| 8/23/06 | 14:24 | 22:00 | Alert | Loss of W. Batesville to Uvalde overloads 138kv line Moore to Downie. |
| 8/23/06 | 14:51 | 20:40 | Alert | Loss of Walnut Springs Auto overloads Olson to Sycamore. |
| 8/23/06 | 16:41 | 19:10 | Alert | Loss of the double ligsw - norsw and norwood switch - cedar hill switch 345kV lines overloads norsw - east levee 138kv line. |
| 8/24/06 | 13:55 | 19:01 | OCN | Physical Responsive Reserve below 3300MW |
| 8/24/06 | 14:53 | 19:01 | Advisory | Physical Responsive Reserve below 3000MW |
| 8/24/06 | 15:21 | 17:57 | Alert | Physical Responsive Reserve below 2500MW |
| 8/25/06 | 10:15 | 16:15 | OCN | A shortage of UBES bids for hours 15:00 thru 18:00. |
| 8/25/06 | 12:45 | 19:00 | OCN | Physical Responsive Reserve less than 3300MW but greater than 3000MW. |
| 8/25/06 | 13:15 | 16:15 | OCN | A capacity shortage for hours 16:00 and 17:00 |
| 8/25/06 | 13:20 | 21:15 | Alert | Loss of the San Miguel 138/69kV Autotransformer overloads the Derby to Pearsall. |
| 8/25/06 | 14:18 | 19:00 | Advisory | Physical Responsive Reserve less than 3000MW but greater than 2500MW. |
| 8/25/06 | 15:00 | 17:45 | Alert | Physical Responsive Reserve less than 2500MW but greater than 2300MW |
| 8/26/06 | 14:20 | 21:00 | OCN | Physical Responsive Reserve less than 3300MW but greater than 3000MW |
| 8/26/06 | 16:35 | 21:00 | Alert | Loss of the San Miguel 138/69kV Autotransformer overloads the Derby to Pearsall |
| 8/26/06 | 16:35 | 21:00 | Alert | Loss of the Asherton 138/69 kV Autotransformer overloads the Uvalde 138/69 kV Autotransformer |
| 8/27/06 | 14:24 | 21:00 | Alert | Loss of the Asherton 138/69 kV Autotransformer overloads the Uvalde 138/69 kV Autotransformer |
| 8/27/06 | 14:25 | 21:00 | Alert | Loss of the San Miguel 138/69kV Autotransformer overloads the Derby to Pearsall 69 kV |
| 8/27/06 | 16:26 | 0:00 | Alert | Loss of Lake Pauline 138/69 kV Autotransformer overloads the Munday to Benjamin 69 kV |
| 8/29/06 | 14:30 | 21:15 | Alert | Loss of San Miguel 138/69 kV Autotransformer overloads Derby to Pearsall 69 kV line |
| 8/29/06 | 16:00 | 18:00 | OCN | Adjusted Responsive Reserve less than 3300 MW but greater than 3000 MW. |
| 8/29/06 | 18:00 | 22:30 | Alert | Loss of Lake Pauline 138/69 kV Autotransformer overloads Munday to Benjamin 69 kV line |
| 8/30/06 | 13:30 | 19:45 | Alert | Loss of San Miguel 138/69 kV Autotransformer overloads Derby to Pearsall 69 kV line |
| 8/30/06 | 14:30 | 15:30 | Alert | Loss of Lake Pauline 138/69 kV Autotransformer overloads Munday to Benjamin 69 kV line |
| 8/30/06 | 15:00 | 19:50 | OCN | Adjusted Responsive Reserve less than 3300 MW but greater than 3000 MW |
| 8/31/06 | 13:30 | 19:00 | OCN | Adjusted Responsive Reserve less than 3300 MW but greater than 3000 MW |
| 8/31/06 | 14:30 | 22:00 | Alert | Loss of San Miguel 138/69 kV Autotransformer overloads Derby to Pearsall 69 kV line |
| 8/31/06 | 15:30 | 19:00 | Advisory | Physical Responsive Reserve less than 3000MW but greater than 2500MW |