## Slide 1: October 17th Event

## Slide 2: October 17th Event
Multiple Planned transmission outages in the San Antonio area.
OCN issued due to Adjusted RR less than 3300 at 13:47
OCN issued due to Capacity shortage for hours ending 17:00 and 18:00
Advisory issued due to due to Adjusted RR less than 3000 at 13:24
At 13:42 forced outage for Lon hill-Nelson Sharpe 345 Kv line.
Emergency notification for post contingency voltage collapse in the valley area with loss of N. Edinburg-Lon hill 345 Kv line.

## Slide 3: October 17th Event
14:42 Unit Trips with 300 Mw.
North to South Zonal flow issues.
17:30 – 18:15 207 MW of Non-Spin Deployed