## Slide 1: System Study for October 3rd College Station Loss of Load Event
ROS Meeting November 9, 2006

## Slide 2
1. CCVT on 138 KV
Gibbons Creek to Roans
Prairie fails

## Slide 3
2. Relay failure leads to explosion of CCVT,
tripping of 3 345/138 KV transformers and clearing
of both 345 KV busses. Major 345 KV path for
North to Houston cut

## Slide 4
3. Loss of Gibbons Creek 345/138 KV transformers and area generation
left only one 138 KV line to supply Bryan/College Station area. Additional loss
of generation (1200 MW total) triggers NERC DCS event and LaaRs shed.

## Slide 5: Oscillation Range
LOCAL
Voltage Oscillation

## Slide 6: Voltage Oscillation: Atkins 69kv 10/3/2006 17:10~10/3/2006 18:30

## Slide 7: Voltage Oscillation: HLK 69kv 10/3/2006 17:10~10/3/2006 18:30

## Slide 8: Voltage Oscillation: JEWET 69kv 10/3/2006 17:10~10/3/2006 18:30

## Slide 9: Possible Reason
The voltage oscillation (instability) only existed around the College Station area and the voltage oscillation frequency was small(2~3mins/cycle), the transient stability, dynamic stability issues can be excluded.
The reason for this voltage oscillation issue is possibly due to a “weak link” between College Station and the rest of ERCOT system, which is a steady state voltage stability issue.

## Slide 10: Possible Reason
Motor/load may try to reconnect to the system when the voltage level reaches normal levels, however, the starting of the motor/load would consume high reactive power, which would then decrease voltage. The voltage oscillation was most likely due to the interaction of motor load.
The recorded historical data showed this kind of scenario.

## Slide 11: Atkins 69kv Load v.s Voltage

## Slide 12
4. Line overload and difficulty maintaining voltage in area necessitated
Shedding of about 339 MW of load to prevent complete collapse of the area

## Slide 14
Future Improvements
Adding breakers between
transformers and busses
and relay improvement
Additional 345/138 KV transformer
and 138 KV lines into area

## Slide 15: Support Units Output
Active Power (MW)
Reactive Power (MVAR)