Texas Nodal

Market Management Systems (MMS)

Requirement Specification

For Day-Ahead Market (DAM) and Supplemental Ancillary Service Market (SASM)

Version 0.9.2

GP&L Comments may be found in the following locations:

- 3.1.2 – Requirement ID PD2

  - Under requirements # 5 & # 6

- 3.3.8 – Requirement ID VA8

  - Under 2 n

- 3.9.3 – Requirement AE3

- 3.9.4 – Requirement AE4

- 3.10.2 – Requirement ID SA2

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 6/30/2006 | 0.1 | Initial Version | Market Ops Support Shuye Teng, Yongjun Ren, Jeff Gilbertson |
| 8/04/2006 | 0.2 | Change input validation Change CE3 and other minor modifications | Vladimir Brandwajn Show Chang Mohit Saigal |
| 8/18/06 | 0.3 | Accepted all previous changes Updates to many requirements Separated action items and questions into comments | Janice Huang, Mohit Saigal Tarek M Mourad |
| 9/03/06 | 0.4 | Accepted all previous changes Updates to many requirements Incorporate ERCOT Comments | Art Cohen, Show Chang, Vladimir B. Janice Huang, Shu Tao, Mostafa Khadem Mohit Saigal Tarek M Mourad |
| 09/16/06 | 0.5 | Accepted all previous changes Updates to many requirements Incorporate ERCOT Comments | Art Cohen, Show Chang, Janice Huang, Shu Tao, Mohit Saigal |
| 09/18/06 | 0.6 | Final review and approval | Mary Nelson |
| 09/21/06 | 0.7 | Updated by ERCOT | Shuye Teng; Yongjun Ren Jeff Gilbertson |
| 9/25/06 | 0.8 | Updates by ABB per ERCOT comments | Mohit Saigal Janice Huang |
| 10/30/06 | 0.9.0 | Updated by ABB per ERCOT comments Replaced Section 1 per Customer Requirements | Mohit Saigal Janice Huang Mary Nelson |
| 11/02/06 | 0.9.1 | Correct Document Name, fix header per Customer | Janice Huang Mary Nelson |
| 11/03/2006 | 0.9.2 | Correct wording in CE4 8.h | Janice Huang |

Table of Contents

1	Introduction	6

1.1	Purpose	6

1.2	Objective	6

1.3	Traceability	6

1.4	Market Management System Requirement Documents	6

2	Day-Ahead Market and Ancillary Services during the Adjustment Period and in Real-Time System Scope	8

2.1	Day-Ahead Market	8

2.2	Ancillary Services during Adjustment Period and Real-Time	11

2.3	Preconditions and Dependencies	13

2.4	Input and Output	13

2.4.1	Inputs	13

2.4.2	Outputs	21

3	Functional Requirements	27

3.1	Business Sub-Process 1: Pre-DAM Activities	27

3.1.1	PD1 – AS Obligation	27

3.1.2	PD2 - QSE Submittal of COP, Bids, Offers, and Trades	28

3.1.3	PD3 – General Validation Process of QSE Input	30

3.2	Business Sub-Process 2: Special Treatment	31

3.2.1	ST1 – RMR	31

3.2.2	ST2 – Combined Cycle Modeling	32

3.3	Business Sub-Process 3: Validation of DAM Submissions and Other Trades	33

3.3.1	VA1 – Validation of Capacity Trades	33

3.3.2	VA2 – Validation of Energy Trades	34

3.3.3	VA3 – Validation of DC Tie Schedules	36

3.3.4	VA4 - Validation of Self Schedules	37

3.3.5	VA5 – Validation of CRR Offers	38

3.3.6	VA6 - Validation of PTP Obligation Bids	40

3.3.7	VA7 – Validation of AS Self-Arrangement	41

3.3.8	VA8 – Validation of AS Offers	42

3.3.9	VA9 – Validation of AS Trade	44

3.3.10	VA10 – Validation of Three-Part Supply Offer - Start-Up and Minimum-Energy Offer and Energy Offer Curve	45

3.3.11	VA11 – Validation of DAM Energy-Only Offers	47

3.3.12	VA12 – Validation of DAM Energy Bids	48

3.3.13	VA13 – Notice of Validation Rules	49

3.3.14	VA14 – Validation of COP	50

3.4	Business Sub-Process 4: Credit Requirement for DAM Bids and Offers	52

3.4.1	CR1 – Credit Requirement	52

3.5	Business Sub-Process 5: Ancillary Service Insufficiency Check	53

3.5.1	SC1 – AS Insufficiency Check	53

3.5.2	SC2 – AS Insufficiency Alert	54

3.5.3	SC3 – Additional AS Offer Validation	54

3.6	Business Sub-Process 6: CRR Day-Ahead Simultaneously Feasibility Test	56

3.6.1	CF1 – CRR Day-Ahead SFT	56

3.7	Business Sub-Process 7: Derating CRR Options Declared for Settlement in Real-Time	58

3.7.1	DC1 – Derating CRR Options Declared for RT	58

3.8	Business Sub-Process 8: Day Ahead Clearing Process	60

3.8.1	CE1 – DAM Pre-processing	60

3.8.2	CE2– Initial Commitment Status	61

3.8.3	CE3 – Network Security Monitor	61

3.8.4	CE4 – DAM Clearing Engine	63

3.8.5	CE5 – Tie-Breaking Rule	69

3.8.6	CE6 – Constraint Penalty Function	69

3.8.7	CE7 – Post-Processing	70

3.8.8	CE8 – Notification of DAM Awards	71

3.8.9	CE9 – Notification of DAM Results	73

3.8.10	CE10 – Control of DAM Clearing Process	74

3.9	Business Sub-Process 9: AS Evaluation in Adjustment Period	75

3.9.1	AE1 – Increased AS Obligation	75

3.9.2	AE2 – Validation of COP Changes	76

3.9.3	AE3 – COP Monitor	76

3.9.4	AE4 – Delivery Evaluation Function	77

3.10	Business Sub-Process 10: Supplemental Ancillary Service Market (SASM)	79

3.10.1	SA1 – SASM Clearing Engine	79

3.10.2	SA2 – Validation of Resubmitted AS Offers	81

3.10.3	SA3 – Validation of AS Self-Arrangement	83

3.10.4	SA4 – Notification of AS awards	84

3.10.5	SA5 - Notification of SASM Results	84

3.11	Business Sub-Process 11: Price Validation and Correction:	85

3.11.1	PC1 – Price Validation and Correction	85

4	Supplementary Requirements	86

4.1	Performance Requirements	86

4.1.1	Market Participant Interface Specific Performance Requirements	86

4.1.2	Market Application Specific Performance Requirements	86

5	Use Cases	87

5.1	Actor Catalog	87

5.2	Use Case Catalog	87

6	Protocol Coverage	91

7	Sub-Process Coverage	96

Appendix 1.	Day-Ahead Market Clearing (DAM)	100

Appendix 2.	Supplemental Ancillary Service Market (SASM) Clearing	112

Appendix 3.	DAM Simultaneous Feasibility Test (SFT)	118

Appendix 4.	Weighted Least Square Method for DAM Derating of CRR Options	120

List of Tables

Table 2-1 Input Data	14

Table 2-2 Output Data	23

Table 5-1 DAM Use Case Actors	87

Table 5-2 DAM Use Cases	87

Table 5-3 MPI Use Cases	88

List of Figures

Figure 2-1 Day-Ahead Operations	8

Figure 2-2 DAM Sub-Process Overview Diagram	11

Figure 2-3 Market Timeline Summary	11

Figure 2-4 AS Sub-Process in Adjustment Period Overview Diagram	13

Figure 3-1 CRR SFT Flow Diagram	57

Figure 3-2 CRR Options Derating Flow Diagram	59

Figure 3-3 NSM Flow Diagram	62

Figure 3-4 DAM Flow Diagram	64

Figure 3-5 DEF Flow Diagram	78

Requirements Specification for Day-Ahead Market

(This Requirements Document is Subordinate To and Compliant with the Texas Nodal Protocols effective May, 2006.)

# Introduction

The primary authority directing the operational characteristics and behavior of the Market Management System is the Texas Nodal Protocols.  This requirements document set is provided as a supplement to assist in the implementation of this system which includes all processes, tools (hardware and software), and operations and constraints necessary for full compliance to the Texas Nodal Protocols.  The Texas Nodal Protocols with this set of requirements documents completes the System “Design To” definition for implementation, test, and operation of a fully compliant Market Management System.

This set of requirements documents consists of five (5) documents as listed in the Market Management Systems Requirement Documents section which follows.

## Purpose

The requirements for the document Texas Nodal Market Management Systems (MMS) Requirement Specification For Day-Ahead Market (DAM) and Supplemental Ancillary Service Market (SASM) and its associated processes are described in the Texas Nodal Protocols.  This supplemental specification describes the external behavior of this specific sub-system.  The Texas Nodal Protocols (Protocols) and this document together with all applied vendor provided products’ functional specifications, describe both functional and nonfunctional requirements, design constraints, and other factors, in order to provide a complete and comprehensive description of the operational performance to be delivered.  All statements or requirements specified in this document are subordinate to the Protocols.

## Objective

The objective of this set of documents is to provide a clear, concise and unambiguous set of requirements together with the Texas Nodal Protocols which provides the complete required technical description of this Texas Nodal Sub-System to allow the developer/implementer to deliver a fully operational, compliant and robust Texas Nodal System.

## Traceability

All requirements are traceable to the Nodal Protocols, and/or regulations such as NERC and FERC.

## Market Management System Requirement Documents

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For Day-Ahead Market (DAM) and Supplemental Ancillary Service Market (SASM)

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For RUC

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For SCED and Real-Time MMS Processes

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For Constraint Competitiveness Test (CCT)

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For Overall MMS System and Other Processes

# Day-Ahead Market and Ancillary Services during the Adjustment Period and in Real-Time System Scope

This Requirements Specification fully describes the functional requirements of the Market Management System (MMS) for the following:

- The Day-Ahead Market (DAM): The DAM is a daily, co-optimized market in the Day-Ahead for Ancillary Service capacity, certain Congestion Revenue Rights, and forward financial energy transactions. Participation in the DAM is voluntary, except for the Reliability Must Run (RMR) Units.

- Ancillary Services during the Adjustment Period and in Real-Time: ERCOT will evaluate Ancillary Service requirements and capacity sufficiency throughout the Adjustment Period and Operating Period and may procure Ancillary Services in the Adjustment Period using the Supplemental Ancillary Service Market (SASM) for:

- Increased need of Ancillary Services capacity above that specified in the Day-Ahead;

- Replacement of Ancillary Services capacity that is undeliverable due to transmission constraints; or

- Replacement of Ancillary Services capacity due to failure of QSEs to provide AS.

The Requirements Specification also describes nonfunctional requirements, design constraints and other factors necessary to provide a complete and comprehensive description of the requirements for DAM and AS during the Adjustment Period and in Real-Time.

Section 4 of the Nodal Protocols describes the features required for the Day-Ahead Market (DAM). Section 6.4.8 of the Nodal Protocols describes the features required for Ancillary Services during the Adjustment Period and in Real-Time. The requirements specified in this document are based mostly on Nodal Protocol Section 4, and also Sections 3, 6, 7, and 16, where appropriate.

## Day-Ahead Market

Figure 2-1 provides the timeline of the major activities that occur in the Day-Ahead Operations.

Figure 2-1 Day-Ahead Operations

The major activities of the Day Ahead Market are:

- Assign Ancillary Service obligations to the QSEs based on ERCOT Ancillary Service Plan requirements.

- Accept/validate:

- Energy offers/bids from the QSEs including:

- Three-Part Supply Offers

- DAM Energy-Only Offers

- DAM Energy Bids

- Energy Trade, Capacity Trade and Ancillary Service Trade data from the QSEs.

- DC tie schedules from the QSEs

- CRR Offers from CRR Account Holders

- PTP Obligation Bids from the QSEs

- Ancillary Service Offers from the QSEs

- Self-Arranged Ancillary Service Quantities from the QSEs

- Self-Schedules from the QSEs

- Read in RMR contract data and prepare RMR Three-Part Supply Offers.

- Obtain electric network data from the EMS and NMMS.

- Perform Ancillary Service Insufficiency check.

- Perform a Simultaneous Feasibility Test (SFT) to determine oversold CRRs quantities.

- Perform a test to determine if the PTP Options declared for settlement in Real-Time can be accommodated by the available transmission capacity. If these options cannot be accommodated, then the options are derated for DAM-modeling purposes proportional to their impact on the overloaded transmission elements.

- Clear the Day-Ahead Market (DAM) and calculate Market Clearing Prices. The DAM maximizes bid demand revenues minus the offer-based costs subject to constraints including:

- Load balance

- Transmission constraints for both the intact network and for the network with selected contingencies

- Ancillary Service requirements

- Bid/offer limits

- Maximum/Minimum On-Line and Minimum Off-Line Time constraints

- Co-optimization constraints limiting both total AS and total AS plus energy from a resource.

- Combined cycle transition constraints

- Split resources constraints

- Block offer constraints

- Process outputs of the DAM clearing engine, post results and publish to Settlement and MIS.

The major DAM sub-processes are shown in Figure 2-2. The sub-functions that make up the DAM Clearing Engine are:

- Pre-processing: Reads in bid/offer data, network data, constraints and requirements and processes the data for use by the remaining sub-functions.

- Initial Unit Commitment (IUC): Optimizes the commitment, energy, AS and CRR dispatch schedules given the various constraints/requirements and generic constraints but without considering any of the other transmission constraints.

- Network Security Monitor (NSM): Evaluates network security given the energy and CRR dispatches from either IUC or NCUC. Generates network constraint equations describing the changes required to the energy and CRR dispatches to remove transmission constraint violations.

- Network Constrained Unit Commitment (NCUC): Optimizes the commitment, energy, AS and CRR dispatch schedules given the various constraints/requirements including the network constraint equations generated by NSM.

The NSM and NCUC shall iterate to ensure all transmission constraints are satisfied. They shall iterate until one of the following conditions is satisfied:

- There are no network constraint violations.

- The remaining transmission constraint violations cannot be cleared.

- The maximum number of iterations allowed has been reached.

Figure 2-2 DAM Sub-Process Overview Diagram

## Ancillary Services during Adjustment Period and Real-Time

Figure 2-3 provides the Market Timeline Summary. The Adjustment Period begins at 1800 in the Day-Ahead and end one full hour before the start of the Operating Hour.

Figure 2-3 Market Timeline Summary

The major activities to support the Ancillary Services during the Adjustment Period and in Real-Time are as follows:

- If AS requirements are more than that specified in the Day-Ahead, then recalculate Ancillary Service Obligations to the QSEs.

- Accept/validate the following:

- Additional Ancillary Service Trade data from the QSEs.

- Additional Ancillary Service Offers from the QSEs.

- Additional Self-arranged Ancillary Service Quantities from the QSEs.

- Replacement of Ancillary Service Trade data from the QSEs.

- Replacement of Ancillary Service Offers from the QSEs.

- Replacement of Self-arranged Ancillary Service Quantities from the QSEs.

- Monitor COP changes.

- Perform Ancillary Service Deliverability check using Deliverability Evaluation Function (DEF).

- Notify QSEs if Ancillary Service substitution is accepted.

- Perform Supplemental Ancillary Service Management (SASM).

- Process outputs of the SASM, post results and publish to Settlement and MIS.

The major AS sub-processes in Adjustment Period are shown in Figure 2-4.

The Supplemental Ancillary Services Market (SASM) procures additional Reg-Up, Reg-Down, Responsive Reserve, and Non-Spinning Reserve Services during the Adjustment Period.  The SASM Clearing Engine minimizes the total cost of AS offers while meeting the AS requirements given the AS offers and self-arranged AS quantities.

Figure 2-4 AS Sub-Process in Adjustment Period Overview Diagram

## Preconditions and Dependencies

In certain cases LMPs produced by the DAM clearing process could be lower than cleared fixed quantity offer prices and/or higher than cleared quantity bid prices

## Input and Output

This section provides a summary of inputs to and outputs from the Day-Ahead Market (DAM) and AS during Adjustment Period and Real-Time processes.

The Market Infrastructure (MI) is a sub-system of the Market Management System. MI provides various functions to support QSE’s data submission and validation. The validated QSE market data are stored in the MI market database to be used as input to DAM and AS during Adjustment Period and Real-Time. The MI database also stores results from DAM and AS during Adjustment Period and Real-Time, including dispatched offers and bids, as well as Market Clearing prices.

### Inputs

Table 2-1 lists all the required input data. The “Source” column of the Input Data table identifies the source where the data is provided to the MMS. The “Used By” column identifies the Application that uses the input data.

Table 2-1 Input Data

| Source | Data | Used By |
| --- | --- | --- |
| Registration | - General Resource Parameters for each Generation Resource represented by the QSE: - The Resource’s name - High Reasonability Limit - Low Reasonability Limit - Type of Resource – steam turbine, hydro, gas turbine, combined cycle, other; - QF status - AS Qualification - Normal Ramp Rate curve - Emergency Ramp Rate curve - Minimum On-Line time - Minimum Off-Line time - Hot start time - Intermediate start time - Cold start time - Seasonal Resource Parameters for each Generation Resource represented by the QSE: - Maximum On-Line time - Maximum daily starts - Load Resource Parameters for each Load Resource represented by the QSE: - The Resource’s name - Minimum interruption time - Minimum restoration time - Maximum interruption time - Maximum daily deployments | MI, DAM |
| QSE | - Three-Part Supply Offers - QSE ID - Resource ID - CCU ID (Combined Cycle Unit ID) - start-up (hot, intermediate, cold) offer price - minimum energy offer price - energy offer curve (price vs. quantity) - First Hour - Last Hour - Percentage of Fuel Index Price (FIP) - Percentage of Fuel Oil Index Price (FOP) - Expiration Time and Date - Exclusive/Inclusive indicator | DAM, RUC, SCED |
| ERCOT/Credit Department | - Credit Information - QSE ID - Credit limit amount | MI |
| QSE | - DAM Energy Bids - QSE ID - Settlement point - Bid ID - Fixed/Variable quantity indicator - Quantity (fixed or variable) price curve - Start Date - First Hour - Last Hour - Expiration Time and Date | DAM |
| QSE | - DAM Energy-Only Offer Curves - QSE ID - Settlement point - Offer ID - Fixed/Variable quantity indicator - Quantity (fixed or variable) price curve - Start Date - First Hour - Last Hour - Expiration Time and Date | DAM |
| QSE | - Self-schedules energy - QSE ID - Quantity for each settlement interval - First Settlement Interval - Last Settlement Interval - Source Settlement Point - Sink Settlement Point | Settlement |
| QSE | - Current Operating Plan (COP) - Operating Plan data for the Current Operating Day - Operating Plan data for the Next Operating Day | DAM |
| QSE | - Ancillary Service Offers - QSE ID - Resource ID - AS Type - Quantity - First Hour - Last Hour - Price for each AS type - Fixed/Variable quantity block indicator - Multi-Hour Block Indicator - Expiration Time and Date | DAM, AS Insufficiency Check, SASM |
| QSE | - Self-Arranged Ancillary Services - QSE ID - AS Type - Date - First Hour - Last Hour - Quantity by Load Resource Type - Quantity of total | DAM, AS Insufficiency Check |
| QSE | - Ancillary Service Trades - Buying QSE ID - Selling QSE ID - AS Type - Trade ID - Trade Date - Quantity - First Hour - Last Hour | SASM, Settlement |
| QSE | - Capacity Trades - Buying QSE ID - Selling QSE ID - Trade ID - Trade Date - Quantity - First Hour - Last Hour | Settlement |
| QSE | - Energy Trades - Buying QSE ID - Selling QSE ID - Trade ID - Trade Date - First Settlement Interval - Last Settlement Interval - Quantity - Settlement Point | Settlement |
| Settlement | - Ancillary Service QSE Obligation calculation - QSE ID - First Hour - Last Hour - Load Ratio Share (LRS) | AS Obligation |
| QSE | - DC Tie Schedule - Buying QSE ID - Selling QSE ID - DC Tie Settlement Point - Quantity (each 15-minute settlement Int. of schedule) - First Settlement Interval - Last Settlement Interval - NERC Tag Information | MI |
| Settlement | - RMR Contract Data | DAM, RUC, SCED |
| Registration | - Combined Cycles Registration Data - Combined Cycle Unit (CCU) Name - CCU mode - Individual Generator Names - Cross reference between CCU and its modes and generators - Transition matrix | DAM |
| CRR | - CRR Ownership Information - Name of CRR Account Holder - CRR ID - First Hour - Last Hour - Hedge Type (OPT or OBL) - CRR Category (PTP or FGR). FGR goes only with OPT Hedge Type - PTP Source Settlement Point - PTP Sink Settlement Point - FGR Identity - CRR Type (With Refund or without Refund) - CRR Quantity | CRR SFT, CRR Option Deration, DAM |
| QSE | - CRR Offers (for NOIE PTP Options Declared to be Settled in RT) - Name of CRR Account Holder - CRR ID - First Hour - Last Hour - Source Settlement Point - Sink Settlement Point - Quantity - Minimum Reservation Price | CRR Option Deration, DAM |
| QSE | - PTP Obligation Bids - QSE ID - Bid ID - Start Date - First Hour - Last Hour - Source Settlement Point - Sink Settlement Point - Quantity - Not to Exceed Price | DAM |
| ERCOT | - Ancillary Service Hourly Requirements (Plan) - AS Type - Hour/Operating Date Quantity - Percentage of Load Resources allowed to provide RRS | AS Insufficiency Check, DAM, SASM |
| NMMS | - Contingency List - Unique contingency sequence number - Unique contingency title - Station ID - Equipment ID - Equipment Type (unit, line, breaker etc.) - SPS/RAP ID | CRR SFT, CRR Option Deration, DAM |
| NMMS | - SPS/RAP | CRR SFT, CRR Option Deration, DAM |
| EMS | - Dynamic Ratings - Equipment ID - Equipment Type - Normal Limit - Emergency Limit - Warning Limit | CRR SFT, CRR Option Deration, DAM |
| EMS | - Load Distribution Factor | CRR SFT, CRR Option Deration, DAM |
| EMS | - Generic Constraints (Security Constraints) | CRR SFT, CRR Option Deration, DAM |
| EMS | - System snapshot - Generator ID - Generator ON/OFF status - Generator Last status change (Date/Time) - Breaker ID - Breaker Status | DAM |
| NMMS | - Network Data (CIM Model based on CPSM plus market extensions) - Bus ID to Hub mapping - Bus ID to load zone mapping | CRR SFT, CRR Option Deration, DAM |
| Outage Scheduler | - Transmission outage schedule data - Equipment ID - Equipment Type (unit, line, breaker, etc.) - Start Time - End Time - Status (outage, in-service, de-rate) - De-rated maximum MW | CRR SFT, CRR Option Deration, DAM |
| Settlement | - Generic Caps - Resource Type - Start-up cost - Minimum energy cost - Fuel Index Price (FIP) - Fuel Oil Index Price (FOP) - RMR Contracts | MI |
| Settlement | - Verifiable Costs - Resource ID - Start-up cost - Minimum energy cost | MI |

### Outputs

Table 2-2 lists the minimum solution data requirements from DAM and AS during Adjustment Period and Real-Time processes to various destinations. Note that the Market Infrastructure (MI) system stores the outputs listed in the table and makes them available to the destination parties. The “Destination” column of the Output Data table identifies the destination target where the data generated by the MMS is sent. The “Generated By” column identifies the Application that generates the output data.

Table 2-2 Output Data

| Destination | Data | Generated By |
| --- | --- | --- |
| QSE, Settlement | - Awarded Hourly DAM Energy-Only Offers - QSE ID - Quantity - Settlement Point - Settlement Point Price - Hour/Date | DAM |
| QSE, Settlement | - Awarded Hourly Three-Part Supply Offers - QSE ID - Resource ID - Quantity - Settlement Point - Settlement Point Price - Hour/Date | DAM |
| QSE, Settlement | - Awarded Hourly DAM Energy Bids - QSE ID - Quantity - Settlement Point - Settlement Point Price - Hour/Date | DAM |
| QSE, Settlement | - Awarded Hourly Ancillary Services Offers - QSE ID - Resource ID - AS type - Quantity - Price - Hour/Date - Market Type Flag (DAM, SASM) - SASM Market ID | DAM, SASM |
| Settlement | - Hourly Oversold CRR Quantities - Violated transmission constraint - Transmission limit quantities - Oversold quantities - Operating Date/Hour - Settlement point - Weighted Shift Factors | CRR SFT |
| Settlement, CRR Account Holder | - Derated CRR Offers (NOIE PTP Options Declared to be Settled in RT) - Name of CRR Account Holder - CRR ID - Operating Date/Hour - Derated Quantity - Minimum Reservation Price | CRR Option Deration |
| Settlement, CRR Account Holder | - Awarded CRR Offers (NOIE PTP Options Declared to be Settled in RT) - Name of CRR Account Holder - CRR ID - Operating Date/Hour - DAM clearing Quantity - Clearing price | DAM |
| Settlement, QSE | - Awarded PTP Obligation Bids - QSE ID - Bid ID - Operating Date/Hour - Source Settlement Point - Sink Settlement Point - DAM Clearing Quantity - Not to Exceed Price - Clearing Price | DAM |
| QSE | - Ancillary Service QSE Obligation - QSE ID - AS Type - First Hour - Last Hour - Quantity | AS Obligation |
| DRUC | - Reduced Ancillary Services Plan - AS type - Reduced AS Quantity - Hour/Date | DAM |
| QSE | - Awarded Combined Cycles Offers - QSE ID - CCU ID - CCU Mode - Quantity - Clearing Price for each CCU Bus - Hour/Date | DAM |
| QSE | - Response (passed/failed validation) to QSE Data submission - COP - Energy Trades - Capacity Trades - AS Trades - CRR Offers - PTP Obligation Bids - Three-Part Supply Offers - Mitigated Offer Caps/Floor - DAM Energy-Only Offers - DAM Energy Bids - Self-schedules energy - Ancillary Service Offers - Self-arranged Ancillary Services - DC Tie Schedule - Combined Cycles offers | MI |
| Settlement | - Additional Data for Settlement - Capacity Trades to settlement system - Energy Trades to settlement system - Self-Schedules - DC-tie Schedules - Ancillary Service Trades - Day-ahead Settlement Point Price for each Settlement Point | MI MI MI MI MI DAM |
| Settlement, MIS | - Market Clearing Price for Capacity (MCPC) - Hour/Date - AS Type - MCPC - Market Type - SASM Market ID | DAM, SASM |
| Settlement, MIS | - DAM Locational Marginal Price (LMP) - Hour/Date - Market Clearing Price - Settlement Point | DAM |

# Functional Requirements

The following sections detail the requirements for the following DAM and AS during Adjustment Period and Real-Time business sub-processes:

- Pre-DAM Activities

- Special Treatment

- Validation of DAM Submissions and Other Trades

- Credit Requirement for DAM Bids and Offers

- Ancillary Service Insufficiency Check

- CRR Day-Ahead Simultaneously Feasibility Test

- Derating CRR Options Declared for Settlement in Real-Time

- Day Ahead Clearing Process

- AS Evaluation in Adjustment Period

- Supplemental Ancillary Service Market (SASM)

- Price Validation and Correction

## Business Sub-Process 1: Pre-DAM Activities

### PD1 – AS Obligation

| Requirement ID | PD1 – AS Obligation |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.2.1.2 |
| Traceability to Sub-Process Maps | AS obligation calculation |
| Description Each QSE shall be assigned its Ancillary Service Obligation based on the Ancillary Service Plan and the Load Ratio Share of each QSE. Requirement - The MMS shall compute each QSE AS Obligation proportionately according to its Load Ratio Share for the same day and hour of the week for the most recent day that Initial Settlement Statements are available. - By 0600 of the Day-Ahead, the QSE shall be notified on the Messaging system of its Ancillary Service Obligation for each service and for each hour of the Operating Day. - By 0600 of the Day-Ahead, ERCOT shall post on the MIS Certified Area each the QSE’s Load Ratio Share used for the Ancillary Service Obligation calculation. - Inputs: - AS Plan from ERCOT - Hourly LRS for each QSE for the same hour and day of the week, for the most recent day for which Initial Statements are available from Settlements - Outputs: - AS Obligation notification to the QSEs |  |

### PD2 - QSE Submittal of COP, Bids, Offers, and Trades

| Requirement ID | PD2 – QSE Submittal of COP, Bids, Offers, Self Schedules, Trades and DC Tie Schedules |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.9, 4.3 (1)(a), 4.3 (1)(b) 4.4 |
| Traceability to Sub-Process Maps | Validated QSE AS self-arrangements, AS Offers, Energy Bids/Offers, COPs, CRR Offers, PTP Obligation Bids, Self Schedules, Energy Trades, Capacity Trades, AS Trades and DC Tie Schedules |
| Description This requirement describes features common to all QSE submissions such as bids, offers, trades, schedules and COPs in the Day-Ahead. General process of Submission, Query and Cancellation of QSE Input Data. The MMS system shall support data requests like submit, query and cancel via the Market Participant Interface (MPI). It performs the necessary validations and processes depending on the data request type: - Submit The following processing steps are followed for the Submit data request: - The submitted data is first validated as per the applicable validation rules. Subsequent steps are performed for only successfully validated data. - The operational database is first queried for the presence of the previous version of the data. - If the data is already present, then the information from the new submission is used to update the data in the operational database. - If the data does not exist in the operational database, new record(s) are inserted into the database. - The results of the bid/offer processing are then relayed back to the QSE. - Query The following processing steps are followed for the Query data request: - The query data is first validated as per the applicable validation rules. Subsequent steps are performed for only successfully validated data. Queries can be for specific data (for example a specific resource for specific trading intervals) or for all data (for example for all facilities for an entire trading day). - The operational database is queried to retrieve the data based on the query request. - The retrieved data is transformed to XML based on the XML Schema and returned to the QSE. - If the data does not exist in the operational database, then error message(s) are inserted into the query data request and returned to the QSE. - Cancel The following processing steps are followed for the Cancel data request: - The cancel data is first validated as per the applicable validation rules. Subsequent steps are performed for only successfully validated data. Cancel requests can be for specific data (for example a specific resource for specific trading intervals) or for all data (for example for all resource for an entire trading day). - The operational database is first queried for the presence of the relevant data. - If the data is present, then the data is marked as removed and shall not be used by any application or system. Successful information message is inserted into the cancel data request and returned to the QSE. - If the data is not present, then error message(s) are inserted into the cancel data request and returned to the QSE. Requirement - All QSE submissions shall be subject to a submission-specific validation process. Refer to Business Requirement section: PD3 (General Validation Process of QSE Input) and specific Business Requirement sections on input validations for more details. - QSEs shall be notified with the results of the validation (pass/fail) along with a transaction ID for tracking purposes. In case of failed submissions, the QSE shall also be notified of the validation errors. Please refer to Business requirement section: PD3 (General Validation Process of QSE Input) for more details. - QSEs shall have the ability to view all of their valid submissions on the MIS at any time. The MMS system shall permit the QSEs to view input data for seven days in the past, the present operating day and future. The time period of seven days in the past is provided for the QSEs to view data for similar days of the week. - Valid submissions shall be permitted to be cancelled prior to the appropriate deadline. - Submissions shall be permitted to be edited, except for those submissions that have been confirmed by two parties (Capacity Trades, Energy Trades and AS Trades). Confirmed two-party submissions shall only be permitted to be rejected by either party. Edited submissions shall be processed as new submissions, and, if valid, shall automatically overwrite the original submission. The original submission shall be preserved for audit purposes. Trade submissions can be edited prior to confirmation from the second party. Offers and bids cannot be edited. - GP&L Comment: “Offers and bids cannot be edited” is in conflict with the rest of part 5 and should be struck. - Submissions of all DAM Offers and Bids shall have the same start date and end date. - GP&L Comment: Should say Offers & Bids having a start date or end date that is not the same date covered by the DAM shall be rejected. - Submissions shall be automatically deactivated at the expiration date/time specified. These are applicable for inputs that require an expiry date. Bids and offers shall be used for the first suitable DAM until the expiry date. If there is no expiry date supplied for inputs that require one, the bid/offer shall be set as default for the next suitable DAM market. - There is no limit to the number of revisions a QSE can make for a given DAM input. - Overlapping offers for Three-Part Supply Offers shall not be allowed. Any offer that is submitted for a period of time where an existing Three-Part Supply Offer exists shall be rejected in full. Overlapping Offers for combined AS Offers shall also be rejected in full. |  |

### PD3 – General Validation Process of QSE Input

| Requirement ID | PD3 – General Validation Process of QSE Input |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4 4.1.1 |
| Traceability to Sub-Process Maps | Validated AS Self-Arrangements, AS Offers, Energy Bids/Offers, COPs, CRR Offers, PTP Obligation Bids, Self Schedules, Energy Trades, Capacity Trades, AS Trades, DC Tie Schedules |
| Description The following table shows the normal timing for the DAM Window on a scheduling day. There is no specified start date. Start Time; End Time; Market Window; Comments. None; 10:00 AM; DAM; Day Ahead Market – Closes the data submission window for D+1 at 10:00 AM, where D is the Scheduling Day.. For most QSE input data (Three-Part Supply Offers, CRR Offers, PTP Obligation Bids, AS Offers), validations shall be in two phases. It is possible that not all validation can be performed at the time of receipt of the DAM data. Validations (Phase 1) shall be performed at the time of receipt to the extent possible. For example, QSE name, price curve formats, expiration date and facilities/participant are validated at the time of receipt of the DAM data. Subsequently, the data shall be re-validated (Phase 2) on every scheduling day for D+1 for credit checks, facilities/participant access rights, validity and other pertinent validations necessary before the DAM market closes. This shall occur at the validation time (nominally at 7:00 am on the scheduling day). Success or failure messages shall be sent to QSE after phase 2 validation has completed. Requirement QSE submitted data shall be validated and stored in the operational database upon receipt. The QSE shall be informed of the results of validation. The communication mechanism during data submission is synchronous, that is the QSE submits the data and waits for the response from the MMS System. QSEs have the ability to revise and/or cancel Trading Data as many times as necessary within the appropriate submission window. General steps of Validating QSE Input: - The submitted data is first validated to ensure it is a valid XML and complies with the MI XML Schema. - Validations related to market window/expiration date are performed. Submit and Cancel data requests for D+1 require the appropriate market window to be open and/or expiration date to be still valid. Query data requests do not require the market window to be open. QSEs can query their data irrespective of the market windows. - The security permission for the combination of QSE, QSE User and the Market is checked. - Validation related to submitted data are performed: - Validations related to the submitted data that does not require any external data are performed. These are validations like Price-Quantity Curve monotonically increasing or decreasing, ending hour and interval are greater than starting hour and interval, etc. - Validations related to the Master File data that require Market Participant Registration data are also performed. The successfully validated and processed data is indicated to QSE by information messages, whereas failures are indicated by error messages. If any validation fails, then all subsequent validations are also performed to the extent possible so that all errors are reported to the QSE. However, there are some critical validations like invalid resource, which shall stop further validations. |

## Business Sub-Process 2: Special Treatment

### ST1 – RMR

| Requirement ID | ST1 – RMR |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.14.1 4.4.8 |
| Traceability to Sub-Process Maps | RMR Offer Creator, RMR Operator, RMR Contract Data |
| Description RMR contracts and other data that are needed for the RMR offer creation shall be provided by the Settlements system via the MMS-Settlements interface. The QSEs who represent RMR resources shall provide the RMR resource availability information by 0600 Day-Ahead. Requirement - The RMR contracts and other data shall be available to the MMS system before the DAM market closes. Before the DAM market closes, the RMR Offer Creator in the MMS system shall automatically create RMR offers based on the RMR contracts provided by the Settlements system. - The ERCOT Operator shall view the RMR offers on the MOI (Market Operator Interface). - The ERCOT Operator shall have the ability to enable/disable each RMR offer by hour through the MOI. - The ERCOT Operator shall have the ability to modify the RMR offers. The modification of the RMR offers shall be subject to the validations in sections PD2 and VA10. The use of RMR offers in DAM shall be ERCOT Operator configurable. - Manual input of the RMR Offers by the ERCOT operator shall not be subject to validations against the RMR contracts. - The QSE representing the RMR unit shall be notified of any RMR awarded offers on the MIS certified area. - Validate RMR Offers if they are modified by the ERCOT operator. - Input - RMR Contracts - Manual Operator Input of RMR Offers - Output - RMR Three-Part Supply Offer data, that is: - Start-up Cost - Min-Energy Cost - Energy Offer Curve - RMR awarded offer notifications to QSE |  |

### ST2 – Combined Cycle Modeling

| Requirement ID | ST2 – Combined Cycle Modeling |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.7.1.1 3.9.1(5) |
| Traceability to Sub-Process Maps | DAM Clearing Engine |
| Requirement - Combined cycle units shall be defined in MMS by a set of configurations (or modes) and the allowed transitions between the modes and the off state. Each mode has a full set of unit parameters such as unit limits, costs, etc. - The MMS functions shall determine, for each time point, which mode is operating and the corresponding mode dispatch. The network model in the MMS functions shall model the various subunits of the combined cycle unit. Data that is input for each mode includes: - Minimum and maximum on-line time (minimum and maximum time the combined cycle unit can be in a given mode prior to transitioning to another mode) - Energy offers (both low and high limits) - Incremental and no-load costs - Startup cost for modes that can start - Reserve bids - Emergency ramp rates for reserve calculations The additional data needed to describe the transitions are: - Startup transition flag -- Y if unit can start up in this mode - Shutdown transition flag -- Y if unit can transition to off from this mode - List of allowed transitions including: - Prior mode - After mode - Minimum on-line and off-line time is also input for the entire unit. - The MMS shall model the configurations of the combined-cycle plant as a separate resource in the optimization. However, inside the Network Security Monitor (NSM), the total MW assigned to each configuration shall be dis-aggregated to individual units for power flow analysis and sensitivity calculation purposes. The System shall use a linear approach to handle the dis-aggregation (i.e., proportional to each unit's capacity). In addition, NSM shall also use the similar linear method to compute the aggregated shift factors for each combined-cycle configuration for resolving network violations. - The combined cycle output to the QSEs shall be the MW dispatch of each generator and the configuration for each time point while the output to the EMS shall be the MW dispatch of each of the generators of the combined cycle unit. |  |

## Business Sub-Process 3: Validation of DAM Submissions and Other Trades

### VA1 – Validation of Capacity Trades

| Requirement ID | VA1 – Validation of Capacity Trades |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.1, 4.4.1.1, 4.4.1.2 |
| Traceability to Sub-Process Maps | Validated Capacity Trades |
| Description The MMS shall validate Capacity Trades against the Protocol specified criteria and reported to the QSEs. This shall provide QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their trade and resubmit, or not submit the trade. Since Capacity Trades involve more than one QSE, both QSEs must confirm the trade before it is considered valid. Valid Capacity Trades only change each QSEs financial responsibility and do not affect the DAM. The QSE shall be notified on the Messaging system when a trade transaction (report, confirm, reject, delete) has occurred. This shall allow any QSE named in a Capacity Trade to view confirmed and unconfirmed Capacity Trades on the MIS certified area. Requirement - The first validation check shall take place when a Capacity Trade is reported to ERCOT. - The first validation check shall check for valid: - Buying QSE ID - Selling QSE ID - Trade ID - Trade Date - First Hour - Last Hour - Rejected if earlier than first hour - Quantity (MW) - Time of submission Capacity Trades submitted after the Adjustment Period for the applicable hours of the Operating Day shall be rejected. - The second validation check shall check for: - Confirmation of trade from both QSEs: - Either the Selling or Buying QSE can report the trade - QSE submitting trade is deemed to have confirmed trade upon submission. - QSE not submitting trade must report confirmation. - The QSE who is the other party to the trade shall be notified of the trade and can view and confirm it by setting a flag against the trade. If the other party attempts to submit the same trade afresh, it shall be rejected. - A given trade is unique for the ordered n-tuple {Trade ID, Buying QSE, Selling QSE and Date/Interval}. For example, QSE-A as buyer and QSE-B as seller can have one unique trade for Capacity for a given Date/Interval and Trade ID. If they have an additional trade, they would enter a new trade with a unique Trade ID to reflect the new trade for the interval. It is possible to have another trade with QSE-B as buyer and QSE-A as buyer since they form a different ordered n-tuple. - Input: - Capacity Trade reported to ERCOT by QSEs - Registration Data (QSE information) - Output: - A notice of a reported capacity trade from ERCOT to both the buying and selling QSEs by using the Messaging System - Status of a reported capacity trade (confirmed or unconfirmed) - Notification to QSE of its invalid capacity trade - Reason for invalidation and Transaction ID of trade (to submitting QSE) - Valid Capacity trade to MIS Certified Area (accessible by both buying and selling QSEs) - Valid Capacity trade to settlement system |  |

### VA2 – Validation of Energy Trades

| Requirement ID | VA2 – Validation of Energy Trades |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.2, 4.4.2.1, 4.4.2.2 |
| Traceability to Sub-Process Maps | Validated Energy Trades |
| Description The MMS shall validate Energy Trades against the Protocol specified criteria and reported to the QSEs. It shall provide QSEs with immediate feedback to allow as much time as possible to make the decision to either correct their trade and resubmit, or not submit the trade. Since Energy Trades involve more than one QSE, both QSEs must confirm the trade before it is considered valid. Valid Energy Trades only change each QSE’s financial responsibility and do not affect the DAM. The QSE shall be notified on the Messaging system when a trade transaction (report, confirm, reject, delete) has occurred. It shall allow any QSE named in an Energy Trade to view confirmed and unconfirmed Energy Trades on the MIS certified area. Requirement - The first validation check shall take place when an Energy Trade is reported to ERCOT. - The first validation check shall check for valid: - Buying QSE ID - Selling QSE ID - Trade Date - Trade ID - First Settlement Interval - Last Settlement Interval Rejected if earlier than first Settlement Interval - Quantity (MW) for each Settlement Interval - Settlement Point - Time of submission - Energy Trades submitted after 14:30 of the day following the applicable Operating Day shall be rejected. - The second validation check shall check for: - Confirmation of trade from both QSEs. - Either the Selling or Buying QSE can report the trade - QSE submitting trade is deemed to have confirmed trade upon submission. - QSE not submitting trade must report confirmation. The QSE who is the other party to the trade shall be notified of the trade and can view and confirm it by setting a flag against the trade. If the other party attempts to submit the same trade afresh, it shall be rejected. - A given trade is unique for the ordered n-tuple {Trade ID, Buying QSE, Selling QSE, Date/Interval and Settlement Point}. For example, QSE-A as buyer and QSE-B as seller can have one unique trade for Energy for a given Trade ID, Date/Interval and Settlement Point. If they have an additional trade, they would enter a new trade with a unique Trade ID to reflect the new trade for the interval. It is possible to have another trade with QSE-B as buyer and QSE-A as buyer since they form a different ordered n-tuple. - Input: - Energy Trade reported to ERCOT by QSEs. - Registration Data (QSE information, Settlement Points information) - Output: - A notice of a reported energy trade from ERCOT to both the buying and selling QSEs by using the Messaging System. - Status of a reported energy trade (confirmed or unconfirmed). - Notification to QSE of its invalid energy trade. - Reason for invalidation and Transaction ID of trade (to submitting QSE). - Valid Energy trade to MIS Certified Area (accessible by both buying and selling QSEs). - Valid Energy trade to settlement system. |  |

### VA3 – Validation of DC Tie Schedules

| Requirement ID | VA3 – Validation of DC Tie Schedules |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.4, 4.4.4.1, 4.4.4.2 |
| Traceability to Sub-Process Maps | Validated DC Tie Schedules |
| Description DC Tie Energy Schedules submitted to the ERCOT MDB shall be tracked back to a similar NERC tagged schedule to facilitate accurate accounting and system operation. This requires that protocol directed specifications be utilized for this validation and linking process. The QSE submitting a DC Tie Energy Schedule shall provide the following data in their submittal: Requirement - Each DC Tie Schedule must be submitted by a QSE and must include the following information: - QSE or non-ERCOT Control Area buying the energy - QSE or non-ERCOT Control Area selling the energy - For the schedule two parties, one shall be a QSE, and the other shall be a non-ERCOT Control Area. - DC Tie Settlement Point for each DC Tie Schedule - Quantity in MW for each 15-minute Settlement Interval of the schedule - First and last 15-minute Settlement Intervals of the schedule and - NERC tag information, which must conform to the standards set forth in NERC Policy 3 and associated appendixes. - Only one QSE out of the buying and selling QSE shall be a non-ERCOT control area. - A DC Tie schedule must be confirmed by the Non-ERCOT control area to be considered valid. This is done outside the MMS system. With this requirement, ERCOT must be able to invalidate a DC Tie schedule in the MMS database that does not have a corresponding NERC tag. This interface should be done through OATI and be automatic based on information available on the schedule and on the NERC tag. - A DC Tie Schedule shall be confirmed by non-ERCOT Control Area to be considered valid. - The following are requirements for a validated DC Tie schedule, as found in protocol 4.4.4.2: These do not imply specific MMS requirements except for bullet (1): - A validated DC Tie Schedule is a schedule that ERCOT has determined: - Meets the criteria listed in Section 4.4.4.1, DC Tie Schedule Criteria; - Is matched —in quantity, time period, DC Tie Settlement Point, and other NERC tag information—by a schedule submitted by a non-ERCOT Control Area; and - For the NERC tag: All Control Areas and transmission service providers with approval rights approve the NERC tag (active approval); or No Entity with approval rights over the NERC tag has denied it and the approval time window has ended (passive approval). - The submitted NERC Tags by the QSE shall be subject to validation for well-formed NERC Tags and against the OATI E-Tags supplied interface data. The manual confirming process is not in MMS. However, the confirmed DC tie schedule should save back to MMS for being used by RUC. - If the relevant E-Tag information is available at the time of submission, QSE shall be notified of the schedules and tags mismatches, if any, as part of the submission response. If the relevant E-Tag information is not available at the time of submission, then as part of a batch process, the ERCOT Operator shall be notified of the schedules and tags mismatches. - Input: - DC Tie Energy Schedules submitted by QSEs to the ERCOT MDB. - OATI E-Tags Interface Data - Output: - Feedback to QSE if schedule does not pass validation and reason. - Notification to ERCOT Operator of mismatch between MDB schedules and implemented OATI NERC tags. |  |

### VA4 - Validation of Self Schedules

| Requirement ID | VA4 – Validation of Self Schedules |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.3, 4.4.3.1, 4.4.3.2 |
| Traceability to Sub-Process Maps | Validated Self Schedules |
| Description Self-Schedules, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. This shall provide QSEs with immediate feedback to allow as much time as possible to make the decision to either correct their report and resubmit, or not submit the report. QSE submissions shall be validated at the time of submission. As part of the submission response, the QSE shall be notified of the PASS or FAIL indicator and appropriate validation errors, if the submission failed. The QSE named in a Self-Schedule shall view the validated Self-Schedules on the MIS certified area. Requirement - Validation shall take place when Self Schedules are reported. - The validation check shall check for valid: - QSE ID - First Settlement Interval (interval includes date information) - Last Settlement Interval (interval includes date information) - Rejected if earlier than first Settlement Interval - Quantity (MW) for each Settlement Interval - Source Settlement Point - Sink Settlement Point - Time of submission - Self-Schedule reports submitted after the end of the Adjustment Period for the applicable Settlement Interval shall be automatically rejected. - Input: - Self-Schedule reported to ERCOT from QSE - Registration Data (QSE information, Settlement Points information) - Output: - Notification of self-schedules received by ERCOT - Notification of invalid self-schedules - Reason for invalidation and Transaction ID of report to QSE - Valid Self-Schedule to MIS Certified Area (accessible by applicable QSE only) - Valid Self-Schedule to Settlements |  |

### VA5 – Validation of CRR Offers

| Requirement ID | VA5 – Validation of CRR Offers |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.5, 4.4.5.1, 4.4.5.2 |
| Traceability to Sub-Process Maps | Validated CRR Offers |
| Description CRR Offers, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the CRR Account Holder. This shall provide the CRR Account Holder with immediate feedback to have as much time as possible to make the decision to either correct their offer and resubmit, or not submit the offer. CRR offer submissions shall be validated at the time of submission. As part of the submission response, the CRR shall be notified of the PASS or FAIL indicator and appropriate validation errors, if the submission failed. The CRR account holder named in a CRR shall view the validated CRR offers on the MIS certified area. Requirement - Validation shall take place when CRR Offers are reported to ERCOT. - The validation check shall check for valid: - Name of CRR Account Holder The CRR Account Holder for whom the CRR Offer is being submitted must be shown as the owner in the ERCOT CRR registration system of the CRRs being offered. - CRR ID: Rejected if CRR Account Holder is not owner of CRR - Source Settlement Point Rejected if not the same as Source Settlement Point associated with CRR ID - Sink Settlement Point: Rejected if not the same as Sink Settlement Point associated with CRR ID - First Hour - Last Hour Rejected if earlier than start time Rejected if start/end time is out of range of time period defined by CRR ID - Quantity Rejected if the sum of offers of the same CRR ID is greater than total quantity of CRR owned by CRR Account Holder (for that CRR ID). Multiple offers for the same CRR ID can be submitted. Rejected if greater than 110% of NOIE peak forecast (for NOIE PTP Options or PTP Options w/Refund for Real-Time Settlement). Minimum Reservation Price ($/MWh): Defaults to $2000/MWh - NOIE Peak Load forecast for Operating Day: - Offer of multiple CRRs All CRRs must be of the same type. All CRRs must have the same source and sink Settlement Points. A block CRR Offer must have the same number of CRRs offered in each hour. A block CRR Offer must have contiguous hours for the CRRs offered. - Time of submission: Rejected if later than DAM market closure for bid/offer submission - Before 7:00 am, any CRR offers submitted shall go through validations (excluding CRR ownership validation and total quantity). Since the CRR auction data is not available to the MMS system, the additional validations shall be done by a background process when the data is available (before 7:00 am) - At 7:00 am, a background process shall run on the MMS system to validate the submitted CRR offers against the CRR auction data (CRR ownership and total quantity). This shall allow enough time for the CRR bilateral trades information to be available to the MMS system. The CRR submitter shall be notified of the additional validation results on the Messaging system. - Any CRR offers submitted by the CRR account holder after the background process completes (time to be determined), shall be subject to additional validations, such as whether this CRR offer owner is the real owner and whether the sum of offers of the same CRR ID is greater than total quantity of CRR owned by CRR Account Holder for that CRR ID. - Input: - CRR auction data from CRR system - CRR Offer from CRR Account Holders who are NOIEs and this is submitted via the MMS QSE interface. - Registration Data - Output: - Notification to CRR Account Holder of invalid CRR Offers (both background processes and submission) - Reason for invalidation and Transaction ID of CRR Offer to CRR Account Holder - Valid offer posted to MIS Certified Area (accessible by applicable CRR Account Holder only) - Valid offer input to DAM |  |

### VA6 - Validation of PTP Obligation Bids

| Requirement ID | VA6 – Validation of PTP Obligation Bids |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.6, 4.4.6.1, 4.4.6.2 |
| Traceability to Sub-Process Maps | Validated PTP Obligation Bids |
| Description PTP Obligation Bids, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. This shall provide QSEs with immediate feedback to allow them to make decision to either correct their offer and resubmit, or not submit the offer. PTP Obligation Bids offer submissions shall be validated at the time of submission. As part of the submission response, the QSE shall be notified of the PASS or FAIL indicator and appropriate validation errors, if the submission failed. The QSE named in a PTP Obligation Bid shall view the validated PTP Obligation Bids on the MIS certified area. Requirement: - Validation shall take place when PTP Obligation bids are reported to ERCOT. - The validation check shall check for valid: - QSE ID submitting the PTP Obligation Bid - Source Settlement Point - Sink Settlement Point - Bid ID (used for overlapping submissions) - Start Date (is Date) - First Hour - Last Hour - Expiration Time and Date: Reject if date is earlier than the Start Date Reject if date is not supplied - Quantity - Not-to-Exceed Price ($/MWh) - Bid for more than one PTP Obligation should: Include the same number of PTP Obligations in each hour of the block Have the same source and sink Settlement Points Have contiguous hours - Time of submission: Rejected if later than DAM market closure for bid/offer submission - Credit Requirement: Rejected if QSE does not meet criteria of Section 16 and 4.4.10 - Input: - PTP Obligation Bid from QSE via the MMS QSE interface - Registration Data (QSE information, Settlement Points information) - Output: - Notification to QSE of invalid PTP Obligation Bid - Reason for invalidation and Transaction ID of PTP Obligation Bid to QSE - Valid bid posted to MIS Certified Area (accessible by applicable QSE) - Valid bid input to DAM |  |

### VA7 – Validation of AS Self-Arrangement

| Requirement ID | VA7 – Validation of AS Self-Arrangement |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.7.1 |
| Traceability to Sub-Process Maps | Validated AS Self-Arrangements |
| Description AS Self-Arrangements, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. This shall provide QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their report and resubmit, or not submit the report. AS Self-Arrangements submissions shall be validated at the time of submission. As part of the submission response, the QSE shall be notified of the PASS or FAIL indicator and appropriate validation errors, if the submission failed. The QSE named in an AS Self-Arrangement shall view the validated AS Self-Arrangement on the MIS certified area. Requirement - Validation shall take place when self-arrangement quantities are reported. - The validation check shall check for valid: - QSE ID - AS type (Reg-Up, Reg-Down, RRS, Non-Spin) - Date - First Hour - Last Hour - Quantity of self-arrangement provided by Load Resources Rejected: If RRS is more than limiting percentage of AS Obligation - Quantity of total self-arrangement by type Curtail to the total AS Obligation if more self-arrangement is more than total AS Obligation. - Time of submission Self-Arrangement reports submitted after DAM market closure for bid/offer submission for the Operating Day shall be automatically rejected, unless a SASM is opened or ERCOT calls for more AS offers due to AS insufficiency. - All unreported hours of self-arrangement shall be considered as no self-arrangement and ERCOT shall procure those AS quantities in the DAM or DRUC as applicable. - This submission shall trigger the credit checking process. - Input: - Self-arrangement report from QSE - Registration Data (QSE information, Resource Parameters) - Output: - Notification to QSE of invalid AS self-arrangement - Notification to QSE that quantity of total self-arrangement is curtailed (in case of excess self-arrangement) - Reason for invalidation and Transaction ID of report to QSE - Valid self-arrangement to MIS Certified Area (accessible by applicable QSE only) - Valid self-arrangement input to DAM |  |

### VA8 – Validation of AS Offers

| Requirement ID | VA8 – Validation of AS Offers |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.7.2, 4.4.7.2.1, 4.4.7.2.2 |
| Traceability to Sub-Process Maps | Validated AS Offers |
| Description AS Offers, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. The MMS shall provide QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their offer and resubmit, or not submit the offer. AS offers shall be categorized in to three groups: - Online Reserves: Reg-Up, Responsive Reserve, Non-Spin Online - Reg-Down - Non-Spin Offline Requirement The System shall not validate Resource specific Ancillary Service Offers against the associated Resource’s COP. Validate AS Offers - Validation shall take place when AS Offers are reported to ERCOT. - The validation check shall check for valid: - QSE ID - Resource ID: Rejected if Resource not represented by QSE - AS type (“Online Reserves”, “Reg-Down”, “Non-Spin Offline”) - Resource ID: qualified to provide the type of AS - First Hour (is Date and Time which indicates start hour) - Last Hour (is Date and Time which indicates end hour): Rejected if earlier than Start Time - Start Date equals End Date - Expiration Time and Date (is Date and Time: wall clock time): Rejected if time/date is in the past - Fixed/Variable Quantity Block indicator - Offer Curves Price ($/MWh): Rejected if more than Offer cap (e.g. $1000/MWh) For Online Reserves: Reg-Up price, Responsive Reserve price and online Non-Spin price. For Reg-Down Reserves: Reg-Down price For Non-Spin Offline: Non-Spin offline price Quantity (MW): Rejected if more than 150 MW (configurable parameter) when ‘Fixed block’ indicated Up to 5 sets of capacity offers: Rejected if more than 5 sets - Multi-Hour Block Indicator: AS Offer shall be rejected if indicator is Multi-Hour Block for Generation Resource. Default is not a “Multi-Hour Block”. - If a fixed quantity block, which may only be offered by a Load Resource, the single price (in $/MW) and single quantity (in MW) for all hours offered in that block; - If a variable quantity block, which may be offered by a Generation Resource or a Load Resource, the single price (in $/MW) and single “up to” quantity (in MW) contingent on the purchase of all hours offered in that block; and - Overlapping AS Offers for the particular AS Type shall be rejected in full. - GP&L Comment: Not clear on word overlap – If QSE has 10 mw of A/S capacity, they can bid those 10 mw for a particular service as 5 mw @ $X and 5 mw @ $Y. In addition, Protocol 4.4.7.2.1(1)(c) states “The quantity in MW and Ancillary Service type from that Resource for this specific offer and the specific quantity in MW and Ancillary Service type of any other Ancillary Service offered from this same capacity;” Therefore, a QSE could bid the same 10 mw capacity for multiple A/S services. - Time of submission Deadline defaults to 1000 for DAM If ERCOT calls for more AS offers due to AS insufficiency, a new deadline must be specified (see SC3). - Credit Requirement: Rejected if QSE does not meet criteria of Section 16 and 4.4.10 - Input: - AS Offer from QSE - Registration Data (QSE information, Resource parameters) - Output: - Reason for invalidation and Transaction ID of AS Offer to QSE - Valid offer posted to MIS Certified Area (accessible by applicable QSE only) - Valid offer input to DAM |  |

### VA9 – Validation of AS Trade

| Requirement ID | VA9 – Validation of AS Trade |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.7.3, 4.4.7.3.1, 4.4.7.3.2 |
| Traceability to Sub-Process Maps | Validated AS Trades |
| Description AS Trades shall be validated by the MMS against the Protocol specified criteria and reported to the QSEs. This shall provide QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their trade and resubmit, or not submit the trade. Since AS Trades involve more than one QSE, both QSEs must confirm the trade before it is considered valid. Valid AS Trades only change each QSE AS Supply Responsibility and do not affect the DAM. Requirement - The first validation check shall take place when an AS Trade is reported to ERCOT. - The first validation check shall check for valid: - Buying QSE ID - Selling QSE ID - AS type (Reg-Up, Reg-Down, Responsive Reserve, Non-Spin) - Trade Date - Trade ID - First Hour - Last Hour Rejected if earlier than First Hour - Quantity (MW) - Time of submission - The second validation check shall check for: - Confirmation of trade from both QSEs: Either Selling or Buying QSE can report the trade QSE submitting trade is deemed to have confirmed trade upon submission QSE not submitting trade must report confirmation The QSE, who is the other party to the trade, shall be notified of the trade and can view and confirm it by setting a flag against the trade. If the other party attempts to submit the same trade again, it shall be rejected. - A given trade is unique for the ordered n-tuple {Trade ID, Buying QSE ID, Selling QSE ID and Date/Interval. For example, QSE-A as buyer and QSE-B as seller can have one unique trade for AS for a given Date/Interval and Trade ID. If they have an additional trade, they would enter a new trade with a unique Trade ID to reflect the new trade for the interval. It is possible to have another trade with QSE-B as buyer and QSE-A as buyer since they form a different ordered n-tuple. - Input: - AS Trade - Registration Data (QSE information) - Output: - Reason for invalidation and Transaction ID of trade (to submitting QSE) - Unconfirmed Capacity trade to other QSE (the one that did not submit) for confirmation - Valid AS trade to MIS Certified Area (accessible by both buying and selling QSEs) - Valid AS trade to settlement system |  |

### VA10 – Validation of Three-Part Supply Offer - Start-Up and Minimum-Energy Offer and Energy Offer Curve

| Requirement ID | VA10 – Validation of Three-Part Supply Offer - Start-Up and Minimum-Energy Offer and Energy Offer Curve |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.9.1, 4.4.9.2, 4.4.9.2.1, 4.4.9.2.2, 4.4.9.3, 4.4.9.3.1, 4.4.9.3.2 |
| Traceability to Sub-Process Maps | Validated (Three-Part Supply) Energy Bids/Offers |
| Description Three-Part Supply Offers- Start-Up and Minimum-Energy Offers and Energy Offer Curves, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSEs. This shall provide the QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their offer and resubmit, or not submit the offer. Requirement The System shall allow at most one hourly Start-Up and Minimum-Energy Offer to be submitted by a Resource into the DAM. The System shall not validate Resource specific Three-Part Supply Offers against the associated Resource’s COP. Offers Validation: - Validation shall take place when Three-Part Supply Offers are reported to ERCOT. - The validation check shall check for valid: - QSE ID - Resource ID: Rejected if Resource is not represented by QSE. Rejected if Resource ID is a RMR unit. Rejected if Resource is a Load Resource. - CCU (Combined Cycle Unit) – required for combined cycle offers when Resource ID represents a combined cycle mode. - Start Time (is Date and Time which indicates start hour) - End Time (is Date and Time which indicates end hour): Rejected if earlier than Start Time - Start Date equals End Date - Expiration Date (is Date and Time: wall clock time): Rejected if date/time is in the past Rejected if date/time is not “n” number of hours ahead of the current system time. - Hot, Intermediate, and Cold Startup Offer Prices ($) Rejected if more than approved verifiable Resource-specific startup cost. Rejected if more than Resource Category Generic Startup Cost and there is no approved verifiable startup cost. - Minimum-Energy Offer Price ($/MWh) Rejected if more than approved verifiable Resource-specific minimum-energy cost. Rejected if more than Resource Category Generic Startup Cost and there is no approved verifiable minimum-energy cost. - Offer Curve Price ($/MWh) and Quantity (MW) pairs – limit of 10 Rejected if any price is not within range of -$250/MWh to $1,000/MWh Rejected if any price is not within the range of the resource-specific price floors and caps Rejected if pairs are not entirely monotonically non-decreasing IDs of AS offers from same capacity of Resource Inclusive or Excusive designation: default is inclusive if not supplied - Percentage of FIP and Percentage of FOP For combined cycle, gas steam, and simple cycle resources: offer rejected unless FIP percentage + FOP percentage=100% - Overlapping Three-Part Supply Offers shall be rejected in full. - Time of submission - Input: - Three-part supply offer - Startup/Minimum Energy Offer and Energy Offer Curve from QSE - Generic Caps - Verifiable Startup - Minimum Energy Costs (from Settlements) - Resource-specific price floors and caps - Registration Data (QSE information, Resource parameters) - Output: - Reason for invalidation and Transaction ID of Startup/Minimum Energy Offer to QSE - Valid offer posted to MIS Certified Area (accessible by applicable QSE only) - Valid offer input to DAM |  |

### VA11 – Validation of DAM Energy-Only Offers

| Requirement ID | VA11 – Validation of DAM Energy-Only Offers |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.9.5, 4.4.9.5.1, 4.4.9.5.2 |
| Traceability to Sub-Process Maps | Validated (Three-Part Supply) Energy Bids/Offers |
| Description DAM Energy-Only Offers, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. This shall provide QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their offer and resubmit, or not submit the offer. Requirement - Validation shall take place when a DAM Energy-Only Offer is reported to ERCOT. The minimum generation for DAM Energy-Only Offer can be zero. - The validation check shall check for valid: - QSE ID - Settlement Point - Offer ID (used for overlapping submissions) - Start Date - First Hour - Last Hour: Rejected if earlier than first hour Expiration Date: Rejected if time/date is in the past - Fixed Quantity/Variable Quantity/Curve indicator - Fixed or Variable Quantity: Price ($/MWh) and Quantity (MW) - Curve: Price ($/MWh) and Quantity (MW) pairs – limit of 10 Rejected if any price is not within range of -$250/MWh to $1,000/MWh Rejected if pairs are not entirely monotonically non-decreasing - Time of submission: Submissions for the Operating Day after the specified DAM market deadline shall be applicable for the next DAM day - Input: - Energy Offer from QSE - Registration Data (QSE information, Settlement Points information) - Output: - Reason for invalidation and Transaction ID of Energy Offer to QSE - Valid offer posted to MIS Certified Area (accessible by applicable QSE only) - Valid offer input to DAM |  |

### VA12 – Validation of DAM Energy Bids

| Requirement ID | VA12 – Validation of DAM Energy Bids |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.9.6, 4.4.9.6.1, 4.4.9.6.2 |
| Traceability to Sub-Process Maps | Validated (Three-Part Supply) Energy Bids/Offers |
| Description DAM Energy Bids, as well as other potential inputs into the DAM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. This shall provide QSEs with immediate feedback to allow them to make the decision to either correct their offer and resubmit, or not submit the offer. Requirement - Validation shall take place when a DAM Energy Bid is reported to ERCOT. - The validation check shall check for valid: - QSE ID - Settlement Point - Bid ID (used for overlapping submissions) - Start Date - First Hour - Last Hour: Rejected if earlier than first hour - Expiration time/date: Rejected if time/date is in the past - Fixed Quantity/Variable Quantity/Curve indicator - Fixed or Variable Quantity: Price ($/MWh) and Quantity (MW) - Curve Price ($/MWh) and Quantity (MW) pairs – limit of 10 Rejected if pairs are not entirely monotonically non-increasing - Time of submission: Submissions for the Operating Day after the specified DAM market deadline shall be applicable for the next DAM day - Input: - DAM Energy Bid from QSE - Registration Data (QSE information, Settlement Points information) - Output: - Reason for invalidation and Transaction ID of DAM Energy Bid to QSE - Valid bid posted to MIS Certified Area (accessible by applicable QSE only) - Valid bid input to DAM |  |

### VA13 – Notice of Validation Rules

| Requirement ID | VA13 – Notice of Validation Rules |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.2.4 |
| Traceability to Sub-Process Maps | Not on map |
| Description Rules for validation of QSE submitted data shall be made available to QSEs so that they can validate their data before submission if they choose to do so. This shall decrease the number of invalid submissions to ERCOT. Validation rules can be published by the MMS to the MIS Secure Area at any time. - Input: - Validation Rules from software documentation and code - Output: - Validation Rules and Code to MIS Secure Area (accessible by all QSEs) |  |

### VA14 – Validation of COP

| Requirement ID | VA14 – Validation of COP |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.9, 3.9.1, 3.9.2 |
| Traceability to Sub-Process Maps | Validated COPs |
| Description Each QSE that represents a Resource must submit a COP to ERCOT that reflects expected operating conditions for each Resource for each hour in the Operating Day and the next seven Operating Days. ERCOT shall accept COPs for resources only from the QSE representing the Resource. QSEs shall update their COPs to reflect changes in availability of any Resource not later than 60 minutes after the event that caused the change. Requirement - Validation shall take place when a COP is reported to the MMS system - The validation shall check for valid: - Name of the Resource - Date - Start Hour - End Hour - Expected Resource Status: Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status - the validation should check that the particular resource type as indicated in the registration data is permitted to have a given status: ONRUC – On-Line and the hour is a RUC-Committed Interval; ONREG – On-Line Resource with Energy Offer Curve providing Regulation Service; ON – On-Line Resource with Energy Offer Curve; ONDSR – On-Line Dynamically Scheduled Resource; ONOS – On-Line Resource with Output Schedule; ONOSREG – On-Line Resource with Output Schedule providing Regulation Service; ONDSRREG – On-Line Dynamically Scheduled Resource providing Regulation Service; ONTEST – On-Line Test with Output Schedule; ONEMR – On-Line EMR (available for commitment or dispatch only for ERCOT-declared Emergency Conditions; the QSE can appropriately set LSL and HSL to reflect operating limits); and ONRR – On-Line as a synchronous condenser (hydro) providing Responsive Reserve but unavailable for dispatch by SCED and available for commitment by RUC. Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource status: OUT – Off-Line and unavailable; OFFNS – Off -Line but reserved for Non-Spin; OFF – Off-Line but available for commitment by DAM and RUC; and EMR – Available for commitment only for ERCOT-declared Emergency Condition events; the QSE can appropriately set LSL and HSL to reflect operating limits; and Select one of the following for Load Resources: ONRGL – Available for dispatch of Regulation Service; ONRL – Available for dispatch of Responsive Reserve Service or Non-Spin, including Load Resources on high-set under frequency relays; and OUTL – Not available; - The High Sustained Limit (HSL); - The Low Sustained Limit (LSL); - The High Emergency Limit (HEL); - The Low Emergency Limit (LEL); and - Ancillary Service capacity in MW for Non-RMR units. Reject submission if COP is submitted for RMR units: Reg-Up; Reg-Down; Responsive Reserve; and Non-Spin - For combined-cycle Resources, the above items are required for each operating configuration. Only one operating configuration can be specified on-line for each time period. - A QSE representing a Wind-Powered Generation Resource (WGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Wind-Powered Generation Resource Production Potential provided by ERCOT. - A QSE representing a Resource that has a Resource Status of ONTEST must self-commit the Resource and must submit an Output Schedule for the Resource. - Reject COPs that do not meet the criteria as listed in protocol sections 3.9.1, 3.9.2 as applicable to DAM and notify the QSE through the Messaging System of the validation errors. - A QSE representing a Resource that has an Energy Offer Curve valid for an hour of the COP, cannot designate a Resource Status of ONTEST, ONOS or ONDSR for that hour for that Resource. - If the COP is modified in the Adjustment period for AS, HSL/LSL and/or status changes, the COP change shall be alarmed to the ERCOT Operator. Refer to section AE2 for further details. - Input: - COP from QSE - Output: - Pass or Fail Indication of COP submission - Reason for invalidation and Transaction ID of COP to QSE |  |

## Business Sub-Process 4: Credit Requirement for DAM Bids and Offers

### CR1 – Credit Requirement

| Requirement ID | CR1 – Credit Requirement |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.10 16.11.4.5 |
| Traceability to Sub-Process Maps | Not on Map |
| Description Each QSE’s ability to bid and offer in the DAM is subject to the criteria under Section 4.4.10, Registration and Qualification of Market Participants. If the criteria are not met, the MMS shall reject all of the QSE’s bids and offers, and shall notify the QSE through the MIS Certified Area. This requirement should be referenced by the validation process of energy bid, energy offer and self-arranged Ancillary Services. The credit check validation (which is part of the Phase 2 validation in section PD3) shall be performed daily at 7:00 am and the results of these validations be notified to the QSE. This shall allow the QSEs to re-submit their DAM input data as necessary before the DAM market closure. Requirement - ERCOT calculates credit exposure for bids and offers in the DAM as follows: - For each DAM Energy Bid, the quantity of the bid multiplied by the bid price. - For each DAM Energy Offer, the product of the quantity of the offer times the 95th percentile of the hourly difference of Real-Time Settlement Point Price and Day-Ahead Settlement Point Price over the previous 30 days for the hour. - For DAM Energy Bids and Offers at the same Settlement Point for the same hour, ERCOT must calculate the credit exposure as the maximum of the credit exposure for the DAM Energy Bid as calculated in 1 or the credit exposure for the DAM Energy Offer as calculated in 2 above. - For PTP Obligation Bids, the sum of the quantity of bid multiplied by the bid price, if positive, plus 95th percentile of the hourly positive price difference between the source Real-Time SPP minus the sink Real-Time SPP over the previous 30 days for the hour. - Only positive price differences shall be used to determine the 95th percentile. Since the hourly price difference between source and sink cannot always be positive, there shall not always be 30 values to take the 95th percentile of, and therefore the equivalency described above in the energy offer percentile cannot always apply. The MMS shall use linear interpolation to compute the 95th percentile when it lies between two different values - For Ancillary Services not self-arranged, the product of the quantity of Ancillary Service not self-arranged times the 95th percentile of the hourly MCPC for that Ancillary Service over the previous 30 days for that hour. - Credit limits will be passed to MMS from the Credit system on Business Day evenings. The credit check validation shall be performed daily at 0700. - The credit check validation will look at each QSE’s DAM activities cumulatively for operating days Sunday, Monday, and Tuesday. The cumulative impact of those auctions shall stay within the credit limit for that QSE sent by the Credit system on Friday evening. - If a weekday is a holiday, the credit check validation shall look at each QSE’s DAM activities cumulatively until it receives a new credit limit for that QSE from the Credit system. - Input - QSE’s credit limit (from ERCOT Credit Monitor System) to bids and offers in the DAM subject to the criteria under Section 4.4.10, Registration and Qualification of Market Participants - QSE’s Ancillary Services not self-arranged, PTP Obligation Bids, DAM Energy Bids and Offers - Real-Time Settlement Point Price and Day-Ahead Settlement Point Price over the previous 30 days for the hour - The hourly MCPC for Ancillary Services over the previous 30 days for that hour - Output - QSE’s Credit exposure for DAM bids and Offers. - If QSE’s credit exposure for DAM bids and Offers is more than the QSE’s Credit limit for DAM: - Reject all Bids and Offers of that QSE - Notify that QSEs violated their credit limit |  |

## Business Sub-Process 5: Ancillary Service Insufficiency Check

### SC1 – AS Insufficiency Check

| Requirement ID | SC1 – AS Insufficiency Check |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.18 4.5.2 (1) |
| Traceability to Sub-Process Maps | AS Insufficiency Check |
| Description The purpose of the AS Insufficiency Check is to determine whether enough AS have been reported (in the form of AS Offers and Self-arrangements) to cover the total AS requirement. If it appears that there is insufficient AS, this gives ERCOT the opportunity to call for additional AS offers for the DAM. The MMS shall perform the AS Insufficiency Check as follows: - The AS Insufficiency check shall normally run at 1000 in the Day-Ahead. The check shall be initiated by the ERCOT Operator. - The AS Insufficiency Check shall determine AS sufficiency for each AS type of each hour of the Operating Day. - If the AS Insufficiency check reports insufficiency, ERCOT shall wait at least 30 minutes before executing DAM to allow submission of new AS offers. - In the AS Insufficiency Alert sent out to QSE, the MMS shall inform the market the available quantity of that type AS and the total of associated linked offers. - If the additional Ancillary Service Offers are insufficient to supply the Ancillary Service required in the Day-Ahead Ancillary Service Plan, then the DAM clearing engine shall preserve AS Plan requirements in the following order of priority: - Reg-Up - Reg-Down - Responsive Reserve - Non-Spin - Inputs: - All DAM clearing engine inputs - Outputs: - AS Insufficiency status (Sufficient/Insufficient) to ERCOT Operator - If Insufficient, the details of the AS insufficiencies to ERCOT Operator and SC2 - Hours, Quantity, and Type of AS as appropriate |  |

### SC2 – AS Insufficiency Alert

| Requirement ID | SC2 – AS Insufficiency Alert |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.2 (1)(a) 6.5.9.3.3(2)(b) 6.5.9.3.3 (7) |
| Traceability to Sub-Process Maps | AS Insufficiency Check |
| Description The purpose of the AS Insufficiency Alert is to notify QSEs of the need for additional AS Offers. The AS Insufficiency Alert shall be specific to help QSEs know what types, quantities, and hours of AS are expected to be insufficient, to the best of the ERCOT Operator’s knowledge. Requirement - Upon completion of the AS Insufficiency Check, if AS insufficiency is determined as specified in SC1, the MMS shall create a draft alert containing the AS insufficiency information output by SC1. - ERCOT Operators shall have the ability to edit the alert before distribution. - The alert shall be posted to the MIS Secure Area (accessible by all QSEs) when released by ERCOT Operators. - Inputs: - Output of AS Insufficiency Check (SC1) - Outputs: - Draft alert to ERCOT Operator - Final alert posted to the MIS |  |

### SC3 – Additional AS Offer Validation

| Requirement ID | SC3 – Additional AS Offer Validation |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.2 (1)(b) |
| Traceability to Sub-Process Maps | Validated AS Self-Arrangements |
| Description Additional AS Offers can be requested by ERCOT prior to executing the DAM when ERCOT believes there shall be insufficient AS, as determined by the AS Insufficiency Check (SC1). The additional offers are subject to additional validation criteria, to prevent the price on existing AS Offers from being increased. The MMS shall receive and validate these offers. Requirement - All criteria for validation of AS Offers (VA8) apply, with the following exceptions: - AS Offers shall not be rejected due to submission after DAM market closure of bid/offer submission. - AS Offers shall be rejected if submitted after the Alert specified deadline. - AS Offers shall be rejected if, for amounts up to the quantity offered before the Alert, the new price of the Offer is higher than the price submitted before the Alert. - New AS Offers shall be rejected if the previously submitted offers are not resubmitted. - Inputs: - AS Offer from QSE - Outputs: - Reason for invalidation and Transaction ID of AS Offer to QSE - Valid offer posted to MIS Certified Area (accessible by applicable QSE only) - Valid offer input to DAM |  |

## Business Sub-Process 6: CRR Day-Ahead Simultaneously Feasibility Test

### CF1 – CRR Day-Ahead SFT

| Requirement ID | CF1 – CRR Day-Ahead SFT |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.1 (2) , 4.5.1 (5), 4.5.1 (6), 4.5.1 (8) 7.1, 7.2, 7.3, 7.9 |
| Traceability to Sub-Process Maps | Simultaneous Feasibility Test |
| Description CRR may have been oversold due to the Network topology difference between the yearly/monthly auction and DAM. The MMS shall complete a Day-Ahead Simultaneous Feasibility Test (SFT) to determine hourly oversold CRR quantities, prior to execution of the DAM. CRR owners can be assigned CRRs through CRR auctions, PCRR allocations; McCamey Area Flowgate Rights allocations, or Bilateral contracts. Each CRR is one of these types: - Point-to-Point (PTP) Option, some of which may be PCRRs - PTP Obligation, some of which may be PCRRs - PTP Option with Refund, all of which are PCRRs - PTP Obligation with Refund, all of which are PCRRs - Flowgate Right (FGR), including a MCFRI Requirement - The SFT shall model the effect of all assigned CRRs on the Day-Ahead Updated Network Model topology. Day-Ahead Updated Network Model shall be built based on the Normal network, Dynamic Ratings, and Outage schedules. - Assigned CRRs that have a source and/or sink at Load Zones or Hubs shall be allocated to electrical buses based on Load Distribution Factor and Hub Distribution Factor respectively. - Sources and sinks of CRRs at Hubs shall be allocated to Hub buses based on Distribution Factors specified in the definition of each Hub and then be further distributed to each electrical bus in that Hub bus on an average basis - For CRR at load zone, if load distribution to an electrical bus and the bus is dead, then the bus’ load shall be distributed to other buses in the zone. For CRR at a bus and the bus is dead, if the disconnected load is defined with a load rollover scheme, the disconnected load shall be rolled over accordingly. If not, the load shall be dropped. If the target bus of the load rollover is also a dead bus, then the fraction of the load rollover to this bus shall be dropped. - PTP options shall be evaluated as the positive power flows on all directional transmission elements, excluding all the negative flows. PTP obligations shall be evaluated as the positive and negative flows on all directional transmission elements. The Flowgate Right (FGR) shall be modeled by reducing the available capacity amount of the Flowgate. - The SFT shall also consider the Contingency List, RAP/SPS and Generic constraints. For base case, the SFT shall use non-linear DC Power Flow for PTP obligations and incremental DC Power Flow for PTP options. For Contingency cases, the SFT shall use incremental DC Power Flow. shows the flow diagram of the basic CRR SFT process. Further details are included in Appendix 3. - With the CRR obligations imposed on the network, if the power flow (nonlinear DC) fails to converge, the process shall stop to allow ERCOT Operators to remedy the possible data problems. The CRR options shall be solved via incremental model. As such, there is no convergence issue. - After SFT execution, Day-Ahead Weighted Shift Factors for settlement points per violated constraint shall be calculated. The Weighted Shift Factors for load zone shall be calculated by using Load Distribution Factors of that zone. The Weighted Shift Factors for Hubs shall be calculated by using Hub Distribution Factors. Figure 3-5 CRR SFT Flow Diagram - Inputs: - Normal network, Dynamic Ratings, and Outage schedules - Contingency List - RAP/SPS - Generic constraints - Load Distribution Factors for load zones - Distribution Factors for Hubs - Point-to-Point (PTP) Option, some of which may be PCRRs - PTP Obligation, some of which may be PCRRs - PTP Option with Refund, all of which are PCRRs - PTP Obligation with Refund, all of which are PCRRs - Flowgate Right (FGR), including a MCFRI - Outputs: - Hourly oversold quantities for each violated constraint - Transmissions limit quantities for each violated constraint - Day-Ahead Weighted Shift Factors for all settlement points per violated constraint |  |

## Business Sub-Process 7: Derating CRR Options Declared for Settlement in Real-Time

### DC1 – Derating CRR Options Declared for RT

| Requirement ID | DC1 – Derating CRR Options Declared for RT |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.5, 4.5.1 (5), 4.5.1 (6), 4.5.1 (8) 7.9 |
| Traceability to Sub-Process Maps | Derating CRR options |
| Description NOIEs could hold PTP Options and PTP Options with refund to be settled in Real-Time. The directional network element flows for PTP Options declared for settlement in Real-Time shall be properly accounted for in determining the available transmission network capacity in the DAM. In the event the available transmission capability in the DAM cannot accommodate all PTP Options declared for settlement in Real-Time, any PTP Option declared for settlement in Real-Time that impacts overloaded directional network elements shall be appropriately derated for DAM modeling purposes only in proportion to that impact. Requirement - In the event the available transmission capability in the DAM cannot accommodate all PTP Options declared for settlement in Real-Time, any PTP Option declared for settlement in Real-Time that impacts overloaded directional network elements shall be appropriately derated for DAM modeling purposes only in proportion to that impact. - The ERCOT Operator shall be able to run the CRR Option Derating prior to DAM. The CRR Options Derating shall use a Weighted Least Square method to derate the CRR Options declared for Real-Time Settlement. The CRR Options Derating shall determine the minimum CRR quantity adjustment to relieve the transmission constraints violations. The CRR derating shall be determined by the MMS where each hour of the DAM study period shall be executed independently. Appendix 4 shows the CRR Derating mathematical problem formulation. Figure 3-6 shows the flow diagram of the CRR Option derating process. Figure 3-6 CRR Options Derating Flow Diagram The above figure shows a procedure that is used in the presence of SPS/RAP in order to correctly account for the action of SPS/RAP. The SFT for Based Case and All Contingencies step determines Transmission constraints (limit and corresponding shift factors) to be used in the Weighted Least-Square Derating of CRR Options step. - Inputs: - PTP Options and PTP Options with Refund that are declared by NOIEs for Real-Time settlement - Normal network, Dynamic Ratings, and Outage schedules - Contingency List - RAP/SPS - Generic constraints - Load Distribution Factors for load zones - Distribution Factors for Hubs (hub is an average of buses in that hub) - Outputs: - CRR options Derated quantities and offer prices to settlements - CRR options Remained quantities for Day-Ahead Network Model |  |

## Business Sub-Process 8: Day Ahead Clearing Process

### CE1 – DAM Pre-processing

| Requirement ID | CE1 – DAM Pre-processing |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.4, 3.5, 4.5.1 (5), 4.5.1 (6) |
| Traceability to Sub-Process Maps | DAM Pre-Process |
| Requirement - ERCOT shall determine the appropriate Load distributions to allocate offers, bids, and source and sink of CRRs at a Load Zone across the Electrical Buses that are modeled with Load in that Load Zone. The default distribution is the State Estimator hourly distribution for the seven days before the Operating Day. If ERCOT decides, in its sole discretion, to change this distribution for reasons such as anticipated weather events or holidays, ERCOT shall select a State Estimator distribution from a proxy day reasonably reflecting the anticipated distribution in the Operating Day. - The MMS shall provide an option to allow ERCOT to change this distribution. - Offers, bids, and sources and sinks of CRRs at Load Zones shall be allocated to electrical buses based on Load Distribution Factors. - Offers, bids, and sources and sinks of CRRs at Hubs shall be allocated to Hub buses based on Distribution Factors specified in the definition of each Hub and then be further distributed to each electrical bus in that Hub bus on an average basis. - For offers, bids, and sources and sinks of CRRs at load zone, if load distribution to an electrical bus and the bus is dead, then the bus’ load shall be distributed to other buses in the zone. - For offers, bids, and sources and sinks of CRRs at bus and the bus is dead, if the disconnected load is defined with a load rollover scheme, the disconnected load shall be rolled over accordingly. If not, the load shall be dropped. If the target bus of the load rollover is a dead bus, then the fraction of the load rollover to this bus shall be dropped. - Inputs: - Load Distribution Factors for load zones - Distribution Factors for Hub - Energy offers and energy bids at Load Zones for each hour - CRRs that have a sources and/or sink at Load Zones for each hour - Energy offers and energy bids at Hubs for each hour - CRRs that have a sources and/or sink at Hubs for each hour - Settlement point relationships to buss - Outputs: - Energy offers and energy bids by bus for each hour - CRRs by bus for each hour |  |

### CE2– Initial Commitment Status

| Requirement ID | CE2- Initial Commitment Status |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.9.1 (4), 4.5.1 (4)(c) |
| Traceability to Sub-Process Maps | DAM Pre-Process |
| Description - DAM shall use the historical commitment data, the On-line and Off-line status for the current Operating hour from EMS and the COP status for remaining hours of the current Operating Day to project the initial commitment status at the beginning of the next Operating Day. - The DAM shall retrieve both the current Resource commitment status (On-line or Off-line) and the historical Resource commitment status from EMS. The historical commitment status data include: - Number of start up of the Operating Day until the end of previous hour. - If the Resource was On-line, the number of hours it has been On-line until the end of previous hour. - If the Resource was Off-line, the number of hours it has been Off-line until the end of previous hour. |  |

### CE3 – Network Security Monitor

| Requirement ID | CE3 – Network Security Monitor |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.1 (4)(c) |
| Traceability to Sub-Process Maps | Network Security Monitor |
| Description - The Network Security Monitor (NSM) function shall be used in the solution process of Day-Ahead Market Clearing Engine (MCE) and Reliability Unit Commitment (RUC). NSM evaluates the security of the network subject to the MW dispatch provided by Network Constrained Unit Commitment (NCUC) for both the base case (intact) system and contingencies. - In the DAM market, the schedules dispatch provided by NCUC include: - Generation dispatch - Demand dispatch - CRR dispatch - The network security constraints evaluated in NSM include: - Transmission constraints - Transfer limits on energy flows through the ERCOT Transmission Grid, e.g., thermal or stability limits. These limits must be satisfied by the intact network and for certain specified contingencies. - Thermal constraints - protect transmission facilities against thermal overload. - Branch Group constraints - protect the ERCOT Transmission Grid against transient instability, dynamic stability or voltage collapse. - Generic constraints – Predefined linear constraints on network flow. - Power flow constraints – the energy balance at required Electrical Buses in the ERCOT Transmission Grid must be maintained. - The NSM consists of the following main components: - Network Data Update Retrieves the network model prepared by the preprocessor and imposes on it the latest NCUC generation and demand dispatch as well as PTP obligations to establish the modified base case. The DAM Network topology used by NSM shall be built based on the Normal network and Outage schedules. All power flow computations shall consider a lossless model while satisfying power flow constraints. Transmission constraints shall be based on Dynamic Ratings. - Modified Base Case Power Flow Solution Performs non-linear DC power flow solution on the modified base case prepared by Network Data Update and computes the modified base case flows. - Contingency Topology Processor Prepares the Final Contingency List, Violation Check List and Generator Allocation List for the DC Contingency Analysis. - Incremental Analysis Performs Incremental Analysis by imposing options and contingencies based on the lists prepared by the Contingency Topology Processor and determines the modified flows. If a SPS triggering condition is satisfied in a contingency, the contingency is dropped (i.e., it is assumed that SPS clears all constraint violations). - Constraint Data Processing Computes the shift factors (sensitivities) for the violated transmission constraints to be used by NCUC. Figure 3-7 shows the flow diagram of the NSM process. Figure 3-7 NSM Flow Diagram - Inputs: - Network model, Equipment Ratings, and Outage schedules - Contingency List, RAP/SPS - Generic constraints - Cleared DAM Energy Bids and PTP Obligation Bids by bus - Cleared Three-Part Supply Offers, DAM Energy-Only Offers, and CRR Offers - User interfaces to control: - Constraints - Contingencies - Equipment monitoring and enforcement - Outputs: - Critical transmission constraint limits - Control shift factors |  |

### CE4 – DAM Clearing Engine

| Requirement ID | CE4 – DAM Clearing Engine |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.8 (6), 3.18, 4.1, 4.5.1 (1), 4.5.1 (3), 4.5.1 (4), 4.5.1 (5), 4.5.1 (6), 4.5.1 (7) |
| Traceability to Sub-Process Maps | DAM Clearing Process |
| Description The Day-Ahead Market (DAM) shall provide a platform to buy and sell Ancillary Services, Congestion Revenue Rights, and forward financial energy. The DAM shall simultaneously clear AS, CRR, and energy transactions. Participation in the DAM shall be voluntary, except for RMR Units. Requirement - The DAM clearing engine shall use a multi-hour mixed integer programming algorithm to maximize bid-based revenues minus the offer-based costs over the Operating Day, subject to security and other constraints, and ERCOT Ancillary Service procurement requirements. Security constraints shall result from the Network Security Management engine as specified in CE3. The other constraints shall be based on the characteristics of each bid or offer and each Resource. All products in the DAM shall be cleared by hour for each hour of the Operating Day. - The Day-Ahead Locational Marginal Price (LMP) for each Electrical Bus for each hour of is the Shadow Price for that Electrical Bus for the hour as determined by the DAM Algorithm. Block offers shall not set the LMP. - The Day-Ahead Market Clearing Price for Capacity (MCPC) for each hour for each Ancillary Service is the Shadow Price for that Ancillary Service for the hour as determined by the DAM algorithm. - If the Ancillary Service Offers can’t meet the Ancillary Service Plan requirement, the DAM clearing engine shall perform a price run and preserve AS Plan requirements in the following order of priority: - Reg-Up; - Reg-Down; - Responsive Reserve; and - Non-Spin - If the Day-Ahead MCPC cannot be calculated by ERCOT, the Day-Ahead MCPC for the particular Ancillary Service is equal to the Day-Ahead MCPC for that Ancillary Service in the same Settlement Interval of the preceding Operating Day. - DAM clearing amount shall be distributed proportionally among price tied offers, if cleared. Figure 3-8 shows the flow diagram of the overall Market Clearing process. Figure 3-8 DAM Flow Diagram - The DAM Clearing Engine consists of following steps: - Pre-processing: Reads in bid/offer data, network data, constraints and requirements and processes the data for use by the remaining sub functions. - Initial Unit Commitment (IUC): Optimizes the commitment, energy and AS dispatch schedule given the various constraints/requirements and generic constraints but without considering any of the transmission constraints. - Network Security Monitor (NSM): Evaluates network security given the energy schedule from either IUC or NCUC. Generates transmission constraint equations describing the changes required to the energy dispatch to remove transmission constraint violations. - Network Constrained Unit Commitment (NCUC): Optimizes the commitment, energy and AS dispatch schedule given the various constraints/requirements including the network constraint equations generated by NSM. - The NSM and NCUC iterate in the left hand side of the Figure until one of the following conditions is satisfied: There are no network constraint violations The remaining transmission constraint violations cannot be cleared The maximum number of iterations allowed has been reached. - SPS Triggering Test: Using the solved NCUC generation, invoke NSM for all contingencies to test the SPS triggering conditions (contingency specific SPS and equipment-based SPS). Any contingencies that trigger SPS shall be ignored in the subsequent NCUC-NSM iterations - Network Security Monitor (NSM): Invoke NSM for the base case and all contingencies without SPS triggering as determined at Step 6 at each time step in the study period to identify network constraints to be enforced in the NCUC solution - Network Constrained Unit Commitment (NCUC): Invoke NCUC to determine the revised generation schedule as impacted by enforcing the additional network constraints - The NSM and NCUC iterate in the right hand side of the Figure to ensure all transmission constraints are satisfied. - DAM shall model following Input Data: - Valid DAM Energy Bids and PTP Obligation Bids - Valid Three-Part Supply Offers, DAM Energy-Only Offers, CRR Offers - Valid AS Offers of Regulation Down, Online AS and Non-spin Offline reserves where Online AS consists of Regulation up, Responsive Reserve and Non-Spin Online Reserves. - For Three-Part Supply Offers, the start-up cost offer includes Resource’s hot, intermediate, and cold start-up cost offers. - Three-Part Supply Offers exclusive/inclusive flag. The energy offer curves can be bid exclusive or inclusive with on-line AS and Regulation down. The default value for the flag is inclusive. - For any offer, except Three-Part Supply Offers, if First Hour and Last Hour are different, the offer shall be treated as a multi-hour block offer which means the cleared quantity shall be the same for all the hours in the block, - For a Three-Part Supply Offer, there is not a multi-hour offer even if the First Hour and the Last Hour are different for the Three-Part Supply offer. - For a Three-Part Supply Offer, if the first price-quantity pair is greater than LSL, the Resource will not be awarded a quantity less than the quantity of the first price-quantity pair. - For DAM Energy Bids and DAM Energy-Only Offers, if the first price-quantity pair is greater than zero, the first price-quantity pair price will be extended to cover the range between zero and the first price-quantity pair quantity. - AS Plan (original Requirement for each AS type) - Self-arranged AS quantities - Transmission constraint limits and shift factors resulting from NSM or generic constraints entered by ERCOT Operator - Resource constraint information – LSL, HSL, Minimum On-Line time, Minimum Off-Line time, configuration, etc. - Registered Combined Cycle units information - Registered Split Generation Resources information - Block Offers - Resource On-line/Off-line status and last time the status changed from EMS - Resource On-line/Off-line status from current day COP - The DAM shall model following Constraints: - Power balance constraints - The sum of all the cleared energy offers is equal to the sum of all the cleared energy bids. - Transmission constraints: Transfer limits on energy flows through the ERCOT Transmission Grid, e.g., thermal or stability limits. These limits must be satisfied by the intact network and for certain specified contingencies. These constraints can present: - Thermal constraints – protect transmission facilities against thermal overload. - Branch Group constraints – protect the ERCOT Transmission Grid against transient instability, dynamic stability or voltage collapse. - Generic constraints – Predefined linear constraints on network flow. - AS Requirement constraints (includes constraints resulting from AS plan): - Ancillary Service needs for each Ancillary Service include the needs specified in the Ancillary Service Plan that are not part of the Self-Arranged Ancillary Service Quantity and that must be met from available DAM Ancillary Service Offers while co-optimizing with DAM Energy Offers. - The DAM shall not buy more of one Ancillary Service in place of the quantity of a different service. - The amount of Load Resources on high-set under-frequency relays procured to provide RRS is limited to 50% of the total ERCOT RRS requirement. The limit shall be able to be reduced by the ERCOT Operator, if ERCOT believes that this amount shall have a negative impact on reliability or if this limit would require additional Regulation to be deployed. - Resource output constraints (Resource Maximum and minimum constraints.): - For hours when both Three-Part Supply Offers and on-line Ancillary Service Offers are offered inclusive of each other, - If only energy offer is cleared from a Resource: The cleared energy offer, if cleared from the Energy Offer Curve of a Three-Part Supply Offer, shall observe the Resource’s LSL and HSL, i.e., higher than or equal to LSL and lower than or equal to HSL. - If only AS offers are cleared from a Resource: The sum of the awarded Ancillary Service capacities for each Resource must be less than or equal to the offer capacity and must be within the Resource limits specified in COP and Section 3.18, Resource Limits in Providing Ancillary Service, and the Resource parameters as described in Section 3.7, Resource Parameters. - If both energy offer and AS offer(s) are cleared from a Resource: The sum of cleared energy offer, Reg-Up offer, Responsive Reserve offer, Non-Spin on-line offer from a Resource should be less than or equal to the Resource’s HSL. The cleared energy offer minus the cleared Reg-Down offer should be greater than or equal to the Resource’s LSL. - For Hours when only AS are offered, the sum of Reg-Up, Reg-Down, Responsive Reserve and Online Non-Spin provided must be less than or equal to the HSL for Generation Resources and LPC for Load Resources minus the LSL for Generation Resources and MPC for Load Resources. - For hours when both Three-Part Supply Offers and on-line Ancillary Service offers are offered exclusive of each other, then either: - The sum of the AS shall be zero, or - AS shall be dispatched. In this case energy shall be dispatched at the resource low limit (LSL) and the Resource startup cost and minimum generation cost specified in Startup and Minimum Energy Offer of the Three-Part Offer shall be applied. - Online AS and Reg-Down shall only be supplied when the resource is online and offline Non-Spin shall only be supplied when the resource is offline. This applies to both generator and load resources. For generation resources, the online and offline commitment status must satisfy the resources' minimum on-line time and minimum off-line time constraints including those times when only AS is bid. For load resources, the online and offline commitment status must satisfy the resources' minimum and maximum interruption time and the minimum restoration time constraints. - If only AS is offered, then the dispatch of On-line reserves shall require that the resource be considered On-line with an energy dispatch of 0 MW. If Off-line Non-Spin is dispatched then the resource shall be considered Off-Line. The commitment schedule shall obey the minimum run time and minimum down time constraints. - For Off-line Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Generation Resources and LPC minus MPC for Load Resources - For Responsive Reserve Service: - The amount of RRS awarded to a Generation Resource shall be less than or equal to 20% of thermal unit HSL for an Ancillary Service Offer and must be less than or equal to 10 times the Emergency Ramp Rate. - The amount of RRS awarded to a Hydro-powered Resources operating in the synchronous condenser fast-response mode shall be less than or equal to the Resource’s proved 20-second response (which shall be 20% of the HSL if AS Offer is inclusive to its Three-Part Supply Offer and 100% of the HSL if AS Offer is not inclusive to its Three-Part Supply Offer). - For any hydro-powered Resource with a five percent droop setting operating as a generator, the amount of RRS awarded shall never be more than 20% of the HSL. - The amount of RRS awarded to a Load Resource shall be less than or equal to the LPC minus the MPC. - Resource operational constraints (min/max on-line time, min off-line time, configuration.): - Min on-line time: If a resource is up, it cannot be shut down until the up time is greater or equal to the minimum up time. - Max on-line time: If a resource is up, the up time shall be less than or equal to the maximum up time - Min off-line time: If a resource is down, it shall not be brought up until the down time is greater or equal to the minimum off-line time. - Maximum daily start-up: A resource shall only start up less than or equal to the Maximum daily start-up. - Combined Cycle Units: Combined cycle units are defined by a set of configurations (or modes) and the allowed transitions between the modes and the off state. Each mode has a set of unit parameters as described in the ST2. The minimum on-line time and off-line time are defined for the entire combined cycle unit. The DAM clearing engine shall determine for each time point, which mode is operating and the corresponding mode dispatch. The network model in the MMS functions shall model the various subunits of the combined cycle unit - Split Resources: For Split Generation Resources, each QSE representing an individual Split Generation Resource can independently submit Energy Offer Curves and Three-Part Supply Offers. Split resources shall be committed/decommitted at the same time. Split resources can be dispatched independently based on their respective energy offers. - Other constraints - Linked offers: The DAM cannot select any one part of that Resource capacity to provide more than one Ancillary Service or to provide both energy and an Ancillary Service in the same Operating Hour. The DAM can select part of that Resource capacity to provide one Ancillary Service and another part of that capacity to provide a different Ancillary Service or energy in the same Operating Hour. - On-line Reserve Offer: On-line Reserve Offer provides a combined offer curve for Reg-up, Responsive Reserve, and On-line Non-Spin reserve. The sum of reserves dispatched from a capacity offer must be less than the quantity of the offer. If the price is not supplied for a given reserve type, then that reserve shall not be available for that capacity offer - Responsive Reserve Offer: The sum of Responsive Reserve shall be less than or equal to the maximum amount of Responsive Reserve available from the Resource - Fixed and Variable AS Offer: The dispatches from each reserve type for each capacity offer shall be constant for hours between the start and stop times and shall be variable or fixed (to the capacity offer quantity) dependent on the block flag (Fixed or Variable). - Fixed Block AS Offers: Fixed Block Ancillary Service Offers for a Load Resource – blocks shall not be cleared unless the entire quantity block can be awarded and, for linked AS Offers, all of the awarded AS shall be assigned to a single service. - Block CRR offers and bids: Block CRR Offers and PTP Obligation Bids- blocks shall not be cleared unless the entire time block can be awarded. - Variable quantity block energy and bids: energy blocks shall be cleared to the same for the entire time block. - Offers of PTP Options declared to settle in RT – PTP Options shall be less than or equal to the Limits determined by the CRR Option Derating. - At the end of the DAM study period, the operational constraints shall be enforced assuming that Resources with unspecified commitment status are Off-line for all hours after the study period. - The DAM system shall not model resource ramp rate limits and start up ramp limit constraints. - The DAM shall not assume any self-commitment due to COP. - The DAM shall not consider any Self-Schedule energy. - Awarded energy shall be real number. - Awarded AS quantities shall be rounded to nearest first decimal point - Output to NSM: - Cleared DAM Energy Bids and PTP Obligation Bids by bus - Cleared Three-Part Supply Offers, DAM Energy-Only Offers, Offers of PTP Options declared to settle in Real-Time, and AS Offers by bus - Output to Post Processor: - Cleared DAM Energy Bids and PTP Obligation Bids by bus - Cleared Three-Part Supply Offers, DAM Energy-Only Offers, Offers of PTP Options declared to settle in Real-Time, and AS Offers by bus - The capacity offer amount cleared for each AS type - Hourly LMPs for each bus - Hourly Shadow Price for each constraint - MCPC for each AS type |  |

### CE5 – Tie-Breaking Rule

| Requirement ID | CE5 – Tie-Breaking Rule |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | N/A |
| Traceability to Sub-Process Maps | DAM Clearing Process |
| Description When two or more Resources offer the same price for blocks of their price curve, then it is possible that there will be more than one optimal (least cost) solutions. These solutions will have different dispatches within the equal price blocks. The units that can have different optimal dispatches are known as marginal resources. Requirement - The DAM shall use the following approach to generate a unique dispatch: the DAM Market Clearing Engine shall break the tie by prorating the dispatch schedules among all the marginal Resources. The proration shall be based on the size of the MW block with equal price offers. Only the part of price curves within Resources’ available region shall be used. |  |

### CE6 – Constraint Penalty Function

| Requirement ID | CE6 - Constraint Penalty Function |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.2 (1)(d) |
| Traceability to Sub-Process Maps | DAM Clearing Process |
| Requirement - DAM shall apply penalty factors to violations of the power balance and security constraints to the NCUC objective function in addition to the offer-based cost. The penalty factors shall be configurable by the authorized ERCOT Operators. - DAM shall apply different penalty factors for different types of violations: - System Deficit Generation / Surplus Generation (i.e. Under Generation / Over Generation) - Transmission Base Case Constraints kV Level of overloaded element (for transformers, the higher kV level is used) - Transmission Contingency Constraints kV Level of overloaded element (for transformers, the higher kV level is used) - Transmission Generic Constraints - Resource Constraints - Reg-Up - Reg-Down - Responsive Reserve Service - Resource Non-Spin |  |

### CE7 – Post-Processing

| Requirement ID | CE7 – Post-Processing |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.3 |
| Traceability to Sub-Process Maps | Post Processing |
| Requirement - After DAM clearing, awarded MW for offers, bids, source and sink CRRs at Load Zone and Hub shall be aggregated by the MMS based on cleared MW by bus. - The awarded Ancillary Services and Energy for Split Generation Resources shall be separated and notify to each represented QSE. - DA Settlement Point Price shall be calculated based on the Nodal LMPs and Distribution Factors. The methodology is defined in Section 4.6.1 of the ERCOT Nodal Protocols. - Inputs: - Load Distribution Factors - Settlement Point relationships to buses - Cleared DAM Energy Bids and PTP Obligation Bids by bus - Cleared Three-Part Supply Offers, DAM Energy-Only Offers, CRR Offers, and AS Offers by bus - Hourly LMPs for each bus - Hourly Shadow Price for each constraint - MCPC for AS - Outputs: - DA Settlement Point Price for each Settlement Point - Total quantity in MWh of AS Offers received for each AS type - Total quantity in MWh bought for each Settlement Point - Total quantity in MWh sold for each Settlement Point - Aggregated AS Offer Curve for all offers for each AS type |  |

### CE8 – Notification of DAM Awards

| Requirement ID | CE8 – Notification of DAM Awards |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.2.1.1 (5) 4.5.3 (1) |
| Traceability to Sub-Process Maps | QSE Notification of Awards |
| Description After the DAM clearing engine is completed, QSEs shall be notified by the MMS of their awarded offers and bids, so that they may plan appropriately for the Operating Day and are aware of their financial obligations. Specifically, the appropriate QSEs shall be notified of: Requirement - QSEs shall be notified of the following: - Awarded AS Offer: - Resource ID - MW awarded - AS Type - Price - Hours - Awarded Energy Offer (from Three-Part Offer and Energy-Only Offers): - Resource ID (except for Energy-Only Offers) - MW awarded - Settlement Point - Settlement Point Price - Hours - Awarded DAM Energy Bid - MW awarded - Settlement Point - Settlement Point Price - Hours - Awarded CRR Offer - CRR ID - Number of CRRs awarded - Source Settlement Point - Sink Settlement Point - Price - Hour - Awarded PTP Obligation Bid - Number of PTP Obligations awarded - Source Settlement Point - Sink Settlement Point - Price - Hours - Inputs: - Results of DAM Clearing Engine - Outputs: - Awarded bids and offers to MIS Certified Area (accessible by appropriate QSE only) |  |

### CE9 – Notification of DAM Results

| Requirement ID | CE9 – Notification of DAM Results |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.3 (2) |
| Traceability to Sub-Process Maps | Post Market Information |
| Description After the DAM clearing engine is completed, the QSEs shall be notified by the MMS of the overall results of the DAM so that everyone can analyze the status of the DAM, plan for the Operating Day and plan for future DAMs. Requirement - For each hour of the DAM, the following shall be posted: - DA MCPC for each AS type - Proration of Load Resource RRS - DA Settlement Point Price for each Settlement Point - DA LMP for each bus - Shadow Prices for each binding constraint - Total quantity in MWh of AS Offers received for each AS type - Total quantity in MWh bought for each Settlement Point - Total quantity in MWh sold for each Settlement Point - Aggregated AS Offer Curve for all offers for each AS type - The MMS System shall calculate the Aggregated AS Offer Curve through aggregating all valid AS offers. Each Ancillary Service type shall have an independent aggregated offer curve. The total aggregated offers can exceed the total available offered AS capacity due to the linked Ancillary Service offers - All output posting values shall be able to be manually modified by ERCOT. - DA MCPCs and LMPs shall be able to be posted with notes, to inform the public of conditions that cause the prices to be questionable. - Inputs: - Results of DAM Post process - Outputs: - Results of DAM to MIS Public Area |  |

### CE10 – Control of DAM Clearing Process

| Requirement ID | CE10 – Control of DAM Clearing Process |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.1.2 |
| Traceability to Sub-Process Maps | DAM Clearing Process |
| Requirement The following functionality shall be provided by the MMS: - Under normal circumstances, ERCOT should begin execution of DAM at 1000. Execution of the DAM shall be manually initiated by the ERCOT Operator - Execution of the DAM shall be able to take place at any time during the Day-Ahead, as there may be circumstances under which DAM execution needs to be delayed. - If the event of temporary deviation from the normal timing, an Alert shall be issued to all QSEs with: - Details of the affected timing and procedures - Details of any interim requirements - An estimate of the period for which the interim requirements apply - Reasons for the temporary variation - DAM execution can be aborted after it has been started, due to circumstances such as the discovery of invalid inputs, emergency conditions, equipment failure, etc. - In the event of DAM abort, an Alert shall be issued to all QSEs with: - Details of the affected timing and procedures - Details of any interim requirements - An estimate of the period for which the interim requirements apply - Reasons for the temporary variation - When execution of the DAM clearing engine is aborted prior to completion, the DAM clearing engine shall not award any bids or offers or set any LMPs. - The DAM execution controller shall support re-execution of the DAM from the beginning or continuation from the last aborted module. - ERCOT shall be able to manually invoke DAM clearing process in order to analyze and review results at different stages of the execution. - The DAM Clearing Engine shall be able to be run in “study mode,” which shall report results to the ERCOT Operator but shall not award or publish any bids or offers. - Inputs: - Initiation of DAM execution by ERCOT Operator - Abort of DAM execution by ERCOT Operator - Outputs: - Signal to DAM Clearing Engine to start - Signal to DAM Clearing Engine to abort - Alert and notification of QSEs regarding a temporary deviation from the normal timing, if applicable - Alert and notification of QSEs regarding an abort of DAM, if applicable |  |

## Business Sub-Process 9: AS Evaluation in Adjustment Period

ERCOT shall evaluate Ancillary Service requirements and capacity sufficiency throughout the Adjustment Period and Operating Period and procure Ancillary Services in the Adjustment Period for:

- increased need of Ancillary Services capacity above that specified in the Day-Ahead

- replacement of Ancillary Services capacity that is undeliverable due to transmission constraints

- replacement of Ancillary Services capacity due to failure to provide

### AE1 – Increased AS Obligation

| Requirement ID | AE1 – Increased AS Obligation |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 6.4.8.1 (1), 6.4.8.1.1 (1), 6.4.8.2 (4) |
| Traceability to Sub-Process Maps | Increased AS obligation |
| Requirement - If the ERCOT Operator determines in the Adjustment Period that more Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead Ancillary Services Plan, the MMS shall recalculate a new AS Obligation for each QSE. - The AS Obligation shall allocate additional Ancillary Service Obligations to QSEs using the same percentages as the original Day-Ahead allocation of Ancillary Service Obligations. - The MMS shall notify each QSE of its increased Ancillary Service Supply Obligation for each service for each recalculated hour. - Inputs: - Revised AS Plan from ERCOT - Hourly LRS for each QSE for the same hour and day of the week, for the most recent day for which Initial Statements are available from Settlements - Outputs: - AS Obligation notification to QSEs |  |

### AE2 – Validation of COP Changes

| Requirement ID | AE2 – Validation of COP Changes |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.9.2 6.4.8.1 (2) 6.4.8.1.2 (3) |
| Traceability to Sub-Process Maps | AS Substitution Feasibility Check; Replacement of Undeliverable AS due to Transmission Constraint/Failure to Provide |
| Requirement - A QSE cannot change the quantity provided of each type Ancillary Services awarded through the ERCOT procurement process or the aggregate amount of Self-Arranged Ancillary Services (by Ancillary Service type) from the DAM. When a QSE requests to change of the specific Resources supplying Ancillary Services, by modifying its Current Operating Plan (COP), ERCOT Operator: - Shall be alarmed of this change and - Shall determine if the requested change adversely affects the deliverability of the Ancillary Service(s) - Two computer functions shall be provided to support this requirement: - The COP Monitor: alarm ERCOT Operators of changes in the COP related to Ancillary Services. - The Delivery Evaluation function: The Delivery Evaluation function provides the ERCOT Operator with the capability of evaluating the network security under various “what if” scenarios with Ancillary Service Schedule activation. - These two functions are described in Requirements AE3 and AE4. - If the substitution is deemed infeasible by ERCOT or the QSE informs ERCOT that the Ancillary Services capacity needs to be replaced, then ERCOT shall procure, if in its sole discretion it finds that the service is still needed, the Ancillary Services capacity required using Supplemental Ancillary Services Market (SASM) described in SA1. - Inputs: - Current Operating Plans - AS Trade - Self-Arrangements - Awarded AS Offers - Outputs: - Status of AS Sufficiency - AS capacity that are undeliverable (resource and amount) |  |

### AE3 – COP Monitor

| Requirement ID | AE3 – COP Monitor |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.9.2 6.4.8.1 (2) |
| Traceability to Sub-Process Maps | AS Substitution Feasibility Check; Replacement of Undeliverable AS due to Transmission Constraint/Failure to Provide |
| Requirement - The COP Monitor shall monitor the QSE’s COP and alarm the ERCOT Operator when the COP changes in Adjustment Period. The following types of changes can be alarmed: - Resource On-Line/Off-Line status - HSL and LSL - Amount and type of Ancillary Service allocated - The COP monitor shall be executed automatically whenever a QSE requests to change its COP. The outputs of this process are the latest COP changes. GP&L Comment: Given the requirement for the COP monitor shown here and in section 3.9.2(7) of the protocols, can QSEs ignore Section 3.9(5) of the protocols which states “To reflect changes to a Resources’ capability, each QSE shall report by exception, changes to the COP for all hours after the Operating Period through the rest of the Operating Day.”??? - Inputs: - Current Operating Plans - Types of changes to be alarmed. - Alarm thresholds - Outputs: - COP Changes |  |

### AE4 – Delivery Evaluation Function

| Requirement ID | AE4 – Delivery Evaluation Function |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.9, 5.5.2 (7) 6.4.8.1 (1) 6.4.8.1.2 (3) 6.4.8.1.3 (2) |
| Traceability to Sub-Process Maps | AS Deliverability Evaluation, Resource Substitution Feasibility Check; COP and AS Schedule Evaluation |
| Requirement - The Delivery Evaluation function (DEF) is a tool to be used by the ERCOT Operators throughout the Adjustment Period and Operating Period on demand or according to a predefined schedule to determine if certain Ancillary Service capacities or their replacement are deliverable. The following diagram in Figure 3-9 shows the processes and workflow that make up the DEF. Figure 3-9 DEF Flow Diagram The DEF process has the following steps: - The ERCOT Operator retrieves an HRUC save case. By default this shall be the latest available save case. - The ERCOT Operator retrieves the current COP. The HRUC save case and COP retrieval initializes the DEF data. - The ERCOT Operator modifies the data to specify the scenario of the test. The operator shall be able to modify any of the resource-dependent input data. Specific screens shall be available to specify: - additional load by zone and/or hub - commitment/decommitment of generators - changes in interchange - which types of reserves to activate - the study horizon - The input data of the NCUC shall be modified to include these changes. - Run the NCUC function with the commitment fixed to that specified in the COP. The NCUC function shall do an economic dispatch over the study horizon and determine the dispatch. - GP&L Comment: Referring to Step 4 of the Delivery Evaluation Function /DEF (3.9.4 AE4), will the NCUC economic dispatch model Resources in the same way as SCED or will it use the more generic model of RUC? In particular, will it model DSR units with an Output Schedule? If not, the results may not be as accurate and as useful as expected. - The NSM function shall evaluate the dispatch from the NCUC function and determine if the Ancillary Service Capacity under evaluation is deliverable. If not, NCUC shall generate constraint equations to specify how the dispatch needs to be changed so the transmission constraints are met. - The NCUC and NSM iterate until all transmission constraints are met, or there is no possible improvement possible in the amount of violations, or the maximum number of iterations is reached. - Following convergence of the NCUC and NSM iteration, any infeasibility shall be reported. A suggestion plan shall be prepared giving the resources that can be used to relieve the transmission constraints based on the shift factors calculated by NSM. The details of requirements of the NCUC and NSM processes and the HRUC function can be found in the Texas Nodal MMS Software Requirement Specification for RUC. - Inputs: - HRUC Save Case - COP - ERCOT Operator Manual updates - System changes - Outputs: - Ancillary Service Capacity Deliverability - Transmission Constraint Violations - Suggested Plan |  |

## Business Sub-Process 10: Supplemental Ancillary Service Market (SASM)

### SA1 – SASM Clearing Engine

| Requirement ID | SA1 – SASM Clearing Engine |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 3.18, 6.4.8.2, 6.4.8.2.2 |
| Traceability to Sub-Process Maps | SASM Clearing Process |
| Requirement - A SASM shall only be run during the Adjustment Period for the ERCOT Operator specified Study Period to procure additional Reg-Up, Reg-Down, Responsive Reserve, and Non-Spinning Services for the reasons, and in the amounts, specified in NP 6.4.8. - SASM study period shall be specified by the ERCOT Operator. The end time of SASM shall not later than the end time of the last DAM run - AS requirements not awarded by the SASM shall be sent to the HRUC. The HRUC process shall procure insufficient AS. - SASM shall procure the additional quantity required of each Ancillary Service, less the quantity self-arranged, if applicable. SASM shall not buy more of one Ancillary Service in place of the quantity of a different service. - The SASM shall select Ancillary Service offers submitted by QSEs that minimize the overall cost of these Ancillary Services. For each of these Ancillary Services, if selection of the Resource offer exceeds ERCOT’s required Ancillary Service quantity, then SASM shall select a portion of the Resource offer to meet the Ancillary Service quantity required. For Load Resources offering a block of capacity, SASM shall ignore the offer unless the entire block can be accepted. - If a QSE has submitted offers of the same Resource capacity for more than one Ancillary Service (sometimes called linked offers), SASM shall not select any one part of that Resource capacity to provide more than one Ancillary Service in the same Operating Hour. SASM can select part of that Resource capacity to provide one Ancillary Service and another part of that capacity to provide a different Ancillary Service in the same Operating Hour. - SASM shall not consider AS offers from a list of the ERCOT Operator specified Resources with Resources capacity that has been determined as undeliverable. - SASM shall respect the maximum AS capacity available for procurement specified by the ERCOT Operator. - SASM shall model the same AS constraints specified in DAM (CE4). The SASM shall ignore energy constraints and assume the unit’s generation schedule is zero. - The SASM shall respect the Resource’s HSL, LSL and AS schedules from COP in determining the amount of AS available from the resource. - AS schedules from COP shall not be reduced by SASM. - The SASM shall retrieve the Resource On-Line/Off-Line status from COP. If the Resource’s status is On-Line in the COP, the Resource shall only provide the On-Line AS and Reg-Down. If the Resource’s status is Off-Line and reserved for Non-Spin in the COP, the Resource shall only provide the Off-Line Non-Spin. If the Resource’s status is Off-Line but available to be online in the COP, the resource shall be able to provide either Off-Line Non-Spin or On-Line AS and Reg-Down based on optimization. - SASM shall not model Resource’s min/max online time and min off--line time constraints - The SASM MCPC for each hour for each service shall be the Shadow Price for the corresponding Ancillary Service constraint for the hour as determined by the SASM algorithm. - The SASM engine shall not clear more than the total requested AS amount for each type of AS. - AS awards shall be distributed proportionally among tied offers, if cleared. - AS awarded quantities shall be rounded to nearest first decimal point. - The SASM shall allow ERCOT Operator approve SASM results. - If an AS offer has been partially cleared in DAM and has not expired for SASM, then SASM shall consider the uncleared portion of the AS offer. Any issues related to linking to a three-part energy offer in DAM shall be ignored for SASM—i.e. use the uncleared portion of the AS offer in SASM and assume that there is no impact of any clearing of the three-part energy offer that happened in DAM. - Inputs: - Additional AS requirement quantity for each AS type for each hour of the SASM - Additional AS Obligation for each QSE - AS Offers for SASM - Additional Self-Arranged AS quantities - COP resource data - Outputs: - Awarded AS Offers - SASM Market Clearing Price (MCPC) - Summary Info (SA5) |  |

### SA2 – Validation of Resubmitted AS Offers

| Requirement ID | SA2 – Validation of Resubmitted AS Offers |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.7.2.1 (2) 6.4.8.2.1 |
| Traceability to Sub-Process Maps | Validated AS Offers |
| Description During the Adjustment Period, resubmitted AS Offers shall be input to the MMS. These offers are subject to additional criteria, to prevent the price on existing yet unawarded AS Offers from being increased. Requirement - All criteria for validation of AS Offers (VA8) apply, with the following exceptions: - AS Offers shall not be rejected due to submission after DAM market closure for offer/bid submission. - If ERCOT notifies Market Participants that additional Ancillary Services are needed, only offers that were submitted before the notice are eligible to participate in the SASM; once the notice is given, no further offers are eligible for that SASM. - GP&L Comment: Protocol 6.4.8.2 (2) states that “The SASM process for acquiring more Ancillary Service capacity must use the following timeline with time “X” being the time that ERCOT sends notice to all QSEs of the SASM.” Please note the words “must use”. In that timeline it states that QSEs may resubmit A/S offers for “Time = X + 30 minutes” By the timeline and words “must use”, QSEs have 30 minutes after “X” time (time of notice) to resubmit if they choose. This “X+30” also is demonstrated in the TX MAC timeline. As written, 1b infers that no additional A/S offers will be accepted even if all A/S offers which were not struck in the DAM or an earlier SASM are entered for the current SASM. This is in conflict with 1d below which infers additional A/S offers will be accepted (shall not be rejected). It is also in conflict with Protocol 6.4.8.2.1(1)(b) which states “For any amount of the offer that is greater in quantity than the QSE’s offer that was not selected in a previous market, the incremental amount of the offer may be submitted at any price subject to applicable offer caps and offer floors…” - AS Offers resubmitted for SASM shall be rejected if, for amounts up to the quantity previously offered but not awarded, the new price of the Offer is higher than the price originally submitted. - AS Offers resubmitted for SASM for additional quantity shall be rejected unless AS Offers exist for previously unawarded quantities. - Input: - AS Offer for SASM from QSE (as indicated by SASM flag in AS Offer) - Output: - Reason for invalidation and Transaction ID of AS Offer to QSE - Valid offer posted to MIS Certified Area (accessible by applicable QSE only) - Valid offer input to SASM |  |

### SA3 – Validation of AS Self-Arrangement

| Requirement ID | SA3 – Validation of AS Self-Arrangement |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.4.7.1 (5)(d) |
| Traceability to Sub-Process Maps | Validated AS Self Arrangement |
| Description AS Self-Arrangements, as well as other potential inputs into the SASM, shall be validated by the MMS against the Protocol specified criteria and reported to the QSE. This will provide the QSEs with immediate feedback so that they have as much time as possible to make the decision to either correct their report and resubmit, or not submit the report. Requirement - Validation requirements are the same as VA7. Requirement Exceptions: - AS Self-Arrangements submitted for SASM shall not be rejected due to submission after DAM market closure for offer/bid submission. - AS Self-Arrangements submitted for SASM shall be rejected if submitted after the SASM deadline. - AS Self-Arrangements submitted for SASM shall be rejected if the additional self-arranged quantity submitted by the QSE exceeds the additional AS quantity allocated by ERCOT to that QSE as stated in the SASM notice. - Input: - AS Self-arrangement submitted for SASM (as indicated by SASM flag) from QSE - Output: - Notification to QSE of invalid AS self-arrangement - Notification to QSE that quantity of total self-arrangement is curtailed (in case of excess self-arrangement) - Reason for invalidation and Transaction ID of report to QSE - Valid self-arrangement to MIS Certified Area (accessible by applicable QSE only) - Valid self-arrangement input to SASM |  |

### SA4 – Notification of AS awards

| Requirement ID | SA4 – Notification of AS awards |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 6.4.8.2.3 (1) |
| Traceability to Sub-Process Maps | QSE Notification of AS Awards |
| Description QSEs shall be notified of their awarded offers by the MMS after the SASM clearing engine is completed to plan appropriately for the Operating Day and to be made aware of their financial obligations. Requirement - The appropriate QSEs shall be specifically notified of (after SASM completion): - Awarded AS Offer - Resource ID - MW awarded - AS Type - Clearing Price (SASM MCPC) - Hours - Inputs: - Awarded AS Offers from the SASM Clearing Engine - Outputs: - Awarded AS Offers to the MIS Certified Area (accessible by applicable QSE only) |  |

### SA5 - Notification of SASM Results

| Requirement ID | SA5 – Notification of SASM Results |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 6.4.8.2.3 (2) 6.4.8.2.3 (3) |
| Traceability to Sub-Process Maps | Posting Total AS Procurement, Posting MCPC, Posting Aggregated AS Offer Curve |
| Description: After the SASM clearing engine is completed, the QSEs shall be notified of the overall results of the SASM by the MMS to allow everyone to analyze the status of the SASM plan for the Operating Day and plan for future SASMs. Requirement - The following data shall be posted for each hour of the SASM: - SASM MCPC for each AS type - Total AS procured in MW for each AS type - Aggregated AS Offer curve for each AS type - All output posting values shall be capable of being manually modified by ERCOT. - Posting shall have area for notes to inform the public of conditions that cause the prices to be questionable. - Input: - SASM Results - Output: - SASM Results to the MIS Public Area |  |

## Business Sub-Process 11: Price Validation and Correction:

### PC1 – Price Validation and Correction

| Requirement ID | PC1 – Price Validation and Correction |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 4.5.1 (9), 4.5.1 (10), 4.5.1 (11) 4.5.3 (3), 4.5.3 (4) |
| Traceability to Sub-Process Maps | Price validation & correction |
| Description: Price Validation and Correction may be necessary in unusual situations or as directed by the Public Utilities Commission. - The ERCOT Operator shall monitor Day-Ahead MCPCs and Day-Ahead hourly LMPs for errors and shall “flag” to review questionable prices before posting and make notations in the posting and to check for conditions that cause the price to be questionable. - If the Day-Ahead MCPC cannot be calculated by the MMS, then the MMS shall set the Day-Ahead MCPC for the particular Ancillary Service equal to the Day-Ahead MCPC for that Ancillary Service in the same Settlement Interval of the preceding Operating Day. - All DAM LMPs, MCPCs, and Settlement Point Prices shall be final at 1000 of the next Business Day after the Operating Day. - After DAM LMPs, MCPCs, and Settlement Point Prices are final, they shall not be changed unless the Board finds that the DAM LMPs, MCPCs, or Settlement Point Prices are significantly affected by a software or data error. |  |

# Supplementary Requirements

## Performance Requirements

### Market Participant Interface Specific Performance Requirements

- 800 bids/offers in 5 minutes with a response time less than 3 seconds for a single bid/offer submission.

- This assumes that the 800-bids/offer submissions are a representative mix of bulk bid/offer submissions and single bid/offer submissions.

### Market Application Specific Performance Requirements

- Determination of Oversold CRRs

The timing requirement for this process shall be based on the requirement of 3 seconds for performing contingency analysis of ERCOT power system model (5000 buses, 6000 branches, 3000 contingencies).

The key data aspect affecting the performance for this process is the number of distinct source-sink pairs for CRR options, number of power flow buses, number of contingencies analyzed and the number of branches to be monitored. There are no restrictions on the number of CRR obligations in determining this performance requirement.

- CRR Option Derating – 5 Minutes

- DAM - 15 Minutes

DAM has the capability to execute multiple iterations between Network Security Monitoring (NSM) and Network Constrained Unit Commitment (NCUC).

The ERCOT Operator may intervene between the NSM and NCUC executions to manually modify the output of NSM.

The 15-minute requirement is measured on no manual intervention between NSM-NCUC iterations.

The DAM requirements for Linked Ancillary Service Offers, Inclusive-Exclusive Offers, and Combined Cycle Units that were further defined during Phase 1 are now understood to be unique to the ERCOT market.

The ILOG Cplex program has not been benchmarked against these requirements.

It is possible that these requirements may adversely affect the market clearing times to be over 15 minutes.

- SASM - 5 Minutes

# Use Cases

Use cases describe sequence of events happening in a system. A use case is initiated by an actor and it continues with interactions between the actor and the system. Basically a use case is phrased in the form of a dialog between the actor and the system. A use case does not go to details of each event.

## Actor Catalog

The following table lists all the actors used in DAM use cases

Table 5-3 DAM Use Case Actors

| # | Actor | Description |
| --- | --- | --- |
| 1 | QSE Operator | An individual who represents Market Participant in MI registration and Bids/Offers/Trades/Schedules submission process |
| 2 | ERCOT Market Operator | An individual who represents ERCOT for execution and control of market |
| 3 | DAM Clearing Engine | DAM Clearing Engine is executed as a part of DAM Clearing Process. DAM Clearing Engine comprises of three main components; IUC, NCUC and NSM. |
| 4 | DAM Clearing Process | In DAM Clearing Process AS, CRR and energy transactions are cleared simultaneously. DAM Clearing process controls execution of DAM Clearing Engine. |

## Use Case Catalog

The following tables list uses cases for the DAM and the Market Participant Interface

Table 5-4 DAM Use Cases

| Use Case ID | Use Case Name | Brief Description |
| --- | --- | --- |
| DAM-UC1 | Ancillary Services Insufficiency Check | Evaluate AS capacity Insufficiency |
| DAM-UC2 | CRR Day-Ahead SFT | Execute SFT to determine oversold CRR quantity |
| DAM-UC3 | Derating CRR Options Declared for RT | Perform a test to determine if the PTP Options declared for settlement in Real-Time can be accommodated by the available transmission capacity. If these options cannot be accommodated, then the options are derated proportional to their impact on the overloaded transmission elements |
| DAM-UC4 | Network Security Monitor (NSM) | Evaluates network security given the energy and CRR dispatches from either IUC or NCUC. Generates network constraint equations describing the changes required to the energy and CRR dispatches to remove transmission constraint violations. |
| DAM-UC5 | DAM Pre-Processing | Reads in bid/offer data, network data, constraints and requirements and processes the data for use by DAM Clearing Engine. |
| DAM-UC6 | DAM Clearing Engine | Clear DAM Clearing Engine and calculate Market Clearing Prices. |
| DAM-UC7 | Control of DAM Clearing Process | Control of DAM Execution. |
| DAM-UC8 | AS Delivery Evaluation Function (DEF) | Perform Ancillary Service Deliverability Check using Delivery Evaluation Function (DEF). The DEF is used by ERCOT Operator throughout the Adjustment Period and Operating Period on demand or according to a predefined schedule to determine if certain Ancillary Service capacities or their replacement are deliverable. |
| DAM-UC9 | Supplemental Ancillary Service Market (SASM) | Execute SASM to procure additional Ancillary Services capacity to resolve the Ancillary Service deficiency. |
| DAM-UC10 | Ancillary Service (AS) Obligation | Calculate Ancillary Service obligation for each QSE. |
| DAM-UC11 | Increased Ancillary Service (AS) Obligation | Recalculate Ancillary Service obligation for each QSE during Adjustment Period. |
| DAM-UC12 | Post-Processing | Post-processing of output results provided by DAM Clearing Engine. |

Table 5-5 MPI Use Cases

| Use Case ID | Use Case Name | Brief Description |
| --- | --- | --- |
| MMS-UC1 | Login to MPI | Login to the secure Market Participant Interface (MPI) system |
| MMS-UC2 | Retrieve Messages/Alerts | Retrieve messages and alerts from the MMS System. |
| MMS-UC3 | Submit CRR Offer | Submit a CRR Offer. |
| MMS-UC4 | Submit Capacity Trade | Submit a Capacity Trade. |
| MMS-UC5 | Submit Energy Trade | Submit an Energy Trade. |
| MMS-UC6 | Submit PTP Obligation Bid | Submit a PTP Obligation Bid. |
| MMS-UC7 | Submit AS Self Arrangement Report | Submit an AS Self-Arrangement Report. |
| MMS-UC8 | Submit AS Offer | Submit an AS Offer. |
| MMS-UC9 | Submit AS Trade | Submit an AS Trade. |
| MMS-UC10 | Submit DAM Energy-Only Offer Curve | Submit an DAM Energy-Only Offer Curve |
| MMS-UC11 | Submit DAM Energy Bid | Submit a DAM Energy Bid. |
| MMS-UC12 | Submit COP | Submit a COP. |
| MMS-UC13 | Submit HRUC Offer | Submit an HRUC Offer. |
| MMS-UC14 | Submit DC Tie Schedule | Submit a DC Tie Schedule. |
| MMS-UC15 | Submit Output Schedule for DSR and Non-DSR | Submit an Output Schedule for Non-DSR. |
| MMS-UC16 | Submit Incremental/Decremental DSR Offer | Submit an Incremental or Decremental Offer for DSR. |
| MMS-UC17 | Submit an AS Adjustment | Submit an AS Adjustment. |
| MMS-UC18 | Submit Three-Part Supply Offer | Submit a Three-Part Supply Offer (Startup Offer, Minimum-Energy Offer, and Energy Offer Curve). |
| MMS-UC19 | Submit Self Schedule | Submit a Self-Schedule. |
| MMS-UC20 | Update COP for De-Committed Resource | Update COP for a De-Committed Resource. |
| MMS-UC21 | Acknowledge Capacity Trade | Acknowledge a Capacity Trade submitted by QSE |
| MMS-UC22 | Acknowledge Energy Trade | Acknowledge an Energy Trade submitted by QSE. |
| MMS-UC23 | Acknowledge AS Trade | acknowledge an AS Trade submitted by the Buying QSE |
| MMS-UC24 | Query a Submission | query and view submitted bids, trades or offers |
| MMS-UC25 | Cancel a Submission | Cancel a Bid/Offer/Trade/Schedule. |
| MMS-UC26 | Notification of DAM Awards | Notify QSE buyers and QSE sellers about DAM Awards. |
| MMS-UC27 | Notification of DAM Results | Notify QSEs about DAM results. |
| MMS-UC28 | Submit File Exchange Request | Submit an Offer, Bid, Trade or a Schedule using the File Exchange display. |
| MMS-UC29 | Submit External Client Application Request | Submit a request using the QSEs External Client Application. |
| MMS-UC30 | Enable or Disable or Modify RMR Offers by ERCOT Operator | ERCOT Operator to view the RMR offers and enable/disable and/or modify the RMR offers by hour using the Market Operator Interface (MOI) |
| MMS-UC31 | Submit Three-Part Supply Offer for Combined Cycle Mode | Submit a Three-Part Supply Offer for Combined Cycle Mode. |
| MMS-UC32 | Submit Energy Offer in Adjustment Period | Submit an Energy Offer in the Adjustment Period. |
| MMS-UC33 | Alarm ERCOT Operator of COP changes | ERCOT Operator to be alarmed on the Market Operator Interface (MOI) of certain COP changes by the QSE in the Adjustment Period. |

# Protocol Coverage

| Protocol Sub-Section # | Description | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| 3.4 | Load Zones | Full: CE1 |
| 3.5 | Hubs | Full: CE1 |
| 3.7 | Resource Parameters | Partial: 1.4.1 (DAM Inputs/Outputs – Registration) Weekly data not required for DAM |
| 3.7.1.1 | Generation Resource Parameters | Partial: ST2 Weekly data not required for DAM |
| 3.8 | Special Considerations for Split Generation Meters | (6): CE4 |
| 3.9 | Current Operating Plan (COP) | Full: PD2, VA14, AE4 |
| 3.9.1 | Current Operating Plan Criteria | Full: VA14 (4): CE2 (5): ST2 |
| 3.9.2 | Current Operating Plan Validation | Full: VA14, AE2, AE3 |
| 3.14.1 | Reliability Must Run | Partial: ST1 Non-MMS responsibility not covered by DAM |
| 3.18 | Resource Limits in Providing Ancillary Service | Full: SC1, SA1, CE4 |
| 4 | Day-Ahead Operations | No NP Requirement |
| 4.1 | Introduction | Full: CE4 |
| 4.1.1 | Day-Ahead Timeline Summary | Full: PD3 |
| 4.1.2 | Day-Ahead Process and Timing Deviations | Full: CE10 |
| 4.2 | ERCOT Activities in the Day-Ahead | No NP Requirement |
| 4.2.1 | Ancillary Service Plan and Ancillary Service Obligation | No NP Requirement |
| 4.2.1.1 | Ancillary Service Plan | Partial (1,2,6): EMS (5): CE8 AS Plan is ERCOT process |
| 4.2.1.2 | Ancillary Service Obligation Assignment and Notice | Full: PD1 |
| 4.2.2 | Wind-Powered Generation Resource Production Potential | ERCOT Process |
| 4.2.3 | Posting Forecasted ERCOT System Conditions | ERCOT Process |
| 4.2.4 | ERCOT Notice of Validation Rules for the Day-Ahead | ERCOT Process VA13 |
| 4.3 | QSE Activities and Responsibilities in the Day-Ahead | Full: (1a, 1b): PD2 |
| 4.4 | Inputs into DAM and Other Trades | Full: PD2, PD3 |
| 4.4.1 | Capacity Trades | Full: VA1 |
| 4.4.1.1 | Capacity Trade Criteria | Full: VA1 |
| 4.4.1.2 | Capacity Trade Validation | Full: VA1 |
| 4.4.2 | Energy Trades | Full: VA2 |
| 4.4.2.1 | Energy Trade Criteria | Full: VA2 |
| 4.4.2.2 | Energy Trade Validation | Full: VA2 |
| 4.4.3 | Self-Schedules | Full: VA4 |
| 4.4.3.1 | Self-Schedule Criteria | Full: VA4 |
| 4.4.3.2 | Self-Schedule Validation | Full: VA4 |
| 4.4.4 | DC Tie Schedules | Full: VA3 |
| 4.4.4.1 | DC Tie Schedule Criteria | Full: VA3 |
| 4.4.4.2 | DC Tie Schedule Validation | Full: VA3 |
| 4.4.4.3 | Oklaunion Exemption | Settlement/Registration |
| 4.4.5 | CRR Offers | Full: DC1, VA5 |
| 4.4.5.1 | CRR Offer Criteria | Full: VA5 |
| 4.4.5.2 | CRR Offer Validation | Full: VA5 |
| 4.4.6 | PTP Obligation Bids | Full: VA6 |
| 4.4.6.1 | PTP Obligation Bid Criteria | Full: VA6 |
| 4.4.6.2 | PTP Obligation Bid Validation | Full: VA6 |
| 4.4.7 | Ancillary Service Supplied and Traded | No NP Requirement |
| 4.4.7.1 | Self-Arranged Ancillary Service Quantities | Full: VA7 (5d): SA3 |
| 4.4.7.2 | Ancillary Service Offers | Full: VA8 |
| 4.4.7.2.1 | Ancillary Service Offer Criteria | Full: VA8 (2): SA2 |
| 4.4.7.2.2 | Ancillary Service Offer Validation | Full: VA8 |
| 4.4.7.3 | Ancillary Service Trades | Full: VA9 |
| 4.4.7.3.1 | Ancillary Service Trade Criteria | Full: VA9 |
| 4.4.7.3.2 | Ancillary Service Trade Validation | Full: VA9 |
| 4.4.8 | RMR Offers | Full: ST1 |
| 4.4.9 | Energy Offers and Bids | No NP Requirement |
| 4.4.9.1 | Three-Part Supply Offers | Full: VA10 |
| 4.4.9.2 | Startup Offer and Minimum-Energy Offer | Full: VA10 |
| 4.4.9.2.1 | Startup Offer and Minimum-Energy Offer Criteria | Full: VA10 |
| 4.4.9.2.2 | Startup Offer and Minimum-Energy Offer Validation | Full: VA10 |
| 4.4.9.2.3 | Startup Offer and Minimum-Energy Offer Generic Caps | Settlement |
| 4.4.9.2.4 | Verifiable Startup Offer and Minimum-Energy Offer Caps | Settlement |
| 4.4.9.3 | Energy Offer Curve | Full: VA10 |
| 4.4.9.3.1 | Energy Offer Curve Criteria | Full: VA10 |
| 4.4.9.3.2 | Energy Offer Curve Validation | Full: VA10 |
| 4.4.9.3.3 | Energy Offer Curve Caps for Make-Whole Calculation Purposes | Settlement |
| 4.4.9.4 | Mitigated Offer Cap and Mitigated Offer Floor | No NP Requirement |
| 4.4.9.4.1 | Mitigated Offer Cap | Covered by SCED Business Requirements Document |
| 4.4.9.4.2 | Mitigated Offer Floor | Covered by SCED Business Requirements |
| 4.4.9.5 | DAM Energy-Only Offer Curves | Full: VA11 |
| 4.4.9.5.1 | DAM Energy-Only Offer Curve Criteria | Full: VA11 |
| 4.4.9.5.2 | DAM Energy-Only Offer Validation | Full: VA11 |
| 4.4.9.6 | DAM Energy Bids | Full: VA12 |
| 4.4.9.6.1 | DAM Energy Bid Criteria | Full: VA12 |
| 4.4.9.6.2 | DAM Energy Bid Validation | Full: VA12 |
| 4.4.10 | Credit Requirement for DAM Bids and Offers | Full: CR1 |
| 4.5 | DAM Execution and Results | No NP Requirement |
| 4.5.1 | DAM Clearing Process | Full: (1, 3, 4, 5, 6, 7): CE4 (1c, 1d, 2): EMS (2): CF1 (4c): CE2, CE3 (5,6,8): CF1, DC1 (5, 6): CE1 (9, 10, 11): PC1 |
| 4.5.2 | Ancillary Service Insufficiency | Full: (1): SC1 (1a): SC2 (1b): SC3 (1c, 1d, 2): EMS (1d): CE6 |
| 4.5.3 | Communicating DAM Results | Full: CE7 (1): CE8 (2): CE9 (3,4): PC1 |
| 5.5.2 | Reliability Unit Commitment Process | Partial (7): AE4. Other requirements are covered by HRUC business requirements. |
| 6.4.8 | Ancillary Services Capacity During the Adjustment Period and in Real | No NP Requirement |
| 6.4.8.1 | Evaluation and Maintenance of Ancillary Service Capacity Sufficiency | Partial: (1): AE1, AE4 (2): AE2, AE3 AS Plan is ERCOT process |
| 6.4.8.1.1 | ERCOT Increases to the Ancillary Services Plan | Partial: (1): AE1 AS Plan is ERCOT process |
| 6.4.8.1.2 | Replacement of Undeliverable Ancillary Service Due to Transmission Constraints | Full: (3): AE2, AE4 AS reduction by HRUC is covered by HRUC Business Requirements |
| 6.4.8.1.3 | Replacement of Ancillary Service Due to Failure to Provide | (2): AE4 ERCOT process: ERCOT determines AS unavailable in RT. |
| 6.4.8.2 | Supplemental Ancillary Services Market | Full: SA1 (4): AE1 |
| 6.4.8.2.1 | Resubmitting Offers for Ancillary Services in the Adjustment Period | Full: SA2 |
| 6.4.8.2.2 | SASM Clearing Process | Full: SA1 |
| 6.4.8.2.3 | Communication of SASM Results | Full: (1): SA4 (2, 3): SA5 |
| 6.5.9.3.3 | Alert | Full: (2b, 7): SC2 (5): EMS |
| 7.1 | Function of Congestion Revenue Rights | Partial: CF1 DAM applicable sections only |
| 7.2 | Characteristics of Congestion Revenue Rights | Partial: CF1 DAM applicable sections only |
| 7.3 | Types of Congestion Revenue Rights to be Auctioned | Partial: CF1 DAM applicable sections only |
| 7.9 | CRR Settlements | Partial: DC1, CF1 DAM applicable sections only |
| 16.11.4.5 | Credit Requirement for DAM Participants | Partial: CR1 Credit Requirements for MMS |

# Sub-Process Coverage

| Sub-Process ID | Sub-Process Name | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
|  | Business Sub-Process 1: Pre-DAM Activities |  |
| PD1 | AS Obligation | 4.2.1.2 |
| PD2 | QSE Submittal of COP, Bids, Offers, Self Schedules, Trades, and DC Tie Schedules | 3.9, 4.3 (1)(a), 4.3 (1)(b), 4.4, |
| PD3 | General Validation Process of QSE Input | 4.4, 4.1.1 |
|  | Business Sub-Process 2: Special Treatment |  |
| ST1 | RMR | 3.14.1 4.4.8 |
| ST2 | Combined Cycle Modeling | 3.7.1.1, 3.9.1 (5) |
|  | Business Sub-Process 3: Validation of DAM Submissions and Other Trades |  |
| VA1 | Validation of Capacity Trades | 4.4.1, 4.4.1.1, 4.4.1.2 |
| VA2 | Validation of Energy Trades | 4.4.2, 4.4.2.1, 4.4.2.2 |
| VA3 | Validation of DC Tie Schedules | 4.4.4, 4.4.4.1, 4.4.4.2 |
| VA4 | Validation of Self Schedules | 4.4.3, 4.4.3.1, 4.4.3.2 |
| VA5 | Validation of CRR Offers | 4.4.5, 4.4.5.1, 4.4.5.2 |
| VA6 | Validation of PTP Obligation Bids | 4.4.6, 4.4.6.1, 4.4.6.2 |
| VA7 | Validation of AS Self-Arrangement | 4.4.7.1 |
| VA8 | Validation of AS Offers | 4.4.7.2, 4.4.7.2.1, 4.4.7.2.2 |
| VA9 | Validation of AS Trade | 4.4.7.3, 4.4.7.3.1, 4.4.7.3.2 |
| VA10 | Validation of Three-Part Supply Offer - Start-Up and Minimum-Energy Offer and Energy Offer Curve | 4.4.9.1 4.4.9.2, 4.4.9.2.1, 4.4.9.2.2 4.4.9.3, 4.4.9.3.1, 4.4.9.3.2 |
| VA11 | Validation of DAM Energy-Only Offers | 4.4.9.5, 4.4.9.5.1, 4.4.9.5.2 |
| VA12 | Validation of DAM Energy Bids | 4.4.9.6, 4.4.9.6.1, 4.4.9.6.2 |
| VA13 | Notice of Validation Rules | 4.2.4 |
| VA14 | Validation of COP | 3.9, 3.9.1, 3.9.2 |
|  | Business Sub-Process 4: Credit Requirement for DAM Bids and Offers |  |
| CR1 | Credit Requirement | 4.4.10, 16.11.4.5 |
|  | Business Sub-Process 5: Ancillary Service Sufficiency Check |  |
| SC1 | AS Insufficiency Check | 3.18, 4.5.2 (1) |
| SC2 | AS Insufficiency Alert | 4.5.2 (1)(a), 6.5.9.3.3 (2)(b) 6.5.9.3.3 (7) |
| SC3 | Additional AS Offer Validation | 4.5.2 (1)(b) |
|  | Business Sub-Process 6: CRR Day-Ahead Simultaneously Feasibility Test |  |
| CF1 | CRR Day-Ahead SFT | 4.5.1 (2), 4.5.1 (5), 4.5.1 (6), 4.5.1 (8) 7.1, 7.2, 7.3, 7.9 |
|  | Business Sub-Process 7: Derating CRR Options Declared for Settlement in Real-Time |  |
| DC1 | Derating CRR Options Declared for RT | 4.4.5, 4.5.1 (5), 4.5.1 (6), 4.5.1 (8), 7.9 |
|  | Business Sub-Process 8: Day Ahead Clearing Process |  |
| CE1 | DAM Pre-processing | 3.4, 3.5, 4.5.1 (5), 4.5.1 (6) |
| CE2 | Initial Commitment Status | 3.9.1 (4), 4.5.1 (4)(c) |
| CE3 | Network Security Monitor | 4.5.1 (4)(c) |
| CE4 | DAM Clearing Engine | 3.8 (6), 3.18, 4.1, 4.5.1 (1), 4.5.1 (3), 4.5.1 (4) 4.5.1 (5), 4.5.1 (6), 4.5.1 (7) |
| CE5 | Tie Breaking Rule | N/A |
| CE6 | Constraint Penalty Function | 4.5.2 (1)(d) |
| CE7 | Post-processing | 4.5.3 |
| CE8 | Notification of DAM Awards | 4.2.1.1 (5), 4.5.3 (1) |
| CE9 | Notification of DAM Results | 4.5.3 (2) |
| CE10 | Control of DAM Clearing Process | 4.1.2 |
|  | Business Sub-Process 9: AS Evaluation in Adjustment Period |  |
| AE1 | Increased AS Obligation | 6.4.8.1 (1), 6.4.8.1.1 (1), 6.4.8.2 (4) |
| AE2 | Validation of COP changes | 3.9.2 6.4.8.1 (2), 6.4.8.1.2 (3) |
| AE3 | COP Monitor | 3.9.2 6.4.8.1 (2) |
| AE4 | Delivery Evaluation Function | 3.9, 5.5.2 (7), 6.4.8.1 (1) 6.4.8.1.2 (3) 6.4.8.1.3 (2) |
|  | Business Sub-Process 10: Supplemental Ancillary Service Market (SASM) |  |
| SA1 | SASM Clearing Engine | 3.18, 6.4.8.2, 6.4.8.2.2 |
| SA2 | Validation of AS Offers | 4.4.7.2.1 (2), 6.4.8.2.1 |
| SA3 | Validation of AS Self-Arrangement | 4.4.7.1 (5)(d) |
| SA4 | Notification of AS awards | 6.4.8.2.3 (1) |
| SA5 | Notification of SASM Results | 6.4.8.2.3 (2) 6.4.8.2.3 (3) |
|  | Business Sub-Process 11: Price Validation and Correction |  |
| PC1 | Price Validation and Correction | 4.5.1 (9), 4.5.1 (10), 4.5.1 (11) 4.5.3 (3), 4.5.3 (4) |

- Day-Ahead Market Clearing (DAM)

The DAM market clearing problem is a Security Constrained Unit Commitment (SCUC) that is formulated as a Mixed Integer Linear Program (MILP) problem. The DAM problem is formulated as followings:

| Maximize | q,t,bidEnergyBidPriceq,bid,t∗EnergyBidClearedMWq,bid,t−q,t,offerEnergyOfferPriceq,offer,t∗EnergyOfferClearedMWq,offer,t +q,t,crrbidCRRBidPriceq,crrbid,t∗CRRBidClearedMWq,crrbid,t−q,t,crrofferCRROfferPriceq,crroffer,t∗CRROfferClearedMWq,crroffer,t −r,asoffer,astype,tASOfferPricer,asoffer,astype,t ∗ASOfferClearedMWr,asoffer,astype,t −PenaltyCostENG∗t(EnergySlackUPMWt+EnergySlackDNMWt)−PenaltyCostURS∗t(ASSlackUPMWURS,t) −PenaltyCostDRS∗t(ASSlackUPMWDRS,t)−PenaltyCostRRS∗t(ASSlackMWRRS,t) −PenaltyCostNSRS∗t(ASSlackUPMWNSRS,t) −t,cTranSlackMWc,t∗TranPenaltyCostc −r,t,offer3pStartupCostr,offer3p,t*ResStartupr,offer3p,t−r,t,offer3pMineneCostr,offer3p,t*ResProcuredr,offer3p,t −r,t,offer3p,segEnergyCurver,offer3p,seg,t*ResSegMWr,offer3p,seg,t |
| --- | --- |
| Subject to | - Energy Demand Supply constraints for each interval, t: |
|  | q,bidEnergyBidClearedMWq,bid,tq,offerEnergyOfferClearedMWq,offer,t+r,offer3p,segResSegMWr,offer3p,seg,t +r,offer3pResProcuedr,offer3p,t∗MinCapMWr,t +EnergySlackUPMWt−EnergySlackDNMWt (SPdemand,t) |
|  | - System A/S Requirement Constraints for each interval, t |
|  | r,asoffer,tt=URSASOfferClearedMWr,tt,asoffer,t+ASSlackUPMWURS,t≥SYSASReqMWURS,t−qseQSEASSchdMWqse,URS,t(SPURS,t) r,asoffer,tt=DRSASOfferClearedMWr,tt,asoffer,t+ASSlackUPMWDRS,t≥SYSASReqMWDRS,t−qseQSEASSchdMWqse,DRS,t(SPDRS,t) r,asoffer,tt=RRSASOfferClearedMWr,tt,asoffer,t+ASSlackUPMWRRS,t≥SYSASReqMWRRS,t−qseQSEASSchdMWqse,RRS,t(SPRRS,t) r,asoffer,tt=NSRSASOfferClearedMWr,tt,asoffer,t+ASSlackUPMWNSRS,t≥SYSASReqMWNSRS,t−qseQSEASSchdMWqse,NSRS,t(SPNSRS,t) r,asoffer,tt=RRS−loadASOfferClearedMWr,tt,asoffer,t+qseQSEASSchdMWqse,RRS−load,t≤SYSASReqMWRRS,t∗LoadProvideRRSMAX% (SPRRS2,t) |
|  | - Energy Bid/Offer Capacity Constraints for each interval, t |
|  | EnergyBidClearedMWq,bid,t≤EnergyBidMWq,bid,tEnergyOfferClearedMWq,offer,t≤EnergyOfferMWq,offer,t |
|  | - CRR Bid/Offer Capacity Constraints for each interval, t |
|  | CRRBidClearedMWq,crrbid,t≤CRRBidMWq,crrbid,tCRROfferClearedMWq,crroffer,t≤CRROfferMWq,crroffer,t |
|  | - CRR Block Offer Capacity Constraints for two intervals t1 and t2 between the first hour and the last hour of the Offer |
|  | CRROfferClearedMWq,crroffer,t1=CRROfferClearedMWq,crroffer,t2 |
|  | - PTP Obligation Block Bid Capacity Constraints for any two intervals t1 and t2 between the first hour and the last hour of the Bid |
|  | CRRBidClearedMWq,crroffer,t1=CRRBidClearedMWq,crroffer,t2 |
|  | - A/S Offer Capacity Constraints for each interval, t |
|  | astype=URS,RRS,NSRSonlineASOfferClearedMWr,asoffer,astype,t≤ResProcuredr,offer3p,t∗OnlineASOfferMWr,asoffer,t ASOfferClearedMWr,asoffer,astype=DRS,t≤ResProcuredr,offer3p,t∗DRSOfferMWr,asoffer,t ASOfferClearedMWr,asoffer,astype=NSRSoffline,t≤(1−ResProcuredr,offer3p,t)∗OfflineASOfferMWr,asoffer,t |
|  | - Fixed Block Offer Constraint for Resource r for each AS type at each interval t: |
|  | ASOfferClearedMWr,asoffer,astype,t=ASBlockProcuredr,asoffer,astype,t∗OnlineASOfferMWr,asoffer,t Where astype=URS,RRS,NSRSOnline This constraint includes RRS Block Offer Constraint for Load Resource. ASOfferClearedMWr,asoffer,astype,t=ASBlockProcuredr,asoffer,astype,t∗OfflineASOfferMWr,asoffer,t Where astype=NSRSOffline ASOfferClearedMWr,asoffer,astype,t=ASBlockProcuredr,asoffer,astype,t∗DRSOfferMWr,asoffer,t Where astype=DRS |
|  | - Time (Variable) Block Offer Constraint for Resource r at each interval t1 and t2 that are within the start and end time of the AS Offer: |
|  | ASOfferClearedMWr,asoffer,astype,t1=ASOfferClearedMWr,asoffer,astype,t2 Where astype=URS,DRS,RRS,NSRSOnline,NSRSOffline |
|  | - A/S Offers link to Three-Part supply offers for each interval t |
|  | asoffer,astype=URS,RRS,NSRSonlineASOfferClearedMWr,asoffer,astype,t+ResMinCapr,t*ResProcuredr,offer3p,t+segResSegMWr,offer3p,seg,tResProcuredr,offer3p,t∗MaxCapMWr,t Energy minus Regulation Down shall be greater than or equal to LSL: segResSegMWr,offer3p,seg,t≥asofferASOfferClearedMWr,asoffer,astype=DRS,t asofferASOfferClearedMWr,asoffer,astype=NSRSOffline,t(1−ResProcuredr,offer3p,t)∗MaxCapMWr,t |
|  | - Exclusive Constraints between Three-Party Energy Offer and AS Offers for each interval t |
|  | asoffer,astype=URS,DRS,RRS,NSRSOnline,NSRSOfflineASOfferClearedMWr,asoffer,astype,t≤(1−EnergyOnlyDispatchr,t)∗MaxCapMWr,t segResSegMWr,offer3p,seg,t≤EnergyOnlyDispatchr,t∗MaxCapMWr,t EnergyOnlyDispatchr,t≤ResProcuredr,t |
|  | - Resource with only AS Offers for each interval t |
|  | asoffer,astype=URS,RRS,NSRSOnlineASOfferClearedMWr(asonly),asoffer,astype,t−(ResProcuredr(asoffer),t∗MaxCapMWr,t)≤0 asoffer,astype=NSRSOfflineASOfferClearedMWr(asonly),asoffer,astype,t−(1−ResProcuredr(asoffer),t)∗MaxCapMWr,t≤0 ResProcuredr(asoffer),t needs to satisfy the minimum on-line and off-line constraints in (13) |
|  | - Transmission Constraints (for all intervals and all monitored constraints) |
|  | For Initial Unit Commitment (IUC), these constraints are the predefined constraints. For Security Constrained Unit Commitment (SCUC), these constraints are passed from Network Security Management (NSM) module at each SCUC-NSM iteration q,ptpbidSFptpbid,c,t∗PTPBidClearedMWq,ptpbid,t+q,crroffer,where SFcrroffer,c,t>0SFcrroffer,c,t∗(CRROfferMWq,crroffer,t−CRROfferClearedMWq,crroffer,t) −q,bidSFbid,c,t∗EnergyBidClearedMWq,bid,t+q,offerSFoffer,c,t∗EnergyOfferClearedMWq,offer,t+r,offer3pSFr,c,t∗(MinCapMWr,t*ResProcuredr,offer3p,t+segResSegMWr,offer3p,seg,t) −TranSlackMWc,t ≤Limitc,t (SPc,t) CRROfferMWq,crroffer,t reserves the network capacity for CRR’s to be settled in RTM. It is the amount after CRR derating. For CRR options, only those options with positive Shift Factor SFcrropton,c,t are included in the transmission constraint c |
|  | - Split Generation Constraints for Jointly Owned Resource r1 and r2 at each interval t |
|  | ResProcuredr1,offer,t=ResProcuredr2,offer,t |
|  | - Resource Constraints for each Resource, r |
|  | ResProcuredr,offer,t−ResProcuredr,offer,t−1=ResStartupr,offer,t−ResShutdownr,offer,t−1 ResStartupr,offer,t+ResShutdownr,offer,t≤1 [min(T−t,mnuptmr−1)]ResStartupr,offer,t≤ResProcuredr,offer,t+1+ResProcuredr,offer,t+2+…+ResProcuredr,offer,t+min[T−t,mnuptmr−1], t≤T [min(T−t,mndntmr−1)]ResShutdownr,offer,t+ResProcuredr,offer,t+1+ResProcuredr,offer,t+2+…+ResProcuredr,offer,t+min[T−t,mndntmr−1]≤[min(T−t,mndntmr−1)], t≤T−1 ResSegMWr,offer,seg,t≤ResOfferSegSizer,offer,seg,t*ResProcuredr,t,offer |
|  | - Operating limits for each Resource r at interval t |
|  | 0≤segResSegr,offer.seg,t≤(MaxCapMWr,t−MinCapMWr,t)*ResProcuredr,offer,t |
|  | - Resource Initial Condition Constraint for Resource r |
|  | ResProcuredr,offer,t=1, t=1,mnuptmr−ResHrinitUpr if ResInitStatus=1 ResProcuredr,offer,t=0, t=1,mndntmr−ResHrinitDnr if ResInitStataus=0 |
|  | - Down Time Dependent Startup Cost for Resource r |
|  | StartupCostr,offer,t≤ResStartupcostOfferr,offer,t(ResHrsDnr,offer,t) StartupCostr,offer,t≥ResStartupcostOfferr,offer,t(ResHrsDnr,offer,t) −maxstartupcost∗(1−ResStartupr,offer,t) StartupCostr,offer,t≤maxstartupcost*ResStartupr,offer,t |
|  | - Fixed Quantity Block Energy Bid and Offer |
|  | EnergyBidClearedMWblock,bid,t=EnergyBidMWblock,bid,t∗EnergyBidProcuredbid,t, EnergyOfferClearedMWblock,offer,t=EnergyOfferMWblock,offer,t∗EnergyOfferProcuredoffer,t EnergyBidClearedMWblock,bid,t1=EnergyBidClearedMWblock,bid,t2EnergyOfferClearedMWblock,offer,t1=EnergyOfferClearedMWblock,offer,t2 for t, t1, t2 between the first and last hour of the fixed quantity block Energy Offer or Bid |
|  | - Variable Quantity Block Energy Bid and Offer |
|  | EnergyBidClearedMWblock,bid,t≤EnergyBidMWblock,bid,tEnergyOfferClearedMWblock,offer,t≤EnergyOfferMWblock,offer,t EnergyBidClearedMWblock,bid,t1=EnergyBidClearedMWblock,bid,t2EnergyOfferClearedMWblock,offer,t1=EnergyOfferClearedMWblock,offer,t2 for t, t1, t2 between the first and last hour of the variable quantity block Energy Offer or Bid. |
|  | - Maximum Run Time Constraint for Resource r |
|  | ResHrsUpr,offer,t≤ResMaxRuntimer, t≥1 |
|  | - Combined Cycle Unit Configuration Constraints of Resource r |
|  | All the unit-level constraints defined above for Resource r remain applicable for any possible configuration for Combine Cycle Generation Resource. In other words, r represents configuration r of the Combined Cycle Unit. The additional inter-configuration constraints for Combined Cycle Unit ccunit with multiple configurations mod at t: ResProcuredccunit,offer3p,t=modResProcuredccunit,mod,offer3p,t≤1, ResMinRuntimeccunit,mod≤ResHrsUpccunit,mod,offer3p,t≤ResMaxRuntimeccunit,mod ResProcuredccunit,offer3p,t is subjected to Combined Cycle Plant Minimum Down and Minimum Run Time The Inter-Configuration transition is feasible between certain configurations and between certain configurations to the off state |

The DAM problem input parameters are:

- T is the number of intervals of the study period;

- SYSASReqMWURS,t is the ERCOT total URS requirement at interval t;

- QSEASSchdMWqse,URS,t is the URS Self-Schedule of QSE qse at interval t;

- SYSASReqMWDRS,t is the ERCOT total DRS requirement at interval t;

- QSEASSchdMWqse,DRS,t is the DRS Self-Schedule of QSE qse at interval t;

- SYSASReqMWRRS,t is ERCOT total RRS requirement at interval t;

- QSEASSchdMWqse,RRS,t is the RRS Self-Schedule of QSE qse at interval t;

- SYSASReqMWNSRS,t is ERCOT total NSRS requirement at interval t;

- QSEASSchdMWqse,NSRS,t is the NSRS Self-Schedule of QSE qse at interval t;

- QSEASSchdMWqse,RRS−load,t is RRS from Load Resource Self-Schedule QSE qse at interval t;

- LoadProvideRRSMAX% is the maximum percentage of RRS requirement that can be provided by Load Resources;

- MaxCapMWr,t and MinCapMWr,t are the max and min operating limits of Resource r at interval t;

- mnuptmr and mndntmr are the minimum up time and minimum down time of Resource r;

- ResInitStatusr is the initial status of Resource rat the start of the study period, 1: Online, 0: Offline.

- ResHrinitUpr is the number of intervals that Resource rhas been Online at the start of the study period.

- ResHrinitDnr is the number of intervals that Resource rhas been Offline at the start of the study period.

- ResMaxRuntimer is maximum run time of Resource r.

- For Combined Cycle unit, ResMaxRuntimeccunit,mod and ResMinRuntimeccunit,mod is the maximum and minimum runtime of Configuration mod of Combined Cycle Unit ccunit.

- EnergyCurver,offer3p,seg,t is the price of MW segment seg of  the Energy offer of Resource r with Three-Part Offer at interval t;

- ResStartupcostOfferr,offer,t is the start up cost offer of Resource r with Three-Part Offer at interval t;

- maxstartupcost is the maximum startup cost of the start up cost offers of  all Resource r.

- MineneCostr,offer3p,t is the minimum generation cost of Resource r with Three-Part Offer at interval t;

- EnergyOfferPriceq,offer,t is the offer price of segment q of Energy Offer offer at interval t;

- EnergyOfferMWq,offer,t is the MW capacity size of segment q of Energy Offer offer at interval t;

- EnergyBidPriceq,bid,t is the energy bid price of segment q of Energy Bid bid at interval t;

- EnergyBidMWq,bid,t is the MW capacity size of segment q of Energy Bid bid at interval t;

- CRROfferPriceq,crroffer,t is the Offer price of segment q of CRR Offer crroffer at interval t;

- CRROfferMWq,crroffer,t is MW capacity size of segment q of CRR Offer crroffer at interval t;

- PTPBidPriceq,crrbid,t is the Bid price of segment q of PTP Obligation Bid crrbid at interval t

- PTPBidMWq,crrbid,t is MW capacity size of segment q of PTP Obligation Bid crrbid at interval t;

- ASOfferPricer,tt,asoffer,t  is the AS Offer price for AS type tt of AS Offer asoffer from Resource r at interval t, where tt=URS,DRS,RRS,NRS,tt≠block.

- OnlineASOfferMWr,asoffer,t is the capacity of AS Offer asoffer (from 1 to up to 5) for Online Reserves including RURS,RRS,NSRSonline from Resource r at interval t. Note that only Online Resource can provide Online Reserves;

- OfflineASOfferMWr,asoffer,t is the capacity of AS Offer asoffer (from 1 to up to 5) for Non-Spin Offline Reserves NSRSoffline from Resource r at interval t. Note that only Offline Resource can provide Offline Reserves;

- DRSOfferMWr,asoffer,t is the capacity of AS Offer asoffer (from 1 to up to 5) for Regulation Down  Reserve DRS from Resource r at interval t. Note that only Online Resource can provide Regulation Down Reserve;

- A flag indicating Fixed or Variable Block Offer of AS Offer asoffer (from 1 to up to 5) from Resource r at interval t;

- ASOfferPricer,asoffer,astype,t  is the price for AS type astype=URS,DRS,NSRSOnline,NRSRSOffline from AS Offer asoffer (from 1 to up to 5) from Resource r at interval t;

- Limitc,t is the limit of transmission constraint c at interval t;

- SFr,c,t is the Shift Factor of Resource r associated with transmission constraint c at interval t;

- SFoffer,c,t is the Shift Factor of Energy Offer offer associated with transmission constraint c at interval t;

- SFbid,c,t is the Shift Factor of Energy Bid bid associated with transmission constraint c at interval t;

- SFccroffer,c,t is the Shift Factor of CRR Offer crroffer associated with transmission constraint c at interval t, where SFccroffer,c,t=SFccrofferSource,c,t−SFccrofferSink,c,t, and SFccrofferSource,c,t is Shift Factor of CRR Offer crroffer Source bus crrofferSource associated with transmission constraint c at interval t, SFccrofferSink,c,t is Shift Factor of CRR Offer crrofferSink Sink bus c associated with transmission constraint c at interval t,

- SFptpbid,c,tis the Shift Factor of PTP Obligation Bid ptpbid associated with transmission constraint c at interval t, where SFptpbid,c,t=SFptpbidSource,c,t−SFptpbidSink,c,t, and SFptpbidSource,c,t is Shift Factor of PTP Obligation Bid ptpbid Source bus SFptpbidSource,c,t associated with transmission constraint c at interval t,  SFptpbidSink,c,t is Shift Factor of PTP Obligation Offer ptpbid Sink bus ptpbidSink associated with transmission constraint c at interval t,

- PenaltyCostENG is the penalty cost of violating the power balance constraint;

- PenaltyCostURS is the penalty cost of violating the URS requirement constraint;

- PenaltyCostDRS is the penalty cost of violating the DRS requirement constraint;

- PenaltyCostRRS is the penalty cost of violating the RRS requirement constraint;

- PenaltyCostNSRS is the penalty cost of violating the NSRS requirement constraint;

- TranPenaltyCostc is the penalty cost of violating the transmission constraint c.

The DAM problem decision variables are

- Binary Variables:

- ResProcuredr,offer3p,tis 1 if Resource r with Three-Part Offer is online for procurement at interval t, 0 offline;

- For Combined Cycle Unit, ResProcuredccunit,mod,offer3p,tis 1 if Configuration mod of Combined Cycle Unit ccunit with Three-Part Offer is online for procurement at interval t, 0 offline;

- For Combined Cycle Unit, ResProcuredccunit,offer3p,tis 1 if any of the multiple Configurations  of Combined Cycle Unit ccunit with Three-Part Offer is online for procurement at interval t, 0 offline;

- ResStartupr,offer3p,t is 1 if Resource r with Three-Part Offer is started up at interval t, 0 otherwise;

- ResShutdownr,offer3p,t is 1 if Resource r with Three-Part Offer is shut down at interval t, 0 otherwise;

- EnergyOfferProcuredoffer,t is 1 if Fixed Quantity Block Energy Offer offer is procured at interval t, 0 otherwise

- EnergyBidProcuredbid,t is 1 if Fixed Quantity Block Energy Bid bid is procured at interval t, 0 otherwise;

- ASBlockProcuredr,asoffer,astype,t is 1 if the Fixed quantity AS offer asoffer (from 1 to up to 5) from Resource r is procured for AS type astype=URS,DRS,NSRSOnline,NRSRSOffline at interval t, 0 otherwise;

- EnergyOnlyDipatchr,tis 1 if only energy is dispatched for Resource r at interval t that have exclusive Three-Part energy offer and AS offers, 0 otherwise

- Continuous Variables:

- EnergyOfferClearedMWq,offer,t is the cleared MW of segment q  of Energy Offer offer at interval t;

- EnergyBidClearedMWq,bid,t is the cleared MW of segment q  of Energy Bid bid at interval t;

- PTPBidClearedMWq,crrbid,t is the cleared MW of segment q  of PTP Obligation Bid crrbid at interval t;

- CRROfferClearedMWq,crroffer,t is the cleared MW of segment q  of CRR Offer crroffer at interval t;

- ASOfferClearedMWr,tt,asoffer,t is the cleared MW of AS Offer asoffer for AS type tt from Resource r at interval t;

- ResSegMWr,offer3p,seg,tis the scheduled MW of segment seq of Energy offer of Resource r with Three-Part Offer at interval t;

- ResHrsUpr,offer,t is the number of intervals that Resource rhas been Online at the end of interval t;

- ResHrsDnr,offer,t is the number of intervals that Resource rhas been Offline at the start of interval t;

- StartupCostr,offer,t is the startup cost for Resource rat the start of interval t

- ASOfferClearedMWr,asoffer,astype,t is the amount of procurement for AS type astype=URS,DRS,RRS,NSRSONline,NSRSOffline from AS Offer asoffer( from 1 up to 5) of Resource r at interval t,

- Dual Variables ( Shadow Prices)

- SPdemand,t is the dual variable associated with the power balance constraint at interval t;

- SPURS,t is the dual variable associated with the URSrequirement constraint at interval t;

- SPDRS,t is the dual variable associated with theDRSrequirement constraint at interval t;

- SPRRS,t is the dual variable associated with theRRSrequirement constraint at interval t;

- SPNSRS,t is the dual variable associated with theNSRSrequirement constraint at interval t;

- SPRRS2,t is dual variable associated with the maximum amount of RRSrequirement that can be met Load Resources constraint at interval t;

- SPc,t is dual variable associated with the transmission constraint  c at interval t;

- Non-Negative Slack Variables:

- EnergySlackUPMWtand EnergySlackDNMWt are the slack variables for the power balance constraint at interval t;

- ASSlackUPMWURS,t  is the slack variable for the Regulation UP URSconstraint at interval t;

- ASSlackUPMWDRS,t is the slack variable for the Regulation Down DRSconstraint at interval t;

- ASSlackUPMWRRS,t is the slack variable for the Responsive Reserve RRSconstraint at interval t;

- ASSlackUPMWNSRS,t is the slack variable for the Non-spin Reserve NSRSconstraint at interval t;

- TranSlackMWc,t is the slack variable for the transmission constraint c at interval t

- DAM Energy LMP:

- LMP at bus bus at interval t is determined as

- LMPbus,t=SPdemand,t+cSFbus,c,t∗SP

- System wide MCPC’s for AS:

- AS MCPC at interval t is determined as

- Supplemental Ancillary Service Market (SASM) Clearing

The SASM Clearing Engine function is run by the ERCOT Operator during Adjustment Period to procure additional Regulation Down, Regulation Up, Responsive Reserve, and Non-Spin Reserve capacities. In order to evaluate and maintain AS capacity sufficiency, the ERCOT Operator may use this function to procure Ancillary Services in the Adjustment Period for:

- Increased need of Ancillary Services capacity above that specified in the Day-Ahead;

- Replacement of Ancillary Services capacity that is undeliverable due to transmission constraints; or

- Replacement of Ancillary Services capacity due to failure to provide

The SASM function calculates the awarded AS schedules that minimize the total procurement costs of all AS types over all hours of the SASM study period while satisfying the required additional AS quantities for the entire ERCOT system and AS modeling constraints for individual Resources.

The SASM optimization problem is formulated as follows:

Minimize:

r,asoffer,astype=URS,DRS,RRS,NSRSonline,NSRSoffline,tASOfferPricer,asoffer,astype,t ∗ASOfferClearedMWr,asoffer,astype,t +asreqtype=URS,DRS,RRS,NSRS,tPenaltyCostasreqtype∗(ASSlackUnderMWasreqtype,t+ ASSlackOverMWasreqtype,t )

Subject To:

- System AS Requirement Constraints for each AS requirement type at each interval t:

r,asoffer,astype=URSASOfferClearedMWr,asoffer,astype=URS,t+qseQSEASSchdMWqse,URS,t+ASSlackUnderMWastype=URS,t−ASSlackUnderMWastype=URS,t=SYSASReqMWURS,t(SPURS,t)

r,asoffer,astype=DRSASOfferClearedMWr,asoffer,astype=DRS+qseQSEASSchdMWqse,DRS,t+ASSlackUnderMWastype=DRS,t−ASSlackOverMWastype=DRS,t=SYSASReqMWDRS,t(SPDRS,t )

r,asoffer,astype=RRSASOfferClearedMWr,asoffer,astype=RRS,t+qseQSEASSchdMWqse,RRS,t+ASSlackUnderMWastype=RRS,t−ASSlackOverMWastype=RRS,tSYSASReqMWRRS,t(SPRRS,t)

r,asoffer,astype=NSRSonline,NSRSofflineASOfferClearedMWr,asoffer,astype=NSRSonline,NSRSoffline,t+qseQSEASSchdMWqse,NSRS,t+ASSlackUnderMWastype=NSRS,t−ASSlackOverMWastype=NSRS,tSYSASReqMWNSRS,t

(SPNSRS,t)

r(load),asoffer,astype=RRSASOfferClearedMWr(load),asoffer,astype=RRS,t+qseQSEASSchdMWqse,RRS−load,t≤SYSASReqMWRRS,t∗LoadProvideRRSMAX%

- AS Offer Capacity Constraint for each AS offer of Resource r ( Offline but available indicated by COP ) each interval t:

astype=URS,RRS,NSRSonlineASOfferClearedMWr,asoffer,astype,t≤ResOnliner,t∗OnlineASOfferMWr,asoffer,t

ASOfferClearedMWr,asoffer,astype=DRS,t≤ResOnliner,t∗DRSOfferMWr,asoffer,t

ASOfferClearedMWr,asoffer,astype=NSRSoffline,t≤(1−ResOnliner,t)∗OfflineASOfferMWr,asoffer,t

asoffer,astype=URS,DRS,RRS,NSRSonline,NSRSofflineASOfferClearedMWr,asoffer,astype,t≤ResOnliner,t∗(ResMaxCapr,t−ResMinCapr,t)+(1−ResOnliner,t)*ResMaxCapr,t

- AS Offer Capacity Constraint for each AS offer of Online Resource r( Online indicated by COP) each interval t:

astype=URS,RRS,NSRSonlineASOfferClearedMWr,asoffer,astype,t≤OnlineASOfferMWr,asoffer,t

ASOfferClearedMWr,asoffer,astype=DRS,t≤DRSOfferMWr,asoffer,t

asoffer,astype=URS,DRS,RRS,NSRSonlineASOfferClearedMWr,asoffer,astype,t≤(ResMaxCapr,t−ResMinCapr,t)

ASOfferClearedMWr,asoffer,astype=URS,RRS,NSRSOnline,t=0 if the price for astype=URS,RRS,NSRSOnline is not supplied by AS Online Reserve Offer asoffer( from 1 to up to 5)

- AS Offer Capacity Constraint for each AS offer of Offline Resource r( Offline but Reserved for Non-Spin indicated by COP) each interval t:

astype=URS,RRS,NSRSonlineASOfferClearedMWr,asoffer,astype,t=0

ASOfferClearedMWr,asoffer,astype=DRS,t=0

asofferASOfferClearedMWr,asoffer,astype=NSRSOffline,t≤ResMaxCapr,t

- Fixed Block Offer Constraint for Resource r for each AS type at each interval t:

ASOfferClearedMWr,asoffer,astype,t=ASBlockProcuredr,asoffer,astype,t∗OnlineASOfferMWr,asoffer,t

Where astype=URS,RRS,NSRSOnline

This constraint includes RRS Block Offer Constraint for Load Resource.

ASOfferClearedMWr,asoffer,astype,t=ASBlockProcuredr,asoffer,astype,t∗OfflineASOfferMWr,asoffer,t

Where astype=NSRSOffline

ASOfferClearedMWr,asoffer,astype,t=ASBlockProcuredr,asoffer,astype,t∗DRSOfferMWr,asoffer,t

Where astype=DRS

- Variable Block Offer Constraint for Resource r at each interval  t1 and t2 that are within the start and end time of the AS Offer:

ASOfferClearedMWr,asoffer,astype,t1=ASOfferClearedMWr,asoffer,astype,t2

Where astype=URS,DRS,RRS,NSRSOnline,NSRSOffline

- AS Procurement for each AS Type from Resource r at each interval t:

ASProcuementMWr,astype.,t=asofferASOfferClearedMWr,asoffer,astype,t

Where astype=URS,DRS,RRS,NSRSOnline,NSRSOffline

- COP AS Schedule for each AS Type from Resource r at each interval t:

ASProcuementMWr,astype.,t≥ASCOPMWr,astype.,t

Where astype=URS,DRS,RRS,NSRSOnline,NSRSOffline

- Maximum Capacity for Procurement for each AS Type from Resource r at interval t:

ASProcuementMWr,astype.,t≤MaxProcurementMWr,astype,t

Where astype=URS,DRS,RRS,NSRSOnline,NSRSOffline

Note that each AS Offer from Resource r has a start and end time. The AS Offer modeling of Resource r is applicable only for the intervals between the start time and the end time of the AS Offer.

The SASM Sufficiency Check problem input data are:

- SYSASReqMWURS,t is the ERCOT total URS requirement at interval t;

- QSEASSchdMWqse,URS,t is the URS Self-Schedule of QSE qse at interval t;

- SYSASReqMWDRS,t is the ERCOT total DRS requirement at interval t;

- QSEASSchdMWqse,DRS,t is the DRS Self-Schedule of QSE qse at interval t;

- SYSASReqMWRRS,t is ERCOT total RRS requirement at interval t;

- QSEASSchdMWqse,RRS,t is the RRS Self-Schedule of QSE qse at interval t;

- SYSASReqMWNSRS,t is ERCOT total NSRS requirement at interval t;

- QSEASSchdMWqse,NSRS,t is the NSRS Self-Schedule of QSE qse at interval t;

- QSEASSchdMWqse,RRS−load,t is RRS from Load Resource Self-Schedule QSE qse at interval t;

- LoadProvideRRSMAX% is the maximum percentage of RRS requirement that can be provided by Load Resources;

- MaxCapMWr,t and MinCapMWr,t are the max and min operating limits of Resource r at interval t;

- OnlineASOfferMWr,asoffer,t is the capacity of AS Offer asoffer (from 1 to up to 5) for Online Reserves including RURS,RRS,NSRSonline from Resource r at interval t. Note that only Online Resource can provide Online Reserves;

- OfflineASOfferMWr,asoffer,t is the capacity of AS Offer asoffer (from 1 to up to 5) for Non-Spin Offline Reserves NSRSoffline from Resource r at interval t. Note that only Offline Resource can provide Offline Reserves;

- DRSOfferMWr,asoffer,t is the capacity of AS Offer asoffer (from 1 to up to 5) for Regulation Down Reserve DRS from Resource r at interval t. Note that only Online Resource can provide Regulation Down Reserve;

- A flag indicating Fixed or Variable Block Offer of AS Offer asoffer (from 1 to up to 5) from Resource r at interval t;

- ASOfferPricer,asoffer,astype,t  is the price for AS type astype=URS,DRS,NSRSOnline,NRSRSOffline from AS Offer asoffer (from 1 to up to 5) from Resource r at interval t;

- ASCOPMWr,astype,t is the AS schedule in COP for AS type astype=URS,DRS,NSRSOnline,NRSRSOffline of Resource r at interval t

- MaxProcurementMWr,astype,t is the maximum capacity available for procurement for AS type astype=URS,DRS,NSRSOnline,NRSRSOffline from Resource r at interval t

- Penaltycostastype is the penalty cost for the AS insufficiency for AS Requirement type asreqtype, where asreqtype=URS,DRS,RRS,NSRS,and PenaltycostURS>PenaltycostDRS>PenaltycostRRS>PenaltycostNSRS.

The SASM optimization problem decision variables are:

- Binary Variables:

- ResOnliner,tis 1 if Resource r ( Offline but available indicated in COP) is online for Online Reserve procurement at interval t, 0 offline for Offline Non-Spin reserve procurement;

- ASBlockProcuredr,asoffer,astype,t is 1 if Fixed Block Offer of AS Offer asoffer( from 1 to up to 5) from  Resource r is procured for AS type astype=URS,DRS,RRS,NSRSONline,NSRSOfflineat interval t, 0 otherwise;

- Non-Negative Continuous Variables:

- ASOfferClearedMWr,asoffer,astype,t is the amount of procurement for AS type astype=URS,DRS,RRS,NSRSONline,NSRSOffline from AS Offer asoffer( from 1 up to 5) of Resource r at interval t,

- ASProcuredMWr,astype,t is the amount of procurement for AS type astype=URS,DRS,RRS,NSRSONline,NSRSOffline from Resource r at interval t

- Non-Negative Slack Variables:

- ASSlackUnderMWasreqtype,t and ASSlackOverMWasreqtype,t are the slack variables for Under or Over procurement for AS requirement type asreqtype=URS,DRS,RRS,NSRS at interval t

- Dual Variables associated with the system AS requirements ( Shadow Price):

- SPURS,t is the dual variable associated with the URSrequirement constraint at interval t;

- SPDRS,t is the dual variable associated with theDRSrequirement constraint at interval t;

- SPRRS,t is the dual variable associated with theRRSrequirement constraint at interval t;

- SPNSRS,t is the dual variable associated with theNSRSrequirement constraint at interval t

- SPasreqtype,t is used to determine AS MCPC for each AS requirement type asreqtype=URS,DRS,RRS,NSRS at interval t.

- DAM Simultaneous Feasibility Test (SFT)

The DAM SFT is executed before DAM to check if CRR is oversold due to the Network Topology difference between yearly/monthly CRR and DAM.

The SFT is executed in the following steps:

- Set up the CRR DAM network model with all the physical generations and loads removed from the network;

- Allocate the Hub or Zone based CRR obligations to individual source/sink buses according to Hub or Zone Distribution Factors, and impose all CRR obligations as pairs of injections and withdrawals on the network;

- Solve nonlinear DC power flow;

- If power flow does not converges, stop and investigate the CRR network model

- If power flow in Step 4 converges:

- obtains the flow on branch between bus i and j---  represents the intact network;

- Solve incremental DC power flow for each Contingency Case --case n represents the post-contingency network;

- Obtains the flow on branch between bus i and j for ;

- For one CRR option at a time:

- Allocate the Hub or Zone based CRR option to individual source/sink buses according to Hub or Zone Distribution Factors, and impose the CRR option as a pair of injection and withdrawal on the network;

- Solve incremental DC power flow for. The flow on branch between bus i and j from  caused by option  is.

- Solve incremental DC power flow for each Contingency Case. The flow on branch between bus i and j caused by option  with respect to  is ;

- Calculate the final flow between bus i and j

- For Transmission Line:

- For base case, the final flow is

- For case n, the final flow is

- For Flowgate:

- For base case, the final flow is

- For case n, the final flow is

Where, fijflow gate is amount of the FGR options of the Flowgate between bus i and j

- Evaluate constraint violations

- For base case, check fij,basecasefinal against normal rating;

- For case n, check fij,case nfinal against emergency rating; If SPS is invoked, the constraint violation is ignored.

Compute shift factors for all violated constraints

Output Day-Ahead Weighted Shift Factors for settlement points, limits and oversold quantities for all violated constraints.

- Weighted Least Square Method for DAM Derating of CRR Options

For each interval of the DAM study period, ERCOT executes the Least Square Method to derate the CRR Options declared for Real-Time Settlement. The CRR derating is executed independently for each interval of the DAM study period.

For each interval t of the DAM study period, the optimization problem is formulated as follows:

Minimize: iwiADJCRRMWi,t2

Subject to:

- Transmission constraints

i,where SFi,c,t>0SFi,c,t(CRRMWi,t−ADJCRRMWi,t)≤ Limitc,t

- CRR quantity constraint

0≤ADJCRRMWi,t≤CRRMWi,t

The CRR Option Derating problem input parameters:

- is the weighting factor for CRR options  with the value of ;

- is the original MW amount of CRR option  at interval t ;

- is the limit of transmission constraint  at interval t

- is the Shift Factor of CRR option  associated with transmission constraint  at interval t.

Note that CRR option  is modeled as a pair of injection and withdrawal on the network that are self-balanced. Thus,

where,  is Shift Factor of CRR option ’s source bus  associated with transmission constraint c at interval t, and  is Shift Factor of CRR option ’s Sink bus  associated with transmission constraint c at interval t.  Without loss of generality, this superposition of Shift Factors can be applied for CRR options defined between a set of source buses (Zone/Hub) and a set of sink buses (Zone/Hub)

For all CRR options, only those CRR options i with positive SFi,c,t are included in transmission constraint c.

The CRR options that create a counter flow to relieve the constraint are excluded.

The DAM CRR Derating Problem Decision variable:

- is the MW amount curtailment for CRR options  at interval t;

- The solution of ADJCRRMWi,t may need to be rounded to the closest integer.