ERCOT Nodal Operating Guides

Section 8:  Telemetry and Communication

Draft (Month, Day, Year)

(Effective Upon Texas Nodal Market Implementation)

Contents

8	Telemetry and Communication	8-3

8.1	Telemetry	8-3

8.1.1	ERCOT Interface RTUs	8-4

8.1.2	ERCOT ICCP Interface	8-48-5

8.1.3	Validation of Real Time Signals with Settlement Metering for Resources	8-68-5

8.1.4	Data from ERCOT to QSE’s	8-6

8.1.5	Data From ERCOT to TSP	8-6

8.1.6	Data from QSE/TSP to ERCOT	8-68-6

8.1.7	TSP/QSE Telemetry Restoration	8-118-10

8.1.8	QSE and TSP Data Acquisition	8-128-10

8.2	Calibration and Testing	8-128-10

8.2.1	Responsibility	8-128-10

8.2.2	Notification	8-128-11

8.2.3	Test Equipment	8-128-11

8.2.4	Disputes	8-128-11

8.2.5	Calibration Testing	8-138-11

8.2.6	Exchange of Information	8-138-11

8.2.7	Documentation	8-138-11

8.2.8	Operator One-line Displays	8-148-13

8.2.9	Notification of Changes	8-148-13

8.3	Communications	8-158-14

8.3.1	ERCOT WAN	8-158-14

8.3.2	ERCOT Responsibilities	8-188-15

8.3.3	QSE and TSP Responsibilities	8-188-15

8.3.4	TSP and QSE Supplied Communications	8-208-17

8.3.5	Maintenance and Restoration	8-208-18

8.4	Document Control	8-228-19

TSP	8-4

8-11

8-11

8-13

Telemetry and Communication

#### 8.1	Telemetry

QSE control centers supply telemetry data to ERCOT and receive signals from ERCOT to implement frequency control.  The QSE’s interface to ERCOT for this purpose is implemented through a QSE-supplied an ICCP interface through the ERCOT WAN  at the QSE control center.

TSPs supplying telemetry to ERCOT shall use an ICCP interface through the ERCOT WAN.

Each QSE or TSP shall continuously provide the data quantities that they are responsible for providing to ERCOT.  The frequency of update, means of communication to ERCOT, and format for each point shall also be as specified in Operating Guide Attachment 8A, ERCOT Data Sets  for that entity, unless approved by ERCOT.  At the frequency specified in the Tables, each update cycle shall provide new readings of all data points being monitored, not averages linked to prior cycle readings or repetition of readings from a previous cycle.  Design accuracy and availability of data points delivered to ERCOT, shall satisfy the requirements and standards for Telemetry Performance and State Estimator Performance as specified under Section 8.1.6, Data from QSEs and TSPs to ERCOT of these guides.

The TSP shall maitinto any telemetered  of the largest line rating at each busERCOT  will identify the top 10% of MW/MVAR telemetry pairs and voltage points that are “essential”to reliability, system observability, support of State Estimator performance, or commercial Market concern which must meet the more stringent availability requirements defined below.

l provide data to ERCthang availability:99% of all data points will have an availability of at least 80% on a monthly basis

- ht (98%) per of the time, excluding approved planned outages.  Availability wil Exceptions to the above may be made with agreement with ERCOT for data points not significant in the solution of the State Estimator or required for the reliable operation on the ERCOT Transmission System.

QSEs, Resources and TSPs are required to provide power operation data to ERCOT including, but not limited to:

- Real time generation data from QSEs;

- Planned Outage information from Resources;

- Network data used by any TSP’s control center, including:

  - Breaker and line switch status of all ERCOT Transmission Elements;

  - Line flow MW and MVAR;

  - Breaker, switches connected to all Resources;

  - Transmission Facility Voltages; and

  - Transformer MW, MVAR and TAP.

- Real time generation and Load Resource meter data from QSEs;

- Real time Generation meter splitting signal from QSEs;

- Planned Transmission Outage information from TSPs;

- Network transmission data (model and constraints) from TSPs;

- Current Operating Plans from QSEs; and

- Dynamic Schedules from QSEs.

Real Time data will be provided to ERCOT at the same scan rate as the TSP or QSE obtains the data from telemetry.

#### 8.1.1	ERCOT ICCP Interface

Inter-Control Area Communications Protocol (ICCP) over Ethernet provides Telemetry data from Market Participant computers, computer networks, or other devices to the ERCOT WAN.  Suppliers of data using an ICCP link must format their data and coordinate installation according to ERCOT procedures.  The data furnished by a Market Participant’s ICCP link shall reflect the data quality codes com_failed dividual data points as coordinated with ERCOT found in the Market Participant’s control computers and data collection system.  Market Participant’s shall provide documentation to ERCOT describing their native system quality codes and defining the conversion of their RTU quality codeso the ERCOT defined quality codes.

8.1.1.1     Quality Codes

Status and  analogs telemetered to ERCOT will be identified with the following quality codes:

- Valid – represents analog or status the TSP considers valid.

- Manual – represents analog or status entered manually at the market participant (not received from the field electronically).

- Suspect - represents analog or status in which the TSP is unsure of the validity.

- Invalid – represents analog or status which the market participant has identified as out of reasonability limits.

- Com_fail – informs ERCOT that due to communications failure, the analog or status provided ERCOT is not current.

8.1.1.2  Reliability of ICCP Links

ICCP links must achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data.  A link will be considered as available when at least eighty-five (85%) percent of the data defined on that link is successfully transferred to ERCOT with a Valid or Manual quality code.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

Each TSP and QSE shall use fully redundant data communication ICCP links between its control center systems and ERCOT systems such that any single element of the communication system can fail and:

(a)	For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and

(b)	For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate.

8.1.2	Validation of Real Time Signals with Settlement Metering for Resources

The integrated real time MW signal obtained from a resource shall be validated.

Signals from resources used to supply power or ancillary services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis.

Where multiple generators share a single net settlement meter, the ratio of integrated real time signals from each generator shall be used to proportion the settlement total quantity.

#### 8.1.3	Data from ERCOT to QSE’s

ERCOT shall issue instructions and information to QSE’s in accordance with the Operating Guide and the Protocols.  Attachment 8A in this guide provides the instructional and informational data sets that ERCOT will send to the QSEs.

#### 8.1.4	Data from ERCOT to TSP

ERCOT will provide operational data and issue instructions to the TSP in accordance with the Operating Guide and the Protocols.

ERCOT is required to provide the following power operation data to TSPs

:

(1)	Relevant information for the purpose of providing reliability as determined by ERCOT, including but not limited to:

        - Status of any breakers and switches in ERCOT's Real Time data base;

        - State estimator solutions;

        - Transmission line flows and voltages;

        - Transformer information;

        - QSE Resource data;

        - Voltage schedules at major transmission busses.

ERCOT will give notice to the Entities supplying the above list of data to ERCOT upon the initial provision of such data to the TSP.

#### 8.1.5	Data from QSEs and TSPs to ERCOT

QSEs and TSPs shall provide Real Time monitoring of power system quantities to ERCOT as defined in the Operating Guides and Protocols.  Attachment 8A of this guide, gives the format and parameters for the content of each type of data point that ERCOT may request from TSPs and QSEs to satisfy the requirements in the Operating Guides and the Protocols.  Not all points in Attachment 8A are necessarily required from each Entity.  ERCOT will inform TSPs and QSEs if additions to presently furnished data are required.  All involved parties will seek to jointly resolve a means and schedule for providing data to ERCOT, including changes to existing data.  ERCOT will consider alternatives and exceptions, on a case-by-case basis, to the extent that ERCOT does not believe its operational needs are compromised.  Ultimately, it is the responsibility of the TSPs and QSEs to provide all data requested by ERCOT as set forth in the  Protocols and Operating Guides.

#### 8.1.5.1	Weather Zone Data

If the TSP is responsible for providing Weather Zone data, they are required to establish a backup to the primary source using one of the options below:

(1)	TSPs having an EMS with a native ICCP application capable of 4 second periodic data set transfers with minimum 300 points per data set, and hot standby backup ICCP servers with automatic fail-over capability, shall provide an additional ICCP association across the ERCOT WAN for the transfer of Weather Zone tie line measurements.  ICCP nodes should exist at primary and backup facilities.

2	Teleme Measurements Data

Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System state at a given point in time while filtering measurement noise (error) and detecting gross errors. The quality and availability of Telemetry provided to ERCOT are important to the performance of ERCOT’s State Estimator.

Beyond general Telemetry performance criterion there are more stringent criterion needed at locations where state estimates are “critically important” (e.g., locations where reliability, security, and Market impact are of more focused concern).

ERCOT is required to protect transmission assets operated at 60 kV or above from damage.  To do this, ERCOT may request that additional MW, MVAR, and voltage telemetry be installed, while attempting to minimize adding equipment to as few locations as practicable.

ERCOT may request additional telemetry when it determines that network observability or the measurement redundancy is not adequate to produce acceptable state estimator results per the established State Estimator TAC approved standards.

Prior to making a request for additional telemetry, ERCOT will provide evidence supporting a congestion or reliability problem requiring additional observability and  define expected improvements in system observibility needed.  If the request is for telemetry additions at more than one location, ERCOT will prioritize the requested additions.

Upon receipt of a request for additional telemetry, the TSP or QSE will have sixty (60) days to either:

(1)	Accept ERCOT’s request for additional telemetry, provide the telemetry within 18 months, and notify ERCOT of the implementation schedule;

(2)	Provide an alternative proposal to ERCOT, for implementation within the next 18 months, which meets the requirements described by ERCOT;

(3)	Propose a normal topology change (change normal status of switch(es)) in the area which would eliminate the security violations which are ERCOT’s concern. (i.e. eliminates the possibility of flow through a Transmission Element and turns the security problem into a planning problem which is un-affected by generation dispatch);

(4)	Indicate that the requested telemetry point is at a location where the TSP or QSE does not have the authority to install the requested telemetry.  For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request; or

(5)	File a request with the PUCT requesting expedited action for an Order directing that the responsibility for reliability and protection of this specific element or elements of the transmission system be withdrawn from ERCOT and assigned to the requesting TSP.  ERCOT will then immediately remove the elements from its Real Time Congestion Management system as monitored elements pending the PUCT decision.

If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.

If ERCOT has not received acknowledgement that a request has been received within thirty (30) days of its sending, ERCOT will contact the TSP or QSE for verification of receipt.

Nothing in this section shall limit the TSP’s appeal process outlined in Protocol Section 3.10.7.4, Telemetry Criteria.

8.1.5.2.1	General Telemetry Performance Criterion

The following criterion will apply in general to Telemetry provided to ERCOT:

(1)	be greater than 4% of full scale.(2)	The TSP shall maintain the sum of flows into any telemetered bus less than the greater of 5 MW or 5% of the largest line rating at each bus.

Each QSE or TDSPTSP shall provide data to ERCOT that meets the following availability:

Nnety-eight (98%)cent of all telemetry provided to ERCOT must achieve a montherly availability of at least eighty (80%) percent., excailability will be measured based on end-to-end connectivity of the  comunications path and the passing of Real-Time data with good quality codes at the scheduled periodicity.  This will include establishing a process t

(b)	ICCP links must achieve a monthly availability of ninety-eight (98%) percent of the time, excluding approved planned outages.  Availability will be measured based on end-to-end connectivity of the  communications path and the passing of Real-Time data.  A link will be considered as available when at least eighty-five (85%) percent of the data defined on that link is successfully transferred to ERCOT with a  quality code.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

TDS’s shall make reasonable efforts to obtain this data from retail customers associated with new customer-owned substations to meet this standard or obtain agreement from ERCOT that these retail customers have entered into arrangements with ERCOT to provide this data to ERCOT.  If the data cannot be obtained under either of these methoids ERCOT shall report such case to the Wholesale Electric Market Monitor.

- Tsubstations to provide this data and meet this standard  obtain into agreements with ERCOT to provide this data.(5)Exceptio significant in the solution of the State Estimator or required for the reliable operation onf the ERCOT Transmission System.  Some examples of these are:

  - station with no more than two transmission lines and less than 1of load;

  - Connection of Loads along a continuous, non-branching circuit that may be combined for telemetry purposes;

  - Substations connected radially to the bulk transmission system.

### 8.1.5.2.2	Critically Important Telemetry Performance Criterion

ERCOT will identify MW/MVAR Telemetry pairs, not exceeding 10% of the lines Transmissements in ERCOT, and 20 voltage points that are “critically important” to reliability, system observability, support of State Estimator performance, or are of a commercial Market concern. TheseThis criti important telemetry must meet more stringent criterion for accuracy and availability where specifically addressed. ERCOT will review and publish this list annually. ERCOT will use the following criterion to identify critically important Telemetry:

(1)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(2)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(3)	Loss of a telemetry point that results in the inability of ERCOT to monitor  loading on transmission facilities designated as critically important to transmission reliability by ERCOT. A list of critical facilities will be published annually.

(4)	Telemetry necessary to monitor transmission elements identified as causing 80% of congestion cost in the year for which the most recent data is available..

(5)	Telemetry necessary to monitor the 20 most voltage critical buses designated by ERCOT and approved by TAC each October.

itically important Telemetry provided toCrit

Each QSE or TDSPTSP shall provide data to ERCOT that meets the following availability:

)	inety-fiv5%) percent of the critically important telemetry defined by ERCOT must achieve a monthquarterly availabilf at least ninety-eight (980%) percent of the excludingnned outages.  Availabil-end connectivity of the  communications path and the passing of Real-Time data with Vvalid or Mmanual  good uality codes at the scheduleddicity.  A link will be considerablishing  process to coordinate downtime for ICCP links, critical important RTU’s and database maintenance.

### 8.1.5.3	State Estimator Data

ERCOT uses a state estimator to produce load flow base cases which are used to analyze the reliability of the transmission grid. Accurate and redundant telemetry and an accurate transmission power system model are required by state estimator in order to produce an optimal estimation of the transmission power system state. The state estimator results are used in contingency analysis, congestion management, and other network analysis real-time sequence functions.

### 8.1.5.3.1	Telemetry Status and Analog Measurements Data

Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System state at a given point in time while filtering measurement noise (error) and detecting gross errors. The quality and availability of telemetry provided to ERCOT are important to the performance of the ERCOT State Estimator.

Telemetry is not needed at every node of the System to arrive at a good estimate of the System’s state. There are general telemetry performance criterion, such that sufficient numbers and placement of measurements and accuracy of measurements that are available to achieve System observability and an overall good State Estimator performance.

Beyond general telemetry performance criterion there are more stringent criterion needed at locations where state estimates are “critically important” (e.g., locations where reliability, security, and Market impact are of more focused concern).

### 8.1.5.3.2	State Estimator Performance Requirements

##### State Estimator converges 97% of runs during a one wely est period.

##### On Transmission Eeements identified as causing 80% of congestion cost in the latest year for which data is available, the residual difference between State Estimator results and Power Flow results for critically monitored Ttrasmission Eeleqnt MW flows shawill  less than ERCOT will  reduce the MW telemetry – MW SE residual to < 3% of the associated emerg samples measured in a one month trial.flo accuracy requirement)bjective met if MW residual of specific identified elements is < 3% of the associated element ratingline flow on overat least 95% of samples measured in a one monthmonthweek trial.

##### Ofor which data is available, the difference between the MW telemetry value and the  MW Se shaless ththe assoca elt emrating o in a one month trial.

##### ERCOT will confirm that the MW base case element flows used in contingency analmato line flows used in crea over 95% of samples measured during a 1 month trial.  To be meaured on all State estimator samples of each month and posted.

##### On 20 most voltage critical buses designated by ERCOT and approved by TAC each Objective met if difference of all identified voltages < equipment accuracy or 2% of nominal voltage over 95% of samples measured during a 1 month trial.  To be measured on all State estimator samples of each month and posted.On 20 most voltage critical buses designated by ERCOT and approved by TAC each October; tThe telemetered bus voltage minus state estimator voltage shall be within the greater of 2% or the accuracy of the telemetered voltage measurement involved for at least 95% of samples measured during a one1 month trial.

##### of all elements during a 30 day period.  All equipment failing this test will be reportedto the associated TSP for repair within 10 days of detection.

##### (1)      ERCOT will work with TSP to resolve problem in accordance with ERCOT Operating Guides prior to directing additional equipment.

##### (2)       In event of failure to meet the standard in 8.1.6.3.2 above, ERCOT may direct additional telemetry be installed on llements contributing most to 80% of congestion costs for the latest year for which data is available, to lprotocols.  6.5.5.2 (7)). If the TSP disputes the request for additional telemetry, the TSP shalilable under Operating Guide Section 8.1.6.2, ERCOT Requests for Telemetry.

##### (3)      ERCOT will enforce the requirements of Protocol 3.10.7.4.2 (5), Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows,  by alarming any sum of flow around a bus the greater of 5% of the largest line rating connected to the bus or 5MW, and requesting that the applicable TSP or QSE correct the failure.

(4)	ERCOT will post monthly results for compliance with Section 8.1.6.3.2 items 1 through 5 above.

### (5)	ERCOT shall consider the quality codes sent by the data provider in assigning confidence factors for the data to be used in the SE.  Valid and Manual quality codes shall be considered as good quality.  Quality codes sent as not good quality shall be considered at a lower confidence.  The confidence shall continue to decrease over time.

8.1.6	TSP and QSE Telemetry Restoration

Telemetered data shall be provided continuously.  Lost data or signals, whether failed or in error, must be restored promptly by the provider of the telemetered data.  It is recognized that some data may be more critical thant other data.  ERCOT will inform the TSP or QSE if a data item is critical and needs to be repaired as quickly as possible.  QSE and TSP repair procedures and records shall be made available to ERCOT upon request.  When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 2b days, either a) Calibrate/repair the mis-behaving equipment b) Request an outage to schedule calibration/repair of the mis-behaving equipment c) Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame or d) Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.   Before ERCOT requests review/re-calibration of a problem piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision on the most appropriate action.

### 8.1.7	QSE and TSP Data Acquisition

Suppliers of telemetry must collect and process field data at their control centers before passing to the ERCOT interface.  The equipment and processes are owned and operated entirely by the supplier.  Traditionally, utilities have used both analog and digital methods of transmission at existing facilities.  It is the responsibility of the QSEs and TSPs who supply other entities’ data to ERCOT to also arrange for reliable delivery of field data from the other entities in order to support the requirements in these Operating Guides.

### 8.2	Calibration and Testing

### 8.2.1	Responsibility

It is the responsibility of the owner to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in this guide, for both the overall system and for individual equipment where detailed herein.  Coordination of outages required for these activities with ERCOT is also the responsibility of the owner.  Each TSP and QSE shall have a plan on file with ERCOT to assure accurate telemetry of data.   If a TSP and/or QSE repeatedly fails other telemetry metrics defined in these Ggides, ERCOT may require a revision of this plan.

### 8.2.2	Notification

ERCOT and all affected parties shall be notified at least 72 hours in advance, or at a mutually acceptable advance notice, prior to any calibrations or planned maintenance. In emergency conditions, the owner of the telemetry and associated equipment may make necessary repairs with notification to affected parties within 24 hours.  ERCOT or other parties sharing data from the equipment may request copies of the repair and calibration records.

### 8.2.3	Test Equipment

Test equipment and test standards intended to be used for the calibration of telemetry and associated equipment shall be certified to values of accuracy and precision that are equal to or better than the accuracy of the equipment under test.

### 8.2.4	Disputes

Where a dispute over the accuracy or performance of any telemetry equipment exists, ERCOT may request a comparison of standards and/or a joint calibration of affected equipment.

### 8.2.5	Calibration Testing

All telemetry and associated equipment for analog data quantities (MW, MVAR, Volts, LTC tap positions, etc.) shall be tested as needed to ensure accuracy and performance.  Entities providing Telemetry data to ERCOT shall make their test records, procedures and maintenance criteria available to ERCOT upon request.

### 8.2.6	Exchange of Information

### Before energizing and placing into service any new or relocated facility connected to the ERCOT Transmission Grid, a TSP, QSE, or Resource Entity shall enter appropriate information in the Outage Scheduler and coordinate with, and receive written notice of approval from, ERCOT, as specified in Protocol Section 3.3.1, ERCOT Approval of New or Relocated Facilities.

8.2.7	Documentation

Information on existing and future ERCOT System components and topology is necessary for ERCOT to create databases and perform tests.  To ensure that such information is made available to ERCOT, each TSP, or its designated agent, shall provide accurate information for all ERCOT Transmission Facilities owned or planned by the TSP.  The information provided shall include, but not be limited to, the following:

1.	Information necessary to represent the TSP’s Transmission Facilities in any model of the ERCOT Transmission Grid whose creation has been approved by ERCOT, including modeling information detailed in procedures of ERCOT and Network Data Support Working Group (NDSWG); and

2.	Identification of a designated contact person responsible for providing answers to questions ERCOT may have regarding the information provided.

3.	Consistent data with existing ERCOT Transmission Facilities owned or operated by the TSP represented in the appropriate Planning Model.  At a minimum, the impedance data (resistance, reactance, and charging), Continuous Rating, and Emergency Rating shall exactly match corresponding data represented in the Planning Model.  TSPs shall provide reasons for any data that does not exactly match.

The energization or removal of equipment in the Network Operations Model shall be done in accordance with Protocol Section 3.3.2.1, Information to Be Provided to ERCOT.

The parties involved shall furnish pertinent information to ERCOT on request, including the following:

- Connection diagrams

- Metering one line diagram

- Substation one line diagram

- Panel schematics and one line diagrams

- Instrument transformer (CT and PT) data (ratios, test reports, nameplate)

- Transducer conversion constants

- Meter constants

- Certified calibration test reports of any device used for telemetry

- Other data as may be requested

### 8.2.8	Operator One-line Displays

Operations staff at each entity providing Telemetry data shall have one-line diagrams displayable on their Energy Management System or other computer systems.  Displays shall be provided for all substations or power plant switchyards that include data passed to the ERCOT interface.

### 8.2.9	Notification of Changes

- ERCOT shall review the information and notify the requestor of any required modifications in accordance with Protocol Section 3.10 (11), Network Operations Modeling and Telemetry.

ERCOT and any other affected parties shall be informed of changes to telemetry and associated equipment per Protocol Section 3.10.1, Time Line for Network Operations Model Change Requests.

### 8.3	Communications

There are two types of data communication that will be implemented in the ERCOT System:

- Real-Time Communications (Operational), and

- Commercial Market Communications (Settlement).

This Operating Guide defines the path standards for real-time data communications (Operational) and voice communications (Operational) that shall be used to exchange security and reliability information between:

- ERCOT and a QSE, and

- ERCOT and a TSP.

As Operational signals may originate with or be destined for organizations connected to a QSE or TSP, path standards are also defined for real-time data communications (Operational) and voice communications (Operational) required by QSEs and TSPs that impact or contribute to security and reliability information required by ERCOT.

Commercial Market Communications (Settlement) are not defined in this Operating Guide, other than facilities needed to provide common communications.  Operational Communication requirements take precedence over Commercial Market Communication requirements.

### 8.3.1	ERCOT WAN

In order to facilitate wholesale operations and frequency control as a single control area, ERCOT provides a wide area network (the ERCOT WAN).  This communications network uses redundant, digital communications between ERCOT control centers and one or more facilities at each QSE and TSP.  The ERCOT WAN has sufficient bandwidth capacity and speed to enable:

- Real time (telemetry) data exchange for frequency control and transmission security

- Operational voice communications for both normal and emergency use.  The ERCOT WAN supports both off-premise exchanges (OPX) with ERCOT’s control facilities and the ERCOT hotlines.

- Data exchange to support applications programming interface (API) routines.  These include power scheduling, operating plans, outage requests, dispatch instructions, posting of information and other applications.

8.3.1.1	QSE Use of Domain Name Service (DNS) or ERCOT Web-Based Front Page for Site Failover

A QSE possessing backup sites must utilize one of the following two options: (1) a WAN (Wide Area Network) Domain Name Service (DNS) server or (2) an ERCOT provided web-based DNS service to facilitate the failover process when moving its operations between primary and backup sites.  The requirements of these options are specified below.

8.3.1.1.1	DNS Server Configuration for Failover Support

A QSE is required to provide and maintain its own DNS servers that must be accessible by the ERCOT WAN.  The failover process requires the following:

(1)	DNS servers must support zone transfers over TCP port 53.

(2)	Firewalls must allow zone transfers to ERCOT DNS servers.

(3)	Zone files for the QSE's domains (e.g. examplepower.com) must reside on its WAN accessible DNS servers.

(4)	DNS servers must be set up as the master for its zone.

(5)	DNS servers must allow ERCOT DNS servers to transfer the zone files (ERCOT will be set up as a secondary/slave server for the zone).

(6)	The zone files must contain names for all local servers the QSE will need ERCOT services to access.  At a minimum, it must contain entries for the servers that can be switched over to the backup site.  The zone file must also contain entries for the QSE's primary website address (e.g. www.examplepower.com) and other common internet accessible sites that ERCOT servers may have occasional need to access.

(7)	Time to Live (TTL) values for backup host entries in the zone file must be set to 0 in order to prevent the host to IP address mappings from being cached on the client machines.  This allows any changes made to a zone file to take effect immediately upon a zone transfer.

Once its DNS servers are operational, the QSE shall timely contact its ERCOT Client Services Representative and request that an ERCOT network administrator work with the QSE to test the functionality of the DNS setup.  The QSE must contact the ERCOT Client Services Representative at least five (5) Business Days before testing.

After the zone transfer testing is complete, the QSE shall supply its ERCOT Client Services Representative with a list of participant servers, their DNS names, and their roles on the network.  The ERCOT Client Services Representative will then contact the application owners at ERCOT to change application communications to use the DNS name instead of IP addresses.

After successful completion of the test, when a QSE backup site failover is desired, the QSE shall update the zone file with its disaster recovery IP addresses and publish it to the ERCOT DNS servers.  The change will be effective immediately.  The QSE shall also implement a DNS server at its backup site.  This allows updated zone files to be published regardless if the primary site is up or not.

8.3.1.1.2	Web-Based DNS Access

This access is provided as an alternative method for any QSE that does not wish to maintain its own DNS servers.  Access is provided over the ERCOT WAN only.  The QSE is responsible for access through its networks to the web servers located on the ERCOT WAN.  The QSE shall adhere to ERCOT password requirements.

To failover to or from a backup site, the QSE shall update the IP address of the existing entry.  ERCOT servers will accept the change and start using the new IP immediately.

Once the QSE has connectivity to the web server over the ERCOT WAN, it shall contact its ERCOT Client Services Representative and request that an ERCOT network administrator work with the QSE to test the functionality of the DNS setup.  The QSE shall contact the ERCOT Client Services Representative at least five (5) Business Days before testing.  After testing is completed, the Client Services Representative will contact the application owners at ERCOT to change application communications to use DNS names instead of IP addresses.

After successful completion of the test, when a QSE site failover is desired, the QSE shall change the Web page entries with the active site information and the change will be effective immediately.

### 8.3.2	ERCOT Responsibilities

ERCOT supplies interface requirements, equipment, installation and 24-hour maintenance for the entire ERCOT WAN, including equipment at each QSE and TSP control facility, as well as ERCOT’s control centers.  ERCOT’s responsibilities include:

    - Supply and install fully configured and tested Customer Premises Equipment including routers, CSU/DSUs, LAN switch/hub and all support equipment for management purposes.

    - Order and provision of local loop, network access point and transport.

    - Design, configure, test, and install network monitoring and management service.

    - Provide 24-hour network monitoring and management.

    - Provide 24X7 maintenance, with 4-hour response, for all ERCOT equipment located at participant site.

    - ERCOT will be the single point of contact for all network issues.

### 8.3.3	QSE and TSP Responsibilities

TSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance.  Users of the ERCOT WAN shall provide signal connections, uninterruptible power, and physical space for ERCOT-supplied WAN interface equipment at their control centers, as well as 24-hour access for ERCOT installation and maintenance personnel.

At these facilities, computer and communications equipment connected to ERCOT WAN interfaces is the complete responsibility of the QSE or TSP.   Facilities shall have uninterruptible power supplies (UPS) capable of independently supplying all equipment connected to the ERCOT WAN for at least 72 hours.

Any TSP or QSE facility, whether primary or backup, involved in the transfer of the data sets identified in Attachment 8A, will be required to connect directly to the ERCOT WAN Primary Private Network and Point-to-Point paths. If a TSP and QSE utilize the same EMS and server network at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TSP and QSE share a centralized PBX, separate OPX circuits will be terminated for each participant.  The Hotline will not be allowed to connect through the PBX system and is required for each participant.

A QSE or TSP involved in the transfer of the critical data identified in Attachment 8A of this guide, will be required to provide the following communication resources to support the connection to the ERCOT private network:

- Private Network

  - Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment.

  - Provide a height of 24” of rack space in a 19” wide rack.

  - Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above.

  - Provide building wiring from circuit termination to equipment rack.

  - Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility.

  - Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors.

  - Provide on site personnel to escort ERCOT employees or contractors.

  - Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN.

  - Market Participant will be required to sign a security connection agreement with ERCOT.

  - Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection.

  - Provide a channel bank with at least one T1 interface, 4 FXS and two 4 wire analog ports. Connect FXS (e.g. PBX, key system) and 4 wire ports to the appropriate equipment.  On the digital T1 stream, levels for voice are zero dpm for transmit and receive

  - Hotline must be a 500 set not attached to the Market Participant’s Phone System.

  - Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended.

  - Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.

- Internet (optional)

A QSE or TSP not involved in the transfer of the data identified in Attachment 8A of this guide, is not required to, but, may request ERCOT to provide an optional connection to the ERCOT private network.  When such a request is met by ERCOT, the QSE or TSP must then provide the above stated communications resources.

CSU/DSU

FIREWALL OR ROUTER

CSU/DSU

ROUTER

ROUTER

SWITCH

SWITCH

ERCOT PROVIDED

EQUIPMENT

CHANNEL

BANK

Taylor Hotline (FXS)

Taylor OPX (FXS)

4WIRE

2WIRE

FRAMEPRIVATE

NETWORK

DACS

NETWORK

TO PARTICIPANT NETWORK

RS232

GATEWAY

Fractional T1

Austin OPX (FXS)

Austin Hotline (FXS)

2WIRE

2WIRE

2WIRE

4WIRE

RTU ICCP WITH 3

ERCOT

PORTS

### 8.3.4	TSP and QSE Supplied Communications

Each TSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN.  For TSPs these include, but may not be limited to, voice communications and SCADA for substations and other transmission facilities.  For QSEs, these include, but may not be limited to, voice and SCADA for generating plants and loads.

QSEs and TSPs shall supply, implement and maintain all data and voice communication facilities required to fulfill the obligations set forth in the Operating Guides.

Proper performance, maintenance and testing of communication paths not directly connected to the ERCOT WAN shall be the responsibility of the TSP or QSE providing the path.

QSEs communicating with connected resources and TSPs communicating with substations are encouraged to use privately owned communication facilities.  Backup facilities utilizing common carriers, different privately owned facilities, or communications paths to a site are encouraged to provide increased reliability (i.e., separate paths to a site using different carrier, having multiple microwave paths leaving a site, etc.).

### 8.3.5	Maintenance and Restoration

It is the joint responsibility of ERCOT WAN-connected parties to coordinate maintenance and restoration activities so its reliability is not compromised.  Coordination and notification procedures defined by ERCOT are to be followed by all parties.

All circuits shall be tested annually or as otherwise requested by ERCOT for end-to-end performance.  Special attention shall be given to circuits not used for routine communications (including backup circuits).

The hotline and any backup (alternate path) voice circuits shall be used regularly to insure proper performance.  ERCOT will specify test procedures for hotline circuits.

Scheduled outages of communication circuits that could reduce the reliability of interconnected operations shall be coordinated between the affected companies and ERCOT.

In the event of wide spread communication failures, priority shall be given to restoring communication circuits between QSE Control Centers/TSP Control Centers and ERCOT Control Area Authority first, and between QSEs and TSPs second.

Test equipment and test standards intended to be used for the calibration or repair of communication equipment shall be certified to values of accuracy and precision, which are equal to or better than the accuracy of the equipment under test.

### Authorities

Distribution List

Change History