## Slide 6: ERCOT Frequency Response
Evaluated 27 events May – Sept 2006
Recommend May – Sept Bias of 636 MW/0.1 Hz
Present Bias setting of 520 MW/0.1 Hz continues through April 2007.
ERCOT to report 2007 Bias settings to NERC by Dec 29, 2006.

## Slide 12: Frequency Response Summary
Frequency Response has improved slightly.
  Some QSE’s are getting calls from the ERCOT Frequency Desk Operator indicating the QSE is short of it’s Responsive Reserve Obligation. This can occur anytime the QSE has adequate RRS at 60 Hz, but due to governor response, will have less when frequency is low.
Frequency Response at the B+30 has improved but some “squelching” continues.